## Introduction
An analysis of the impacts of all-electric heat pumps and peak mitigation technologies on peak power demand in Ontario
This spreadsheet is designed to help the user understand the calculation made for the report on the impacts of all-electric heat pump and peak mitigation technologies on peak power demand in Ontario. Users also have the opportunity to change some of the assumptions and data points used and test the impacts on the outcomes.
The ASHPs and GSHPs sheets contain the raw data used to determine the power draw of different sized heat pumps in each temperature bin. Tables showing the home heating load calculations are found at the bottom of these sheets.
The input sheet contains additional input data and sources for all equipment used in the analysis, geographical housing statistics and data used in calculating the avoided costs of building new electricity generation. Values in this sheet can be changed to test the impacts on the calculated outcomes.
The regional outcomes sheet summarizes the heat pump and peak mitigation technology outcomes for each of the geographic regions as well as the outcomes for an average Ontario single family home after taking the geographically weighted average. These outcomes form the basis of the values in the Figures.
The data used to plot the Figures can be seen in the corresponding Figure sheets.
The assumptions sheet lists the assumptions that were made in this analysis.
The formulas sheet shows the calculations and methodology used. For further details, please refer to the full report.

## ASHPs
ASHP data from manufacturer specification sheets
|  |  |  | without backup | [5 empty] | capacity | [5 empty] | capacity met by backup resistance heater | [5 empty] | COP | [5 empty] | % of time HP is running | [5 empty] | % of time electric resistance is running
brand | model | size | scop | kW at -10 | kW at -13.5 | kW at -15 | kW at -20 | kW at -25 | kW a -30 | -10 | -13.5 | -15 | -20 | -25 | -30 | -10 | -13.5 | -15 | -20 | -25 | -30 | -10 | -13.5 | -15 | -20 | -25 | -30 | -10 | -13.5 | -15 | -20 | -25 | -30 | -10 | -13.5 | -15 | -20 | -25 | -30
Capacity calculated using 36,000 BTU/hr at -20'C
-30'C design temperature
Moovair | FMA48HIAHUU230X7/DMA48HOS20230E7 | 4t |  | 6.86 | 6.93 | 7.1 | 7.46 | 7.83 | 7.59 | 50440 | 48830 | 47060 | 43290 | 38960 | 33120 | 0 | 0 | 0 | 0 | 2355.7029 | 12932.545 | 2.155 | 2.0651 | 1.9426 | 1.7007 | 1.4583 | 1.2789 | 0.53737 | 0.623 | 0.67663 | 0.84497 | 1 | 1 | 0 | 0 | 0 | 0 | 0.046028 | 0.25269
Daikin Comfort | FTQ48TAVJU + RZQ48TAVJUA | 4t |  | 6.67 | 6.47 | 6.41 | 6.03 | 6.395 | 6.395 | 52203.6 | 48109.2 | 46744.4 | 40602.8 | 36542.52 | 20301.4 | 0 | 0 | 0 | 0 | 4773.1829 | 25751.145 | 2.2939 | 2.1793 | 2.1373 | 1.9735 | 1.6747 | 0.93041 | 0.51922 | 0.63233 | 0.68119 | 0.9009 | 1 | 1 | 0 | 0 | 0 | 0 | 0.093263 | 0.50315
Fujitsu | AMUG48LMAS | 4t |  | 6.34 | 6.37 | 6.39 | 6.34 | 6.29 | 6.346 | 51000 | 51000 | 51000 | 45500 | 39000 | 34039.4032 | 0 | 0 | 0 | 0 | 2315.7029 | 12013.1418 | 2.3576 | 2.3465 | 2.3392 | 2.1034 | 1.8172 | 1.5721 | 0.53147 | 0.59649 | 0.62435 | 0.80393 | 1 | 1 | 0 | 0 | 0 | 0 | 0.045246 | 0.23472
Mitsubishi Zuba | PVA‐A42AA7/PUZ-HA42NKA | 4t |  | 7.67 | 7.6 | 7.54 | 7.35 | 7.1 | 7.452 | 48000 | 48000 | 48000 | 43200 | 38400 | 34239.0207 | 0 | 0 | 0 | 0 | 2915.7029 | 11813.5244 | 1.8342 | 1.8511 | 1.8658 | 1.7226 | 1.5851 | 1.3466 | 0.56469 | 0.63377 | 0.66338 | 0.84673 | 1 | 1 | 0 | 0 | 0 | 0 | 0.05697 | 0.23082
GE Connect | AUH4060ZGDA/UUY60ZGDAA | 5t |  | 7.1 | 7.13 | 7.16 | 7 | 6.7 | 6.35 | 49000 | 46500 | 44000 | 37000 | 32000 | 27000 | 0 | 0 | 0 | 0 | 9315.7029 | 19052.545 | 2.0227 | 1.9114 | 1.8011 | 1.5492 | 1.3998 | 1.2462 | 0.55317 | 0.65421 | 0.72368 | 0.98862 | 1 | 1 | 0 | 0 | 0 | 0 | 0.18202 | 0.37227
average |  |  |  | 6.928 | 6.9 | 6.92 | 6.836 | 6.863 | 6.8266 | 50128.72 | 48487.84 | 47360.88 | 41918.56 | 36980.504 | 29739.9648 | 0 | 0 | 0 | 0 | 4335.1989 | 16312.5803 | 2.1327 | 2.0707 | 2.0172 | 1.8099 | 1.587 | 1.2748 | 0.54119 | 0.62796 | 0.67385 | 0.87703 | 1 | 1 | 0 | 0 | 0 | 0 | 0.084705 | 0.31873
-25'C design temperature
Moovair | FMA48HIAHUU230X7/DMA48HOS20230E7 | 4t |  | 6.86 | 6.93 | 7.1 | 7.46 | 7.83 | 7.59 | 50440 | 48830 | 47060 | 43290 | 38960 | 33120 | 0 | 0 | 0 | 0 | 2355.7029 | 12932.545 | 2.155 | 2.0651 | 1.9426 | 1.7007 | 1.4583 | 1.2789 | 0.53737 | 0.623 | 0.67663 | 0.84497 | 1 | 1 | 0 | 0 | 0 | 0 | 0.069042 | 0.37903
Daikin Comfort | FTQ48TAVJU + RZQ48TAVJUA | 4t |  | 6.67 | 6.47 | 6.41 | 6.03 | 6.395 | 6.395 | 52203.6 | 48109.2 | 46744.4 | 40602.8 | 36542.52 | 20301.4 | 0 | 0 | 0 | 0 | 4773.1829 | 25751.145 | 2.2939 | 2.1793 | 2.1373 | 1.9735 | 1.6747 | 0.93041 | 0.51922 | 0.63233 | 0.68119 | 0.9009 | 1 | 1 | 0 | 0 | 0 | 0 | 0.13989 | 0.75472
Fujitsu | AMUG48LMAS | 4t |  | 6.34 | 6.37 | 6.39 | 6.34 | 6.29 | 6.346 | 51000 | 51000 | 51000 | 45500 | 39000 | 34039.4032 | 0 | 0 | 0 | 0 | 2315.7029 | 12013.1418 | 2.3576 | 2.3465 | 2.3392 | 2.1034 | 1.8172 | 1.5721 | 0.53147 | 0.59649 | 0.62435 | 0.80393 | 1 | 1 | 0 | 0 | 0 | 0 | 0.067869 | 0.35209
Mitsubishi Zuba | PVA‐A42AA7/PUZ-HA42NKA | 4t |  | 7.67 | 7.6 | 7.54 | 7.35 | 7.1 | 7.452 | 48000 | 48000 | 48000 | 43200 | 38400 | 34239.0207 | 0 | 0 | 0 | 0 | 2915.7029 | 11813.5244 | 1.8342 | 1.8511 | 1.8658 | 1.7226 | 1.5851 | 1.3466 | 0.56469 | 0.63377 | 0.66338 | 0.84673 | 1 | 1 | 0 | 0 | 0 | 0 | 0.085454 | 0.34623
GE Connect | AUH4060ZGDA/UUY60ZGDAA | 5t |  | 7.1 | 7.13 | 7.16 | 7 | 6.7 | 6.35 | 49000 | 46500 | 44000 | 37000 | 32000 | 27000 | 0 | 0 | 0 | 0 | 9315.7029 | 19052.545 | 2.0227 | 1.9114 | 1.8011 | 1.5492 | 1.3998 | 1.2462 | 0.55317 | 0.65421 | 0.72368 | 0.98862 | 1 | 1 | 0 | 0 | 0 | 0 | 0.27303 | 0.5584
average |  |  |  | 6.928 | 6.9 | 6.92 | 6.836 | 6.863 | 6.8266 | 50128.72 | 48487.84 | 47360.88 | 41918.56 | 36980.504 | 29739.9648 | 0 | 0 | 0 | 0 | 4335.1989 | 16312.5803 | 2.1327 | 2.0707 | 2.0172 | 1.8099 | 1.587 | 1.2748 | 0.54119 | 0.62796 | 0.67385 | 0.87703 | 1 | 1 | 0 | 0 | 0 | 0 | 0.12706 | 0.47809
-20'C design temperature
Moovair | FMA36HIAHUU230X7/DMA36HOS20230E7 | 3t |  | 6.44 | 6.33 | 6.25 | 6.56 | 6.89 | 6.91 | 42840 | 40720 | 38890 | 35780 | 32200 | 27690 | 0 | 0 | 0 | 798.8608 | 9115.7029 | 18362.545 | 1.9496 | 1.8854 | 1.8237 | 1.5986 | 1.3697 | 1.1745 | 0.63271 | 0.74708 | 0.81877 | 1 | 1 | 1 | 0 | 0 | 0 | 0.023413 | 0.26717 | 0.53818
Daikin Comfort | FTQ36TAVJUD/A + RZQ36TAVJUA | 3t |  | 5.25 | 5.9 | 6.09 | 7.42 | 6.165 | 6.165 | 39920.4 | 39920.4 | 39920.4 | 39920.4 | 35928.36 | 19960.2 | 0 | 0 | 0 | 0 | 5387.3429 | 26092.345 | 2.2286 | 1.9831 | 1.9212 | 1.5768 | 1.708 | 0.94891 | 0.67898 | 0.76204 | 0.79764 | 0.91629 | 1 | 1 | 0 | 0 | 0 | 0 | 0.15789 | 0.76472
Mitsubishi Zuba | PVA‐A36AA4/PUZ-HA36NHA5 | 3t |  | 5.69 | 5.98 | 6.1 | 6.12 | 6.15 | 6.008 | 38000 | 38000 | 38000 | 34200 | 30400 | 27105.8914 | 0 | 0 | 0 | 2378.8608 | 10915.7029 | 18946.6537 | 1.9573 | 1.8624 | 1.8258 | 1.6378 | 1.4487 | 1.3223 | 0.71329 | 0.80055 | 0.83795 | 1 | 1 | 1 | 0 | 0 | 0 | 0.06972 | 0.31992 | 0.55529
Fujitsu | AMUG36LMAS | 3t |  | 5.82 | 5.85 | 5.85 | 5.8 | 5.75 | 5.814 | 44150 | 43000 | 42000 | 38000 | 32000 | 27703.137 | 0 | 0 | 0 | 0 | 9315.7029 | 18349.4081 | 2.2233 | 2.1543 | 2.1042 | 1.9202 | 1.6311 | 1.3965 | 0.61393 | 0.70746 | 0.75814 | 0.9626 | 1 | 1 | 0 | 0 | 0 | 0 | 0.27303 | 0.53779
GE Connect | AUH4860ZGDA1/UUY48ZGDAA | 4t |  | 6.88 | 6.9 | 6.92 | 6.2 | 5.9 | 5.7 | 48000 | 45500 | 43000 | 34200 | 28500 | 26400 | 0 | 0 | 0 | 2378.8608 | 12815.7029 | 19652.545 | 2.0448 | 1.9327 | 1.8212 | 1.6167 | 1.4157 | 1.3574 | 0.56469 | 0.66859 | 0.74051 | 1 | 1 | 1 | 0 | 0 | 0 | 0.06972 | 0.37561 | 0.57598
average |  |  |  | 6.016 | 6.192 | 6.242 | 6.42 | 6.171 | 6.1194 | 42582.08 | 41428.08 | 40362.08 | 36420.08 | 31805.672 | 25771.8457 | 0 | 0 | 0 | 1111.3165 | 9510.0309 | 20280.6994 | 2.0807 | 1.9636 | 1.8992 | 1.67 | 1.5147 | 1.2399 | 0.64072 | 0.73715 | 0.7906 | 0.97578 | 1 | 1 | 0 | 0 | 0 | 0.032571 | 0.27872 | 0.59439
Moovair | FMA30HIAHUU230X7/DMA30HOS20230E7 | 2.5t |  | 3.84 | 3.97 | 4.13 | 4.34 | 4.55 | 4.52 | 29620 | 29080 | 28550 | 26270 | 23900 | 21040 | 0 | 1340.9661 | 3292.0187 | 10308.8608 | 17415.7029 | 25012.545 | 2.2607 | 2.1468 | 2.026 | 1.774 | 1.5395 | 1.3643 | 0.9151 | 1 | 1 | 1 | 1 | 1 | 0 | 0.039301 | 0.096484 | 0.30214 | 0.51043 | 0.73308
Daikin Comfort | FTQ30TAVJUD/A + RZQ30TAVJUA | 2.5t |  | 4.11 | 4.61 | 4.77 | 5.81 | 4.825 | 4.825 | 33983.52 | 33983.52 | 33983.52 | 33983.52 | 30585.168 | 16991.76 | 0 | 0 | 0 | 2595.3408 | 10730.5349 | 29060.785 | 2.4234 | 2.1605 | 2.0881 | 1.7143 | 1.8578 | 1.0321 | 0.7976 | 0.89517 | 0.93698 | 1 | 1 | 1 | 0 | 0 | 0 | 0.076065 | 0.31449 | 0.85172
Mitsubishi Zuba | PVA‐A30AA7/PUZ-HA30NHA5 | 2.5t |  | 4.58 | 4.73 | 4.87 | 4.91 | 4.95 | 4.808 | 32000 | 32000 | 32000 | 28800 | 25600 | 22826.0138 | 0 | 0 | 0 | 7778.8608 | 15715.7029 | 23226.5313 | 2.0477 | 1.9828 | 1.9258 | 1.7191 | 1.5157 | 1.3914 | 0.84704 | 0.95066 | 0.99506 | 1 | 1 | 1 | 0 | 0 | 0 | 0.22799 | 0.4606 | 0.68073
Fujitsu | AMUG30LMAS | 2.5t |  | 4.98 | 5 | 5.01 | 4.97 | 4.93 | 4.978 | 34290 | 33600 | 33000 | 29000 | 26000 | 22459.0666 | 0 | 0 | 0 | 7578.8608 | 15315.7029 | 23593.4785 | 2.018 | 1.9695 | 1.9305 | 1.7101 | 1.5457 | 1.3223 | 0.79047 | 0.90539 | 0.96491 | 1 | 1 | 1 | 0 | 0 | 0 | 0.22212 | 0.44888 | 0.69149
GE Connect | AUH2436ZGDA/UUY36ZGDAA | 3t |  | 5.45 | 4.8 | 4.8 | 4.63 | 4.43 | 4.15 | 36000 | 33000 | 30000 | 25200 | 21100 | 18400 | 0 | 0 | 1842.0187 | 11378.8608 | 20215.7029 | 27652.545 | 1.936 | 2.0149 | 1.8318 | 1.5952 | 1.3959 | 1.2995 | 0.75292 | 0.92185 | 1 | 1 | 1 | 1 | 0 | 0 | 0.053986 | 0.3335 | 0.59249 | 0.81045
average |  |  |  | 4.592 | 4.622 | 4.716 | 4.932 | 4.737 | 4.6562 | 33178.704 | 32332.704 | 31506.704 | 28650.704 | 25437.0336 | 20343.3681 | 0 | 268.1932 | 1026.8075 | 7928.1568 | 15878.6693 | 25709.177 | 2.1372 | 2.0549 | 1.9604 | 1.7025 | 1.5709 | 1.2819 | 0.82062 | 0.93461 | 0.97939 | 1 | 1 | 1 | 0 | 0.0078603 | 0.030094 | 0.23236 | 0.46538 | 0.75349
Capacity calculated with 30,000 BTU/hr at -20'C
-25'C design temperature
Moovair | FMA48HIAHUU230X7/DMA48HOS20230E7 | 4t |  | 6.86 | 6.93 | 7.1 | 7.46 | 7.83 | 7.59 | 50440 | 48830 | 47060 | 43290 | 38960 | 33120 | 0 | 0 | 0 | 0 | 0 | 5353.5977 | 2.155 | 2.0651 | 1.9426 | 1.7007 | 1.4583 | 1.2789 | 0.44972 | 0.52114 | 0.56591 | 0.70637 | 0.8862 | 1 | 0 | 0 | 0 | 0 | 0 | 0.1569
Daikin Comfort | FTQ48TAVJU + RZQ48TAVJUA | 4t |  | 6.67 | 6.47 | 6.41 | 6.03 | 6.395 | 6.395 | 52203.6 | 48109.2 | 46744.4 | 40602.8 | 36542.52 | 20301.4 | 0 | 0 | 0 | 0 | 0 | 18172.1977 | 2.2939 | 2.1793 | 2.1373 | 1.9735 | 1.6747 | 0.93041 | 0.43453 | 0.52895 | 0.56973 | 0.75312 | 0.94482 | 1 | 0 | 0 | 0 | 0 | 0 | 0.5326
Fujitsu | AMUG48LMAS | 4t |  | 6.34 | 6.37 | 6.39 | 6.34 | 6.29 | 6.346 | 51000 | 51000 | 51000 | 45500 | 39000 | 34039.4032 | 0 | 0 | 0 | 0 | 0 | 4434.1945 | 2.3576 | 2.3465 | 2.3392 | 2.1034 | 1.8172 | 1.5721 | 0.44479 | 0.49897 | 0.52219 | 0.67206 | 0.88529 | 1 | 0 | 0 | 0 | 0 | 0 | 0.12996
Mitsubishi Zuba | PVA‐A42AA7/PUZ-HA42NKA | 4t |  | 7.67 | 7.6 | 7.54 | 7.35 | 7.1 | 7.452 | 48000 | 48000 | 48000 | 43200 | 38400 | 34239.0207 | 0 | 0 | 0 | 0 | 0 | 4234.577 | 1.8342 | 1.8511 | 1.8658 | 1.7226 | 1.5851 | 1.3466 | 0.47259 | 0.53015 | 0.55482 | 0.70784 | 0.89912 | 1 | 0 | 0 | 0 | 0 | 0 | 0.12411
GE Connect | AUH4060ZGDA/UUY60ZGDAA | 5t |  | 7.1 | 7.13 | 7.16 | 7 | 6.7 | 6.35 | 49000 | 46500 | 44000 | 37000 | 32000 | 27000 | 0 | 0 | 0 | 0 | 2526.2293 | 11473.5977 | 2.0227 | 1.9114 | 1.8011 | 1.5492 | 1.3998 | 1.2462 | 0.46294 | 0.54725 | 0.60526 | 0.82646 | 1 | 1 | 0 | 0 | 0 | 0 | 0.07404 | 0.33627
average |  |  |  | 6.928 | 6.9 | 6.92 | 6.836 | 6.863 | 6.8266 | 50128.72 | 48487.84 | 47360.88 | 41918.56 | 36980.504 | 29739.9648 | 0 | 0 | 0 | 0 | 505.2459 | 8733.6329 | 2.1327 | 2.0707 | 2.0172 | 1.8099 | 1.587 | 1.2748 | 0.45291 | 0.52529 | 0.56358 | 0.73317 | 0.92309 | 1 | 0 | 0 | 0 | 0 | 0.014808 | 0.25597
-20'C design temperature
Moovair | FMA36HIAHUU230X7/DMA36HOS20230E7 | 3t |  | 6.44 | 6.33 | 6.25 | 6.56 | 6.89 | 6.91 | 42840 | 40720 | 38890 | 35780 | 32200 | 27690 | 0 | 0 | 0 | 0 | 2326.2293 | 10783.5977 | 1.9496 | 1.8854 | 1.8237 | 1.5986 | 1.3697 | 1.1745 | 0.52951 | 0.62493 | 0.68479 | 0.85464 | 1 | 1 | 0 | 0 | 0 | 0 | 0.068178 | 0.31605
Daikin Comfort | FTQ36TAVJUD/A + RZQ36TAVJUA | 3t |  | 5.25 | 5.9 | 6.09 | 7.42 | 6.165 | 6.165 | 39920.4 | 39920.4 | 39920.4 | 39920.4 | 35928.36 | 19960.2 | 0 | 0 | 0 | 0 | 0 | 18513.3977 | 2.2286 | 1.9831 | 1.9212 | 1.5768 | 1.708 | 0.94891 | 0.56823 | 0.63745 | 0.66711 | 0.766 | 0.96097 | 1 | 0 | 0 | 0 | 0 | 0 | 0.5426
Mitsubishi Zuba | PVA‐A36AA4/PUZ-HA36NHA5 | 3t |  | 5.69 | 5.98 | 6.1 | 6.12 | 6.15 | 6.008 | 38000 | 38000 | 38000 | 34200 | 30400 | 27105.8914 | 0 | 0 | 0 | 0 | 4126.2293 | 11367.7063 | 1.9573 | 1.8624 | 1.8258 | 1.6378 | 1.4487 | 1.3223 | 0.59695 | 0.66967 | 0.70083 | 0.89412 | 1 | 1 | 0 | 0 | 0 | 0 | 0.12093 | 0.33317
Fujitsu | AMUG36LMAS | 3t |  | 5.82 | 5.85 | 5.85 | 5.8 | 5.75 | 5.814 | 44150 | 43000 | 42000 | 38000 | 32000 | 27703.137 | 0 | 0 | 0 | 0 | 2526.2293 | 10770.4607 | 2.2233 | 2.1543 | 2.1042 | 1.9202 | 1.6311 | 1.3965 | 0.5138 | 0.5918 | 0.63408 | 0.80471 | 1 | 1 | 0 | 0 | 0 | 0 | 0.07404 | 0.31566
GE Connect | AUH4860ZGDA1/UUY48ZGDAA | 4t |  | 6.88 | 6.9 | 6.92 | 6.2 | 5.9 | 5.7 | 48000 | 45500 | 43000 | 34200 | 28500 | 26400 | 0 | 0 | 0 | 0 | 6026.2293 | 12073.5977 | 2.0448 | 1.9327 | 1.8212 | 1.6167 | 1.4157 | 1.3574 | 0.47259 | 0.55928 | 0.61934 | 0.89412 | 1 | 1 | 0 | 0 | 0 | 0 | 0.17662 | 0.35386
average |  |  |  | 6.016 | 6.192 | 6.242 | 6.42 | 6.171 | 6.1194 | 42582.08 | 41428.08 | 40362.08 | 36420.08 | 31805.672 | 25771.8457 | 0 | 0 | 0 | 0 | 3000.9834 | 12701.752 | 2.0807 | 1.9636 | 1.8992 | 1.67 | 1.5147 | 1.2399 | 0.53622 | 0.61663 | 0.66123 | 0.84272 | 0.99219 | 1 | 0 | 0 | 0 | 0 | 0.087954 | 0.37227
Moovair | FMA30HIAHUU230X7/DMA30HOS20230E7 | 2.5t |  | 3.84 | 3.97 | 4.13 | 4.34 | 4.55 | 4.52 | 29620 | 29080 | 28550 | 26270 | 23900 | 21040 | 0 | 0 | 0 | 4308.8608 | 10626.2293 | 17433.5977 | 2.2607 | 2.1468 | 2.026 | 1.774 | 1.5395 | 1.3643 | 0.76584 | 0.87508 | 0.9328 | 1 | 1 | 1 | 0 | 0 | 0 | 0.12629 | 0.31144 | 0.51095
Daikin Comfort | FTQ30TAVJUD/A + RZQ30TAVJUA | 2.5t |  | 4.11 | 4.61 | 4.77 | 5.81 | 4.825 | 4.825 | 33983.52 | 33983.52 | 33983.52 | 33983.52 | 30585.168 | 16991.76 | 0 | 0 | 0 | 0 | 3941.0613 | 21481.8377 | 2.4234 | 2.1605 | 2.0881 | 1.7143 | 1.8578 | 1.0321 | 0.6675 | 0.74881 | 0.78366 | 0.89981 | 1 | 1 | 0 | 0 | 0 | 0 | 0.11551 | 0.6296
Mitsubishi Zuba | PVA‐A30AA7/PUZ-HA30NHA5 | 2.5t |  | 4.58 | 4.73 | 4.87 | 4.91 | 4.95 | 4.808 | 32000 | 32000 | 32000 | 28800 | 25600 | 22826.0138 | 0 | 0 | 0 | 1778.8608 | 8926.2293 | 15647.5839 | 2.0477 | 1.9828 | 1.9258 | 1.7191 | 1.5157 | 1.3914 | 0.70888 | 0.79523 | 0.83223 | 1 | 1 | 1 | 0 | 0 | 0 | 0.052135 | 0.26161 | 0.4586
Fujitsu | AMUG30LMAS | 2.5t |  | 4.98 | 5 | 5.01 | 4.97 | 4.93 | 4.978 | 34290 | 33600 | 33000 | 29000 | 26000 | 22459.0666 | 0 | 0 | 0 | 1578.8608 | 8526.2293 | 16014.5311 | 2.018 | 1.9695 | 1.9305 | 1.7101 | 1.5457 | 1.3223 | 0.66154 | 0.75736 | 0.80701 | 1 | 1 | 1 | 0 | 0 | 0 | 0.046274 | 0.24989 | 0.46936
GE Connect | AUH2436ZGDA/UUY36ZGDAA | 3t |  | 5.45 | 4.8 | 4.8 | 4.63 | 4.43 | 4.15 | 36000 | 33000 | 30000 | 25200 | 21100 | 18400 | 0 | 0 | 0 | 5378.8608 | 13426.2293 | 20073.5977 | 1.936 | 2.0149 | 1.8318 | 1.5952 | 1.3959 | 1.2995 | 0.63011 | 0.77113 | 0.88772 | 1 | 1 | 1 | 0 | 0 | 0 | 0.15765 | 0.3935 | 0.58832
average |  |  |  | 4.592 | 4.622 | 4.716 | 4.932 | 4.737 | 4.6562 | 33178.704 | 32332.704 | 31506.704 | 28650.704 | 25437.0336 | 20343.3681 | 0 | 0 | 0 | 2609.0887 | 9089.1957 | 18130.2296 | 2.1372 | 2.0549 | 1.9604 | 1.7025 | 1.5709 | 1.2819 | 0.68677 | 0.78952 | 0.84869 | 0.97996 | 1 | 1 | 0 | 0 | 0 | 0.076468 | 0.26639 | 0.53137
heating load at different temperatures for home with an ASHP (HPWH heating penalty included)
| temp heat turned on | temp where 36000 BTU used | slope and intercept |  | HPWH load
heating load for 48000 BTU/hr at design temperature | 18 | -20 | -1263.1579 | 22736.8421 | 578.8608 |  | -5 | -10 | -13.5 | -15 | -20 | -25 | -30 | -35 | -40
| 0 | 48000 |  |  |  |  | 29631.4924 | 35947.2819 | 40368.3345 | 42263.0714 | 48578.8608 | 54894.6503 | 61210.4398 | 67526.2293 | 73842.0187
heating load for 42000 BTU/hr at -25'C | 18 | -20 | -1105.2632 | 19894.7368 | 578.8608 |  | -5 | -10 | -13.5 | -15 | -20 | -25 | -30 | -35 | -40
| 0 | 42000 |  |  |  |  | 25999.9135 | 31526.2293 | 35394.6503 | 37052.545 | 42578.8608 | 48105.1766 | 53631.4924 | 59157.8082 | 64684.124
heating load for 36000 BTU/hr at -20'C - the "average home" | 18 | -20 | -947.3684 | 17052.6316 | 578.8608 |  | -5 | -10 | -13.5 | -15 | -20 | -25 | -30 | -35 | -40
| 0 | 36000 |  |  |  |  | 22368.3345 | 27105.1766 | 30420.9661 | 31842.0187 | 36578.8608 | 41315.7029 | 46052.545 | 50789.3872 | 55526.2293
heating load (kW) | [6 empty] | 6.5558 | 7.9441 | 8.9159 | 9.3324 | 10.7207 | 12.1089 | 13.4972 | 14.8855 | 16.2738
heating load for 30000 BTU/hr at -30'C | 18 | -20 | -789.4737 | 14210.5263 | 578.8608 |  | -5 | -10 | -13.5 | -15 | -20 | -25 | -30 | -35 | -40
| 0 | 30000 |  |  | heating load |  | 18736.7556 | 22684.124 | 25447.2819 | 26631.4924 | 30578.8608 | 34526.2293 | 38473.5977 | 42420.9661 | 46368.3345
[5 empty] | heating load (kW) |  | 5.4914 | 6.6483 | 7.4582 | 7.8052 | 8.9622 | 10.1191 | 11.276 | 12.4329 | 13.5898
heating load for 24000 BTU/hr at design temperature | 18 | -20 | -631.5789 | 11368.4211 | 578.8608 |  | -5 | -10 | -13.5 | -15 | -20 | -25 | -30 | -35 | -40
| 0 | 24000 |  |  |  |  | 15105.1766 | 18263.0714 | 20473.5977 | 21420.9661 | 24578.8608 | 27736.7556 | 30894.6503 | 34052.545 | 37210.4398

## GSHPs
GSHP data from manufacturer software
|  |  |  | average kW per hour | [6 empty] | capacity of heat pump | [6 empty] | capacity met by backup resistance heater
brand |  | size | scop | kW at -10 | kW at -13.5 | kW at -15 | kW at -20 | kW at -25 | kW at -30 | kW at -35 | -10 | -13.5 | -15 | -20 | -25 | -30 | -35 | -10 | -13.5 | -15 | -20 | -25 | -30 | -35
Capacity calculated using 36,000 BTU/hr at -20'C
-20'C design temperature
TE 038 Digital with horizontal loop |  | 3t |  | 1.6653 | 1.8428 | 2.0109 | 2.2 | 2.3333 | 2 | 2 | 36000 | 36000 | 36000 | 36000 | 36000 | 36000 | 36000 | 0 | 0 | 0 | 289.4304 | 5026.2725 | 9763.1146 | 14499.9567
Average | for Toronto, Windsor |  |  | 1.6653 | 1.8428 | 2.0109 | 2.2 | 2.3333 | 2 | 2 | 36000 | 36000 | 36000 | 36000 | 36000 | 36000 | 36000 | 0 | 0 | 0 | 289.4304 | 5026.2725 | 9763.1146 | 14499.9567
-25'C design temperature
TE 049 digital with horizontal loop |  | 4t |  | 1.7941 | 1.9673 | 2.1415 | 2.32 | 2.75 | 3.25 | 3 | 48000 | 48000 | 48000 | 48000 | 48000 | 48000 | 48000 | 0 | 0 | 0 | 0 | 0 | 0 | 2499.9567
Average | for Ottawa area |  |  | 1.7941 | 1.9673 | 2.1415 | 2.32 | 2.75 | 3.25 | 3 | 48000 | 48000 | 48000 | 48000 | 48000 | 48000 | 48000 | 0 | 0 | 0 | 0 | 0 | 0 | 2499.9567
-30'C design temperature
TE 049 digital with horizontal loop |  | 4t |  | 1.9101 | 2.0892 | 2.2649 | 2.4597 | 2.8881 | 3.3077 | 3.5 | 48000 | 48000 | 48000 | 48000 | 48000 | 48000 | 48000 | 0 | 0 | 0 | 0 | 0 | 0 | 2499.9567
Average | for Thunder Bay area |  |  | 1.9101 | 2.0892 | 2.2649 | 2.4597 | 2.8881 | 3.3077 | 3.5 | 48000 | 48000 | 48000 | 48000 | 48000 | 48000 | 48000 | 0 | 0 | 0 | 0 | 0 | 0 | 2499.9567
heating load at different temperatures for home with a GSHP (desuperheater load included)
| temp heat turned on | temp where 36000 BTU used | slope and intercept |  | desuperheater load
heating load for 48000 BTU/hr at design temperature | 18 | -20 | -1263.1579 | 22736.8421 | 289.4304 |  | -5 | -10 | -13.5 | -15 | -20 | -25 | -30 | -35 | -40
| 0 | 48000 |  |  |  |  | 29342.062 | 35657.8515 | 40078.9041 | 41973.6409 | 48289.4304 | 54605.2199 | 60921.0094 | 67236.7988 | 73552.5883
heating load for 42000 BTU/hr at -25'C | 18 | -20 | -1105.2632 | 19894.7368 | 289.4304 |  | -5 | -10 | -13.5 | -15 | -20 | -25 | -30 | -35 | -40
| 0 | 42000 |  |  |  |  | 25421.0526 | 30947.3684 | 34815.7895 | 36473.6842 | 42000 | 47526.3158 | 53052.6316 | 58578.9474 | 64105.2632
heating load for 36000 BTU/hr at -20'C - the "average home" | 18 | -20 | -947.3684 | 17052.6316 | 289.4304 |  | -5 | -10 | -13.5 | -15 | -20 | -25 | -30 | -35 | -40
| 0 | 36000 |  |  |  |  | 22078.9041 | 26815.7462 | 30131.5357 | 31552.5883 | 36289.4304 | 41026.2725 | 45763.1146 | 50499.9567 | 55236.7988
heating load (kW) | [6 empty] | 6.471 | 7.8592 | 8.831 | 9.2475 | 10.6358 | 12.0241 | 13.4124 | 14.8007 | 16.189
heating load for 30000 BTU/hr at -30'C | 18 | -20 | -789.4737 | 14210.5263 | 289.4304 |  | -5 | -10 | -13.5 | -15 | -20 | -25 | -30 | -35 | -40
| 0 | 30000 |  |  |  |  | 18447.3252 | 22394.6936 | 25157.8515 | 26342.062 | 30289.4304 | 34236.7988 | 38184.1673 | 42131.5357 | 46078.9041
[7 empty] | 5.4066 | 6.5635 | 7.3733 | 7.7204 | 8.8773 | 10.0342 | 11.1911 | 12.348 | 13.505
heating load for 24000 BTU/hr at design temperature | 18 | -20 | -631.5789 | 11368.4211 | 289.4304 |  | -5 | -10 | -13.5 | -15 | -20 | -25 | -30 | -35 | -40
| 0 | 24000 |  |  |  |  | 14815.7462 | 17973.6409 | 20184.1673 | 21131.5357 | 24289.4304 | 27447.3252 | 30605.2199 | 33763.1146 | 36921.0094

## Input
ETS | Value | Source
upfront costs | 10000 | Steffes and Hydro Quebec unofficial quotes
15-year annualized cost | 1029.6276 | annual payments
% adoption | 24% | IESO DER study BAU+
ETS heating efficiency | 0.78
Charging Input (Kw) | 14 | https://www.steffes.com/wp-content/uploads/2020/12/Steffes-Forced-Air-Furnace.pdf
Charging time (Hr) | 10.989 | Charging time for the heating load requirement = energy draw/power draw
Air Supply Outlet (Fan) (Kw) | 0.84 | supplier notes max 7amp draw for blower and control, assumes 120V https://www.steffes.com/wp-content/uploads/2020/12/Steffes-Forced-Air-Furnace.pdf
Discharging time (Hr) | 13.3712 | based on output capacity and storage capacity https://www.steffes.com/wp-content/uploads/2020/12/Steffes-Forced-Air-Furnace.pdf
size (total kWh stored) | 120 | https://www.steffes.com/wp-content/uploads/2020/12/Steffes-Forced-Air-Furnace.pdf
efficiency | 100%
after diversity maximum demand or coincidence factor | 1 | assuming that during discharge, the fan is running 100% of the time and therefore there is maximum coincidence
Batteries (Tesla Powerwall) | Value | Source
Upfront costs | 21500 | https://kubyenergy.ca/blog/complete-guide-to-tesla-powerwall-in-canada | installation included, $CAN
lifespan (yrs) | 10 | https://kubyenergy.ca/blog/complete-guide-to-tesla-powerwall-in-canada
10-year annualized cost | 2921.1611 | annual payments
% adoption | 27% | IESO DER study BAU+
Size needed (Kwh) | 13.5 | https://www.tesla.com/en_ca/powerwall
Discharge efficiency | 90% | https://www.tesla.com/en_ca/powerwall
discharge time (hours) | 2.43
practical discharge time (hours) | 2
Charging Input (Kw) | 5.5556 | https://www.tesla.com/en_ca/powerwall
Charging Time (Hr) | 2.7 | https://www.ndh-ltd.co.uk/sites/default/files/2020-08/Tesla%20Battery%20User%20Guide.pdf
Power available during discharge (kW) | 5 | https://www.tesla.com/en_ca/powerwall
Electricity draw during charging times (Kwh) | 15 | https://www.ndh-ltd.co.uk/sites/default/files/2020-08/Tesla%20Battery%20User%20Guide.pdf
EV batteries | Value | Source
bidirectional charger | 9950 | $1310 US + $3895 US Integration System converted to CAN$ + HST https://chargers.ford.com/products/ford-charge-station-pro + $2000 installation cost | for estimated installation cost, see https://www.linkedin.com/feed/update/urn:li:activity:7042123940617482240/?commentUrn=urn%3Ali%3Acomment%3A(ugcPost%3A7042123940198064129%2C7042845035297456128)&dashCommentUrn=urn%3Ali%3Afsd_comment%3A(7042845035297456128%2Curn%3Ali%3AugcPost%3A7042123940198064129)
EV/vehicle lifetime | 15 | https://www.cell.com/joule/pdfExtended/S2542-4351(20)30231-2
15-year annualized cost | 1024.4795
% adoption | 31% | IESO DER study BAU+
Battery Size (Kwh) | 98 | https://www.caranddriver.com/ford/f-150-lightning
Discharge efficiency | 90.02% | Calculated value
maximum discharge time (hours) | 9.19
practical discharge time (hours) | 4
Power available during discharge (kW) | 9.6 | https://www.ford.com/trucks/f150/f150-lightning/features/capability/
Power draw during charging times (Kw) | 11.52 | https://insideevs.com/news/508674/battery-capacity-ford-f150-lightning/ (240V*48amps considering a Lvl. 2 Charger, std. Range battery)
Charging time (Hr) 15%-80% | 6.1422 | Calculated value depending on the battery size, considering the battery is at 15% and is charged at 80% of its capacity
ASHP | Value | Source
Upfront cost | 19000 | source from NG vs ASHP v
average lifespan (yr) | 15
15-year annualized cost | 1956.2925
% adoption | 100%
Heating efficiency | 2.7 | based on a minimum HSPF performance of 10.5 in zone IV
Cooling efficiency | 4.01 | https://energy-models.com/tools/how-convert-seer-eer-or-cop-kwton-hspf?page=1
coincidence factor | 1 | conservative assumption
GSHP | Value | Source
Upfront cost | 27000 | based on quotes from 3 installers including Dunsky report on GSHP https://www.hrai.ca/uploads/userfiles/files/Dunsky__HRAI_Benefits%20of%20GSHPs_(2020-10-30)_F.PDF
average lifespan (yr) | 20
20-year annualized cost | 697.4765 | annualized incremental cost over an ASHP
% adoption (high) | 30% | from https://www.hrai.ca/uploads/userfiles/files/Dunsky__HRAI_Benefits%20of%20GSHPs_(2020-10-30)_F.PDF
% adoption (low) | 10% | from https://www.hrai.ca/uploads/userfiles/files/Dunsky__HRAI_Benefits%20of%20GSHPs_(2020-10-30)_F.PDF
Heating efficiency | 3.7 | Dunsky report on GSHP https://www.hrai.ca/uploads/userfiles/files/Dunsky__HRAI_Benefits%20of%20GSHPs_(2020-10-30)_F.PDF
Cooling efficiency | 5.79 | average value for GSHP with heating SCOP of 3.7
coincidence factor | 1 | many GSHPs are designed to run 100% of the time at colder temperatures
electric resistance heating | Value | Source
electric resistance heating (kW) | 15 | output in 5 kW stages
electric resistance heating efficiency | 1
electric resistance heating coincidence factor | 0.9 | conservative estimate based on AC coincidence factor
fossil gas furnace and water heater | Value | Source
home furnace ventilation fan (kW) | 0.84 | max 7amp draw for blower and control, assumes 120V https://www.steffes.com/wp-content/uploads/2020/12/Steffes-Forced-Air-Furnace.pdf (also 6.3 amp for https://keeprite.hvacpartners.com/products/detail/G96VTN )
furnace efficiency | 0.95
furnace coincidence factor | 0.8 | https://www3.dps.ny.gov/W/PSCWeb.nsf/ca7cd46b41e6d01f0525685800545955/06f2fee55575bd8a852576e4006f9af7/$FILE/TRM%20Version%202%20December%2010,%202014.pdf | based on https://www.h2ouse.org/how-often-should-a-furnace-cycle/ https://jpsfurnace.ca/do-high-efficiency-furnaces-run-more-often/
gas water heater efficiency | 67% | based on typical EF values for gas tank water heaters at Home Depot
HPWH | Value | Source
Upfront cost | 3750 | based on quotes from 2 installers
average lifespan (yr) | 15
15-year annualized cost | 386.1104
Efficiency | 3.75 | HPWH: 3.75 Home Depot 50 gal hybrid heat pump water heater https://www.homedepot.ca/product/rheem-proterra-50-gallon-189l-10-year-4-5kw-hybrid-high-efficiency-tank-electric-water-heater/1001586346
Peak power draw (Kw) | 1.23 | https://www.homedepot.ca/product/rheem-proterra-50-gallon-189l-10-year-4-5kw-hybrid-high-efficiency-tank-electric-water-heater/1001586346 | assumes water is heated with the heat pump only
coincidence factor | 0.15 | NRDC heat pump demand flexibility study https://www.aceee.org/sites/default/files/pdf/conferences/hwf/2018/2a-delforge.pdf
coincidence factor when used with GSHP | 0.075 | EWH coincidence factor multiplied by 0.5 because the GSHP desuperheater provides half of the water heating in winter
EWH | Value | Source
Upfront cost | 2200 | conventional electric tank water heater: $2200 based on 3 quotes
average lifespan (yr) | 15
15-year annualized cost | -159.5923 | annualized incremental cost over a HPWH
Efficiency | 0.91 | conventional electric tank water heater: 0.91 https://www.rheem.com/product/marathon-50-gallon-electric-water-heater-with-limited-lifetime-warranty-msr50245c
Peak power draw (Kw) | 4.5 | https://www.homedepot.ca/product/rheem-proterra-50-gallon-189l-10-year-4-5kw-hybrid-high-efficiency-tank-electric-water-heater/1001586346
coincidence factor | 0.2 | NRDC heat pump demand flexibility study https://www.aceee.org/sites/default/files/pdf/conferences/hwf/2018/2a-delforge.pdf
Other | Value | Source
Electrical panel upgrade for ETS and ASHP | 2000 | estimated average cost of upgrade for ASHP only
15-year annualized cost | 205.9685
cost of building envelope upgrades | 10000 | this value needs a reference
15-year annualized cost of building envelope upgrades | 1029.6276 | based on average occupancy of 13 years or so
Average annual heating load (GJ) | 74.6 | Tables 33 and 16 of https://oee.nrcan.gc.ca/corporate/statistics/neud/dpa/menus/trends/comprehensive/trends_res_on.cfm
Average annual cooling load (GJ) | 20.7 | Tables 4 and 27 of https://oee.nrcan.gc.ca/corporate/statistics/neud/dpa/menus/trends/comprehensive/trends_res_on.cfm
Average annual water heating load (GJ) | 10.7 | based on an OEB analysis of gas demand side management options - derived from values in Table 1 on page 31 of https://www.oeb.ca/sites/default/files/OEB-Natural-Gas-DSM-TRM-V5.0-20201112.pdf
GJ/kWh | 0.0036
discount rate | 6% | rate used by Dunsky in DER potential study
Housing stock | value | source
Southwestern Ontario occupied single detached, attached and row housing | 2764290 | https://www12.statcan.gc.ca/census-recensement/2021/dp-pd/prof/details/page.cfm?Lang=E&SearchText=Ontario&DGUIDlist=2021A000235&GENDERlist=1,2,3&STATISTIClist=1&HEADERlist=0
Occupied single detached, attached and row housing in Ontario | 3751515 | https://www12.statcan.gc.ca/census-recensement/2021/dp-pd/prof/details/page.cfm?Lang=E&SearchText=Ontario&DGUIDlist=2021A000235&GENDERlist=1,2,3&STATISTIClist=1&HEADERlist=0
stock of single detached in ON | 3214900 | https://oee.nrcan.gc.ca/corporate/statistics/neud/dpa/showTable.cfm?type=CP&sector=res&juris=on&rn=15&page=0
stock of single attached in ON | 919500 | https://oee.nrcan.gc.ca/corporate/statistics/neud/dpa/showTable.cfm?type=CP&sector=res&juris=on&rn=15&page=0
% built before 1984 (detached) | 46.6% | https://oee.nrcan.gc.ca/corporate/statistics/neud/dpa/showTable.cfm?type=CP&sector=res&juris=on&rn=15&page=0
% built before 1984 (attached) | 33.2% | https://oee.nrcan.gc.ca/corporate/statistics/neud/dpa/showTable.cfm?type=CP&sector=res&juris=on&rn=15&page=0
% using electric resistance heat (detached) | 20% | https://oee.nrcan.gc.ca/corporate/statistics/neud/dpa/showTable.cfm?type=CP&sector=res&juris=on&rn=23&page=0
% using electric resistance heat (attached) | 19.5% | https://oee.nrcan.gc.ca/corporate/statistics/neud/dpa/showTable.cfm?type=CP&sector=res&juris=on&rn=23&page=0
Housing stock | value | source
sources | https://www12.statcan.gc.ca/census-recensement/2021/dp-pd/prof/details/page.cfm?Lang=E&SearchText=Ontario&DGUIDlist=2021A000235&GENDERlist=1,2,3&STATISTIClist=1&HEADERlist=0
https://oee.nrcan.gc.ca/corporate/statistics/neud/dpa/showTable.cfm?type=CP&sector=res&juris=on&rn=15&page=0
region | Ont total | Toronto area | Windsor area | Ottawa area | Thunder Bay | North Bay plus Kapuskasing | source
design temperature |  | -18 | -19 | -24 | -31 | -30 | https://www.nrcan.gc.ca/maps-tools-and-publications/tools/modelling-tools/toolkit-for-air-source-heat-pump-sizing-and-selection/23558
Census Economic Region |  | Toronto, Hamilton-Niagara, Kitchener-Waterloo-Barrie, Muskoka-Kawarthas, Stratford-Bruce Peninsula | Windsor-Sarnia, London | Ottawa, Kingston-Pembroke | Northwest | Northeast
Occupied single detached, attached and row housing | 3751515 | 2480935 | 427055 | 575690 | 79155 | 188675 | From 2021 Census, using economic regions
% using electric resistance heat | 15% | 15% | 15% | 15% | 15% | 15% | weighted average from CEUD Tables 22 and 23
% using heat pumps | 9% | 9% | 9% | 9% | 9% | 9% | weighted average from CEUD Tables 22 and 24
occupied single detached, attached and row housing without a heat pump | 3413878.65 | 2257650.85 | 388620.05 | 523877.9 | 72031.05 | 171694.25
% homes without heat pumps using electric resistance heat | 16.48% | 16.48% | 16.48% | 16.48% | 16.48% | 16.48%
% of Ontario homes | 100% | 66.13% | 11.38% | 15.35% | 2.11% | 5.029%
Avoided costs | value | source
capital cost of wind energy in Ontario per kW (2023) | 1955 | capex value from https://cleanenergycanada.org/report/a-renewables-powerhouse/
project life (years) | 31 | from https://cleanenergycanada.org/report/a-renewables-powerhouse/
cost of capital | 6% | discount rate used by Dunsky in DER study
amortized capital cost of wind energy in Ontario per kW-year | 140.3538
capital cost of 8-hour energy storage in Ontario in 2023 per KW | 4810 | capex value from https://cleanenergycanada.org/report/a-renewables-powerhouse/
project life (years) | 12 | from https://cleanenergycanada.org/report/a-renewables-powerhouse/
cost of capital | 6% | discount rate used by Dunsky in DER study
amortized capital cost of storage per kW-year | 573.7225
Energy storage to wind ratio | 60% | from https://cleanenergycanada.org/report/a-renewables-powerhouse/
reserve margin | 11.8% | NERC 2022-2023 Winter Reliability Assessment p38 https://www.nerc.com/pa/RAPA/ra/Reliability%20Assessments%20DL/NERC_WRA_2022.pdf
energy losses for distribution/transmission | 5.7%
Total cost of wind + storage $/kW-year | 572.6494
avoided/deferred transmission capacity cost ($/MW-day) | 116.8 | Dunsky/IESO DER study Accelerated scenario 2023 https://ieso.ca/en/Sector-Participants/Engagement-Initiatives/Engagements/DER-Potential-Study
transmission losses | 2.8% | IESO customer relations
annualized transmission losses | 30.0176
avoided/deferred distribution capacity costs ($/MW-day) | 4.46 | Dunsky/IESO DER study Accelerated scenario 2023 https://ieso.ca/en/Sector-Participants/Engagement-Initiatives/Engagements/DER-Potential-Study
distribution losses | 2.92% | Alectra direct engagement
annualized transmission losses | 1.1476 | Alectra and IESO direct engagement
total $/kW-year | 603.8146

## regional outcomes
Single Toronto or Windsor home peak power draw analysis for space heating (kW) | [7 empty] | Single Ottawa home peak power draw analysis for space heating (kW) | [7 empty] | Single Northern home peak power draw analysis for space heating (kW)
condition | at -10'C | at -13.5'C | at -15'C | at -20'C | at -25'C | at -30'C |  | condition | at -10'C | at -13.5'C | at -15'C | at -20'C | at -25'C | at -30'C |  | condition | at -10'C | at -13.5'C | at -15'C | at -20'C | at -25'C | at -30'C | at -35
ASHP alone | 3.8546 | 4.5644 | 4.9349 | 6.5902 | 8.9582 | 12.0633 |  | ASHP alone | 3.7493 | 4.3329 | 4.663 | 5.9954 | 8.1336 | 11.6075 |  | ASHP alone | 3.7493 | 4.3329 | 4.663 | 5.9954 | 8.1336 | 11.6075 | 15
ASHP with ETS for peak hours | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 |  | ASHP with ETS for peak hours | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 |  | ASHP with ETS for peak hours | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84
ASHP powered with home batteries | 0 | 0 | 0 | 1.5902 | 3.9582 | 7.0633 |  | ASHP powered with home batteries | 0 | 0 | 0 | 0.99538 | 3.1336 | 6.6075 |  | ASHP powered with home batteries | 0 | 0 | 0 | 0.99538 | 3.1336 | 6.6075 | 10
ASHP powered with EV battery | 0 | 0 | 0 | 0 | 0 | 2.4633 |  | ASHP powered with EV battery | 0 | 0 | 0 | 0 | 0 | 2.0075 |  | ASHP powered with EV battery | 0 | 0 | 0 | 0 | 0 | 2.0075 | 5.4
ASHP after retrofits | 3.1537 | 3.6492 | 4.0024 | 5.5979 | 7.4009 | 9.9699 |  | ASHP after retrofits | 3.2259 | 3.8181 | 4.1274 | 5.4102 | 7.0024 | 9.8421 |  | ASHP after retrofits | 3.1378 | 3.6245 | 3.9 | 5.012 | 6.5573 | 10.6661 | 15
GSHP alone | 1.6653 | 1.8428 | 2.0109 | 2.2848 | 3.8064 | 4.8614 |  | GSHP alone | 1.7941 | 1.9673 | 2.1415 | 2.32 | 2.75 | 3.25 |  | GSHP alone | 1.9101 | 2.0892 | 2.2649 | 2.4597 | 2.8881 | 3.3077 | 4.2327
improved ASHP model | 3.3638 | 4.3123 | 4.625 | 5.9852 | 8.5372 | 11.6439 |  | improved ASHP model | 3.4311 | 4.0001 | 4.3059 | 5.2885 | 6.29 | 6.346 |  | improved ASHP model | 3.4311 | 4.0001 | 4.3059 | 5.2885 | 6.29 | 6.346 | 15
Fossil gas heated home | 0.672 | 0.672 | 0.672 | 0.672 | 0.672 | 0.672 |  | fossil gas heated home | 0.672 | 0.672 | 0.672 | 0.672 | 0.672 | 0.672 |  | fossil gas heated home | 0.672 | 0.672 | 0.672 | 0.672 | 0.672 | 0.672 | 0.672
electric resistance space heating | 7.1497 | 8.0243 | 8.3991 | 9.6486 | 10.898 | 12.1475 |  | electrically heated home | 7.1497 | 8.0243 | 8.3991 | 9.6486 | 10.898 | 12.1475 |  | electrically heated home | 7.1497 | 8.0243 | 8.3991 | 9.6486 | 10.898 | 12.1475 | 13.397
Single Toronto or Windsor home peak power draw analysis for space and water heating (kW) | [7 empty] | Single Ottawa home peak power draw analysis for space and water heating (kW) | [7 empty] | Single Northern home peak power draw analysis for space and water heating (kW)
condition | at -10'C | at -13.5'C | at -15'C | at -20'C | at -25'C | at -30'C |  | condition | at -10'C | at -13.5'C | at -15'C | at -20'C | at -25'C | at -30'C |  | condition | at -10'C | at -13.5'C | at -15'C | at -20'C | at -25'C | at -30'C | at -35'C
ASHP +HPWH | 4.0391 | 4.7489 | 5.1194 | 6.7747 | 9.1427 | 12.2478 |  | ASHP +HPWH | 3.9338 | 4.5174 | 4.8475 | 6.1799 | 8.3181 | 11.792 |  | ASHP +HPWH | 3.9338 | 4.5174 | 4.8475 | 6.1799 | 8.3181 | 11.792 | 15.1845
ASHP with ETS for peak hours + HPWH | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 |  | ASHP with ETS for peak hours + HPWH | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 |  | ASHP with ETS for peak hours + HPWH | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245
ASHP/HPWH powered with home batteries | 0 | 0 | 0.11944 | 1.7747 | 4.1427 | 7.2478 |  | ASHP/HPWH powered with home batteries | 0 | 0 | 0 | 1.1799 | 3.3181 | 6.792 |  | ASHP/HPWH powered with home batteries | 0 | 0 | 0 | 1.1799 | 3.3181 | 6.792 | 10.1845
ASHP/HPWH powered with EV battery | 0 | 0 | 0 | 0 | 0 | 2.6478 |  | ASHP/HPWH powered with EV battery | 0 | 0 | 0 | 0 | 0 | 2.192 |  | ASHP/HPWH powered with EV battery | 0 | 0 | 0 | 0 | 0 | 2.192 | 5.5845
GSHP/HPWH | 1.7576 | 1.935 | 2.1031 | 2.3771 | 3.8987 | 4.9537 |  | GSHP/HPWH | 1.8864 | 2.0595 | 2.2338 | 2.4122 | 2.8422 | 3.3422 |  | GSHP/HPWH | 2.0024 | 2.1815 | 2.3572 | 2.5519 | 2.9803 | 3.3999 | 4.3249
Fossil gas space and water heating | 0.672 | 0.672 | 0.672 | 0.672 | 0.672 | 0.672 |  | fossil gas space and water heaters | 0.672 | 0.672 | 0.672 | 0.672 | 0.672 | 0.672 |  | fossil gas space and water heaters | 0.672 | 0.672 | 0.672 | 0.672 | 0.672 | 0.672 | 0.672
Electric resistance space and water heating | 8.0497 | 8.9243 | 9.2991 | 10.5486 | 11.798 | 13.0475 |  | electric resistance space and water heating | 8.0497 | 8.9243 | 9.2991 | 10.5486 | 11.798 | 13.0475 |  | electric resistance space and water heating | 8.0497 | 8.9243 | 9.2991 | 10.5486 | 11.798 | 13.0475 | 14.297
Toronto and Windsor area homes increased peak power draw analysis for space and water heating (GW) | [7 empty] | Ottawa area homes increased peak power draw analysis for space and water heating (GW) | [7 empty] | Northern area homes peak power draw analysis for space and water heating (GW)
These values show the increase in peak power draw when homes currently heated with fossil gas and electric resistance heaters shift to heat pumps
condition | % adoption | at -10'C | at -13.5'C | at -15'C | at -20'C | at -25'C | at -30'C | condition | % adoption | at -10'C | at -13.5'C | at -15'C | at -20'C | at -25'C | at -30'C | condition | % adoption | at -10'C | at -13.5'C | at -15'C | at -20'C | at -25'C | at -30'C | at -35'C
ASHP +HPWH | 100% | 5.6921 | 7.189 | 8.006 | 11.8413 | 17.5627 | 25.2346 | ASHP +HPWH | 100% | 1.0717 | 1.3019 | 1.4425 | 2.0326 | 3.0448 | 4.7569 | ASHP +HPWH | 100% | 0.4986 | 0.6057 | 0.67109 | 0.94562 | 1.4166 | 2.2131 | 2.9897
ASHP with ETS for peak hours + HPWH | 24% | 3.7775 | 4.8236 | 5.4053 | 8.1893 | 12.4068 | 18.1066 | ASHP with ETS for peak hours + HPWH | 24% | 0.24487 | 0.3443 | 0.41876 | 0.75933 | 1.4208 | 2.614 | ASHP with ETS for peak hours + HPWH | 24% | 0.11392 | 0.16018 | 0.19482 | 0.35327 | 0.66098 | 1.2161 | 1.7562
ASHP/HPWH powered with home batteries | 27% | 2.8062 | 3.7959 | 4.4335 | 8.2688 | 13.9902 | 21.6621 | ASHP/HPWH powered with home batteries | 27% | 0.0078506 | 0.10037 | 0.17061 | 0.73476 | 1.803 | 3.6553 | ASHP/HPWH powered with home batteries | 27% | 0.0036524 | 0.046697 | 0.079375 | 0.34183 | 0.83883 | 1.7006 | 2.5401
ASHP/HPWH powered with EV battery | 31% | 2.3786 | 3.2932 | 3.8063 | 6.2837 | 10.0625 | 17.3593 | ASHP/HPWH powered with EV battery | 31% | -0.046779 | 0.036537 | 0.10115 | 0.40043 | 0.99099 | 2.551 | ASHP/HPWH powered with EV battery | 31% | -0.021763 | 0.016998 | 0.04706 | 0.18629 | 0.46104 | 1.1868 | 2.0228
GSHP/HPWH | 100% | -0.34545 | -0.25735 | 0.023991 | 0.20394 | 3.6856 | 5.9322 | GSHP/EWH | 100% | -0.00090687 | 0.014279 | 0.073189 | 0.058801 | 0.17617 | 0.33022 | GSHP/EWH | 100% | 0.027857 | 0.036367 | 0.064129 | 0.061399 | 0.11561 | 0.16769 | 0.34294
Ontario single home weighted average power draw (kW)
These values show the geographically weighted average power demand for a single family home in Ontario
| at local morning minimum | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp)
ASHP +HPWH | 6.985 | 5.0023 | 5.3875 | 9.9806
ASHP with ETS for peak hours + HPWH | 1.0245 | 1.0245 | 1.0245 | 1.0245
ASHP/HPWH powered with batteries | 2.0944 | 0.13833 | 0.49693 | 4.9806
ASHP/HPWH powered with EV battery | 0.11024 | 0 | 0 | 0.73507
GSHP/HPWH | 2.4421 | 2.1118 | 2.1738 | 3.8437
NG space and water heater | 0.672 | 0.672 | 0.672 | 0.672
electric resistance space and water heating | 10.6079 | 9.2197 | 9.527 | 12.1682

## Fig 1
power draw for an average single family home in Ontario |  | sourced from "regional outcomes sheet"
local afternoon maximum
ASHP +HPWH | 5.0023
ASHP with ETS for peak hours + HPWH | 1.0245
ASHP/HPWH powered with home batteries | 0.13833
ASHP/HPWH powered with EV battery | 0
GSHP/HPWH | 2.1118
Fossil gas space and water heating | 0.672
Electric resistance space and water heating | 9.2197

## Fig 2
power draw for an average single family home in Ontario |  | sourced from "regional outcomes sheet"
local afternoon maximum
ASHP +HPWH | 5.0023
ASHP with ETS for peak hours + HPWH | 1.0245
ASHP/HPWH powered with home batteries | 0.13833
ASHP/HPWH powered with EV battery | 0
GSHP/HPWH | 2.1118
Fossil gas space and water heating | 0.672
Electric resistance space and water heating | 9.2197

## Fig 3
power draw for an average single family home in Ontario
At local afternoon maximum
current heating/water heating power draw | 8.7931
| % adoption | power draw | net increase
existing mix of space and water heating systems |  | 8.7931
100% of homes have ASHPs and HPWHs |  | 18.7663 | 9.9731
ASHP/HPWH + ETS | 100% | 3.8434 | -4.9497
ASHP/HPWH + home batteries | 100% | 0.51894 | -8.2742
ASHP/HPWH + EV battery | 100% | 0 | -8.7931
100% of homes have GSHPs and HPWHs | 100% | 7.9223 | -0.87083
| Ontario single home weighted average power draw (kW) |  |  |  | sourced from "regional outcomes sheet"
| at local morning minimum | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp)
ASHP +HPWH | 6.985 | 5.0023 | 5.3875 | 9.9806
ASHP with ETS for peak hours + HPWH | 1.0245 | 1.0245 | 1.0245 | 1.0245
ASHP/HPWH powered with batteries | 2.0944 | 0.13833 | 0.49693 | 4.9806
ASHP/HPWH powered with EV battery | 0.11024 | 0 | 0 | 0.73507
GSHP/EWH | 2.4421 | 2.1118 | 2.1738 | 3.8437
NG space and water heater | 0.672 | 0.672 | 0.672 | 0.672
electric resistance space and water heating | 10.6079 | 9.2197 | 9.527 | 12.1682

## Fig 4
power draw for an average single family home in Ontario |  | sourced from "regional outcomes sheet"
local afternoon maximum
ASHP +HPWH | 5.0023
ASHP with ETS for peak hours + HPWH | 1.0245
ASHP/HPWH powered with home batteries | 0.13833
ASHP/HPWH powered with EV battery | 0
GSHP/HPWH | 2.1118
Fossil gas space and water heating | 0.672
Electric resistance space and water heating | 9.2197

## Fig 5
power draw for an average single family home in Ontario |  | sourced from "regional outcomes sheet"
local afternoon maximum
ASHP +HPWH | 5.0023
ASHP with ETS for peak hours + HPWH | 1.0245
ASHP/HPWH powered with home batteries | 0.13833
ASHP/HPWH powered with EV battery | 0
GSHP/HPWH | 2.1118
Fossil gas space and water heating | 0.672
Electric resistance space and water heating | 9.2197

## Fig 6
power draw for an average single family home in Ontario |  |  | sourced from "regional outcomes sheet"
| extreme winter day | local afternoon maximum
ASHP +HPWH | 9.9806 | 5.0023
ASHP with ETS for peak hours + HPWH | 1.0245 | 1.0245
ASHP/HPWH powered with home batteries | 4.9806 | 0.13833
ASHP/HPWH powered with EV battery | 0.73507 | 0
GSHP/HPWH | 3.8437 | 2.1118
Fossil gas space and water heating | 0.672 | 0.672
Electric resistance space and water heating | 12.1682 | 9.2197

## Fig 7
power draw for an average single family home in Ontario |  | sourced from "regional outcomes sheet" | Annual kWh energy use for space and water heating in single family homes
| local afternoon maximum |  |  | Annual kWh energy use for space heating | Annual GJ energy use for space heating | Annual GJ energy use for water heating | Annual GJ heating penalty for HPWH | assumptions
ASHP +HPWH | 5.0023 |  | ASHP +HPWH | 9017.9012 | 27.6296 | 2.8533 | 1.9815 | includes heating penalty but not cooling benefit
ASHP with ETS for peak hours + HPWH | 1.0245 |  | ASHP with ETS for peak hours + HPWH | 12391.4824 | 39.7745 | 2.8533 | 1.9815 | ETS used 6 hours/day 5 days a week during heating season
ASHP/HPWH powered with home batteries | 0.13833 |  | ASHP/HPWH powered with home batteries | 9081.8587 | 27.8599 | 2.8533 | 1.9815 | batteries used 2 hours/day 7 days a week during heating season
ASHP/HPWH powered with EV battery | 0 |  | ASHP/HPWH powered with EV battery | 9145.5029 | 28.089 | 2.8533 | 1.9815 | EV battery used 4 hours/day 7 days a week during heating season
GSHP/HPWH | 2.1118 |  | GSHP/HPWH | 6197.7227 | 20.1622 | 2.1496 |  | assumes 50% of water heater heat comes from EWH, 25% from GSHP in winter, 25% free heat from GSHP in summer
Fossil gas space and water heating | 0.672 |  | Fossil gas space and water heating | 26249.0181 | 78.5263 | 15.9701
Electric resistance space and water heating | 9.2197 |  | Electric resistance space and water heating | 23988.4005 | 74.6 | 11.7582

## customer cost (hidden)
Electricity Rates
| Toronto Hydro | Toronto Hydro | Toronto Hydro | Toronto Hydro | Toronto Hydro | Toronto Hydro | Toronto Hydro
source | https://www.torontohydro.com/for-home/rates | TOU off peak | TOU on peak | TOU mid peak | ULO overnight | ULO on peak | ULO mid peak
time-averaged TOU rate ($/kWh) | 0.09275 | 0.074 | 0.151 | 0.102 | 0.024 | 0.24 | 0.102
electricity distribution ($/kWh) | 0.00304 | 0.00304 | 0.00304 | 0.00304 | 0.00304 | 0.00304 | 0.00304
electricity transmission charge ($/kWh) | 0.01891 | 0.01891 | 0.01891 | 0.01891 | 0.01891 | 0.01891 | 0.01891
regulatory charges ($/kWh) | 0.0052 | 0.0052 | 0.0052 | 0.0052 | 0.0052 | 0.0052 | 0.0052
HST | 13% | 13% | 13% | 13% | 13% | 13% | 13%
Ontario Electricity Rebate | 11.7% | 11.7% | 11.7% | 11.7% | 11.7% | 11.7% | 11.7%
line loss adjustment factor | 1.0295 | 1.0295 | 1.0295 | 1.0295 | 1.0295 | 1.0295 | 1.0295
total electricity variable cost ($/kWh) | 0.12316 | 0.1039 | 0.183 | 0.13267 | 0.052543 | 0.27442 | 0.13267
weekdays when peak reduction is used for heating | 108.631
weekend days when peak reduction used for heating | 43.4524
weekdays when peak reduction used for everything | 260.7143
weekend days when peak reduction used for everything | 104.2857
| annualized cost | kW for charging | hours charging | hours discharge | annual savings with TOU | annual savings with ULO |  | assumptions
ETS | 1029.6276 | 14 | NA | 13.3712 | -534.771 | 181.6733 |  | used every weekday during heating season | based on total seaonal heating load
battery | 2921.1611 | 5.5556 | 2.2222 | 2 | 35.2233 | 147.1182 |  | used year round to offset peaks | based on hours of use per day
EV bidirectional charger | 1024.4795 | 11.52 | 4.8 | 4 | 60.8148 | 317.7752 |  | used year round to offset peaks | based on hours of use per day
assumptions
equipment is only used during peak hours
equipment is charged long enough to cover the six peak hours or the max amount of output time, whichever is less
equipment is used for 5 months of the year
assumes batteries are used all months of the year for heating and for other applications during peak hours
batteries are only used on weekdays with TOU but used on weekends with ULO
assumes heating use is distributed evenly throughout the day

## Fig 8
| Ontario single home weighted average power draw (kW) |  |  |  | weighted change to ON power draw (electric/furnace subtracted |  |  |  | annualized equipment cost $ |  |  | avg utility cost for the KW saved with wind + storage |  |  |  |  | cost savings by investing in mitigation measures over utility upgrades
| at local morning minimum | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp) | at local morning minimum | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp)
[12 empty] | at local morning minimum | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp) |  | at local afternoon maximum | extreme cold (5'C below design temp)
ASHP +HPWH | 6.985 | 5.0023 | 5.3875 | 9.9806 | 4.2545 | 2.6584 | 2.9629 | 6.7464
ASHP with ETS for peak hours + HPWH | 1.0245 | 1.0245 | 1.0245 | 1.0245 | -1.1696 | -0.96138 | -1.0075 | -1.4037 | 1029.6276 | 1029.6276 | 1029.6276 | 3599.055 | 2401.8649 | 2634.467 | 5407.8285 | ETS | 1372.2372 | 4378.2008
ASHP/HPWH powered with batteries | 2.0944 | 0.13833 | 0.49693 | 4.9806 | -0.19598 | -1.7678 | -1.4876 | 2.1964 | 2921.1611 | 2921.1611 | 2921.1611 | 2953.0195 | 2936.9479 | 2953.0195 | 3019.0688 | Home battery | 15.7868 | 97.9077
ASHP/HPWH powered with EV battery | 0.11024 | 0 | 0 | 0.73507 | -2.0016 | -1.8937 | -1.9398 | -1.667 | 1024.4795 | 1024.4795 | 1024.4795 | 4151.095 | 3020.4721 | 3253.0742 | 5582.5884 | EV battery | 1995.9926 | 4558.1089
GSHP/HPWH | 2.4421 | 2.1118 | 2.1738 | 3.8437 | 0.12041 | 0.028024 | 0.038424 | 1.1619 | 537.8842 | 537.8842 | 537.8842 | 2743.0838 | 1745.3611 | 1940.4768 | 3705.5325 | GSHP | 1207.4769 | 3167.6484
NG space and water heater | 0.672 | 0.672 | 0.672 | 0.672
electric resistance space and water heating | 10.6079 | 9.2197 | 9.527 | 12.1682

## Table 2
Table 2: Cost of Reducing ASHP Power Demand During Ontario Winter Peak Demand Hour by 1 kW Using Available Technologies
Column1 | ETS | home battery | EV battery | GSHP/HPWH
capacity (kWh) | 120 | 13.5 | 98 | na
lifetime (yrs) | 15 | 10 | 15 | 20
upfront cost ($) | 10000 | 21500 | 9950 | 8000
annualized cost ($) | 1029.6276 | 2921.1611 | 1024.4795 | 697.4765
maximum duration of peak reduction (hrs) | 13.3712 | 2.43 | 9.19 | na
kW saved in 2023/24 winter peak | 3.9778 | 4.864 | 5.0023 | 2.8906
annualized cost per W-year in winter 2023/24 peak | 258.8423 | 600.5689 | 204.801 | 241.2947
cost savings/installation/yr | 1372.2372 | 15.7868 | 1995.9926 | 1047.8847
kW saved in extreme cold event | 8.9561 | 5 | 9.2455 | 6.1369
annualized cost per kW-year in extreme cold event | 114.9637 | 584.233 | 110.808 | 113.6534
annualized capital cost per kW of wind + storage | 603.8146 | 603.8146 | 603.8146 | 603.8146
cost savings/household/yr | 4378.2008 | 97.9077 | 4558.1089 | 3008.0561

## assumptions
assumptions
ducted central system, assumes that the ductwork can accommodate the increased air flow
average 36,000 BTU/hr heat loss at -20'C
sized for heating at design temperature according to NRCan Heat Pump sizing and selection guide, option D https://www.nrcan.gc.ca/sites/nrcan/files/canmetenergy/pdf/ASHP%20Sizing%20and%20Selection%20Guide%20(EN).pdf
design temperatures for cities based on NRCan heat pump sizing tool
| Toronto | -18'C
| Thunder Bay | -31
| Windsor | -19
| Ottawa | -24
| Kapuskasing | -34
| North Bay | -28
indoor air temperature of 20-21'C
where heat pump data was not available at lower temperatures, the average power draw at higher temperatures was used and the capacity was linearly extrapolated from the capacity at higher temperatures
assume the backup heater comes on once the heating load exceeds the heat pump capacity to generate the heating shortfall
assumes max 10 KW backup heater for Southern areas, and 15 kW backup heater for Northern areas (Thunder Bay, Kapuskasing, North Bay)
when modelling ASHP at -35'C, assumed only backup heater was providing heat (12 kW used for Northern areas when retrofits are included)
used IESO weather station cities
used Economic region census data for Ontario and for Northern cities (Thunder Bay = Northwest region, North Bay + Kapuskasing = Northeast region)
homes heated with propane, oil and other fuels are treated as though they were heated with NG
assumption that improved ASHP model has a seasonal COP of 3.0
assumed homes use the same heating type to heat water as they do for space heating (eg heat pumps, electric resistance, gas)
heating load does not including effect of heating penalty from HPWH
existing gas, heat pump and electric resistance heating are evenly distributed across the province
Ontario only needs new infrastructure if the demand for electricity increases during the peak demand hour, not the coldest hour if it is a non-peak hour
internal gains not included in heating load calculations
GSHP minimum loop temp is 32'F
GSHP includes desuper heater that provides 50% of the domestic hot water heating, half of which is free heat in summer
the coincidence factor for the HPWH with GSHP has halved to account for the fact that the GSHP provides half of the domestic hot water
ETS used 6 hours/day 5 days a week during heating season
batteries used 2 hours/day 5 days a week during heating season
EV battery used 4 hours/day 5 days a week during heating season
HPWH total energy use is for the entire year and includes winter heating penalty but does not include summer heating benefit
EWH total energy use is for the entire year but GSHP provides half of the heat (free waste heat in summer, at GSHP efficiency in winter)
HPWH are adopted alongside ASHPs
all installed heat pumps in 2023 are ASHP and have a HPWH
when ETS is in use, it runs continuously during the peak hour (i.e. coincidence factor of 1)
assumed coincidence factor of 1 for ASHP and GSHP
ASHP defrost cycles do not occur during peak demand hours
for steady adoption, homes with electric resistance heat and gas heat convert to heat pumps at the same rate
for steady adoption, homes with ASHP/HPWH
for 100% ASHP adoption, the increase in power draw is over current levels with 9% heat pump adoption
when all peak mitigation technologies are used ON homes, they are adopted in the same relative rates based on IESO/Dunsky modeled adoption assumptions
batteries and EV batteries are used by the customer to save money during peak times through the entire year
Toronto = Hamilton-Niagara, Kitchener-Waterloo-Barrie, Muskoka-Kawarthas, Stratford-Bruce Peninsula, Toronto
Windsor = London, Windsor-Sarnia
Ottawa = Kingston-Pembroke, Ottawa
Thunder Bay = Northwest
North Bay + Kapuskasing = Northeast

## formulas
Formulas used
See report for further details
ASHP
GSHP
ASHP with home or EV batteries
kWh energy use
Cost of meeting a 1 kW increase in demand with wind energy and utility-scale storage
Row Number | Input | Cost | Source
1 | Capital Cost of Wind Energy | $1,955 per kW[1] | Clean Energy Canada
2 | Annualized Capital Cost of Wind Energy | $140 per kW-Year[2]
3 | Capital Cost of 8-Hour Energy Storage | $4,810 per kW[3] | Clean Energy Canada
4 | Annualized Capital Cost of 8-Hour Storage | $574 per kW-Year[4]
5 | Annualized Capital Cost of 1 kW of wind and storage capacity | $484 per kW-Year[5] | Clean Energy Canada
6 | Generation Reserve Margin Adder | $57 per kW-Year[6] | North American Electric Reliability Corporation
7 | Transmission Loss Adder | $15 per kW-Year[7] | IESO
8 | Distribution Loss Adder | $16 per kW-Year[8] | Alectra
9 | Total Annualized Capital Cost of Wind and Storage Capacity to meet 1 kW increase in customer demand [Rows: 5+6+7+8] | $573 per kW-Year
10 | Annualized Capital Cost of Additional Transmission capacity including transmission loss adder | $30 per kW-Year[9] | Dunsky Report for IESO
11 | Annualized Capital Cost of Additional Distribution capacity including distribution loss adder | $1 per kW-Year[10] | Dunsky Report for IESO
12 | Total Annualized Capital Cost of Meeting 1 kW increase in consumer demand [Rows: 9+10+11] | $604 per kW-Year
[1] See the Workbook for Clean Energy Canada’s A Renewables Powerhouse. https://cleanenergycanada.org/report/a-renewables-powerhouse
[2] According to Clean Energy Canada’s Workbook, the expected economic life of new wind turbines is 31 years. We have amortized the capital cost over 31 years using a 6% cost of capital.
[3] See the Workbook for Clean Energy Canada’s A Renewables Powerhouse.
[4] According to Clean Energy Canada’s Workbook, the expected life of a new energy storage facility is 12 years. We have amortized the capital cost over 12 years using a 6% cost of capital.
[5] The Clean Energy Canada report uses an energy storage to wind ratio of 60%. The combined cost is $140 per kW-Year + [$574 per kW-Year x 0.6]. Email from Evan Pivnick, Program Manager, Clean Energy Canada to Jack Gibbons, Ontario Clean Air Alliance (March 20, 2023).
[6] Ontario’s generation reserve margin for the winter of 2022-23 was 11.8%. The reserve margin is the amount of capacity the grid needs to have available over and above the peak demand under normal weather conditions. North American Electric Reliability Corporation, 2022-2023 Winter Reliability Assessment, (November 2022), page 38.
[7] To meet a 1 kW increase in customer demand, wind generation and storage capacity must be increased by 2.8% to account for the 2.8% energy loss in the transmission system during the winter peak. Email from Customer Relations, IESO to Jack Gibbons, Ontario Clean Air Alliance, (February 13, 2023).
[8] To meet a 1 kW increase in customer demand, wind generation and storage capacity must be increased to account for the energy loss in the distribution system during the winter peak. Alectra Utilities’ distribution losses during the peak winter hour are 2.92%. Email from Tom Wasik, Vice President, Asset Management, Alectra Utilities, to Jack Gibbons, Ontario Clean Air Alliance, (March 7, 2023).
[9] According to a report for the IESO, the cost of new transmission capacity is $116.80 per MW-day. According to Colin Campbell of the IESO, this cost can be converted to an annual cost by multiplying it by 250 days. We have also increased the cost by 1.028 to account for the need for additional capacity to account for transmission losses. Dunsky, Ontario’s Distributed Energy Resources Potential Study, Vol 2, (2022), page 29; and Email from Colin Campbell, IESO to Jack Gibbons, Ontario Clean Air Alliance, (January 19, 2023).
[10] According to a report for the IESO, the cost of new distribution capacity is $4.46 per MW-day. According to Colin Campbell of the IESO, this cost can be converted to an annual cost by multiplying it by 250 days. We have also increased the cost by 1.0292 to account for the need for additional capacity to account for distribution losses. Dunsky, Ontario’s Distributed Energy Resources Potential Study, Vol 2, (2022), page 29; and Email from Colin Campbell, IESO to Jack Gibbons, Ontario Clean Air Alliance, (January 19, 2023).

## ON power outcomes (hidden)
Figure 1
| local afternoon maximum |  |  |  |  | extreme winter day | local afternoon maximum
ASHP +HPWH | 5.0023 |  | 0.2048 |  | ASHP +HPWH | 9.9806 | 5.0023
ASHP with ETS for peak hours + HPWH | 1.0245 |  | 1.8431 |  | ASHP with ETS for peak hours + HPWH | 1.0245 | 1.0245 | 0.2048
ASHP/HPWH powered with home batteries | 0.13833 | 0.027653 |  |  | ASHP/HPWH powered with home batteries | 4.9806 | 0.13833
ASHP/HPWH powered with EV battery | 0 |  |  |  | ASHP/HPWH powered with EV battery | 0.73507 | 0
GSHP/HPWH | 2.1118 |  | 0.42216 |  | GSHP/HPWH | 3.8437 | 2.1118
Fossil gas space and water heating | 0.672 |  |  |  | Fossil gas space and water heating | 0.672 | 0.672
Electric resistance space and water heating | 9.2197 |  |  |  | Electric resistance space and water heating | 12.1682 | 9.2197
| Annual kWh energy use for space heating | Annual GJ energy use for space heating | Annual GJ energy use for water heating | Annual GJ heating penalty for HPWH | assumptions
ASHP +HPWH | 9017.9012 | 27.6296 | 2.8533 | 1.9815 | includes heating penalty but not cooling benefit
ASHP with ETS for peak hours + HPWH | 12391.4824 | 39.7745 | 2.8533 | 1.9815 | ETS used 6 hours/day 5 days a week during heating season
ASHP/HPWH powered with home batteries | 9081.8587 | 27.8599 | 2.8533 | 1.9815 | batteries used 2 hours/day 7 days a week during heating season
ASHP/HPWH powered with EV battery | 9145.5029 | 28.089 | 2.8533 | 1.9815 | EV battery used 4 hours/day 7 days a week during heating season
GSHP/HPWH | 6197.7227 | 20.1622 | 2.1496 |  | assumes 50% of water heater heat comes from EWH, 25% from GSHP in winter, 25% free heat from GSHP in summer
Fossil gas space and water heating | 26249.0181 | 78.5263 | 15.9701
Electric resistance space and water heating | 23988.4005 | 74.6 | 11.7582

## steady adoption (hidden)
Ontario increased peak hour power draw for space and water heating (GW) | [9 empty] | difference between projected winter peak (21.3 GW) and 2022 APO winter 2023/24 effective capacity (29.7 GW)
8.4
condition | year | % adoption | at local morning miniumum | 2023/24 peak hour | at local evening minimum | extreme cold (5'C below design temp) | 2023/24 peak hour with all tech | morning min with tech in 50% of BAU+ adoption | extreme cold with all tech | current peak | current maximum capacity
100% gas and electric |  | 0% | 8.6652 | 7.8068 | 7.9968 | 9.63 | 7.8068 | 8.6652 | 9.63 | 8.7931 | 17.1931
current mix | 2023 | 9% | 10.2437 | 8.7931 | 9.0961 | 12.1331 | 8.0868 | 9.3039 | 10.8949 | 8.7931 | 17.1931
ASHP +HPWH | 2024 | 15.07% | 11.3083 | 9.4584 | 9.8375 | 13.8214 | 8.2798 | 9.7439 | 11.7663 | 8.7931 | 17.1931
ASHP +HPWH | 2025 | 21.14% | 12.373 | 10.1236 | 10.579 | 15.5096 | 8.4727 | 10.1838 | 12.6377 | 8.7931 | 17.1931
ASHP +HPWH | 2026 | 27.21% | 13.4376 | 10.7888 | 11.3204 | 17.1978 | 8.6657 | 10.6238 | 13.509 | 8.7931 | 17.1931
ASHP +HPWH | 2027 | 33.28% | 14.5022 | 11.4541 | 12.0618 | 18.886 | 8.8586 | 11.0638 | 14.3804 | 8.7931 | 17.1931
ASHP +HPWH | 2028 | 39.35% | 15.5669 | 12.1193 | 12.8033 | 20.5742 | 9.0515 | 11.5038 | 15.2518 | 8.7931 | 17.1931
ASHP +HPWH | 2029 | 45.42% | 16.6315 | 12.7846 | 13.5447 | 22.2624 | 9.2445 | 11.9438 | 16.1232 | 8.7931 | 17.1931
ASHP +HPWH | 2030 | 51.49% | 17.6961 | 13.4498 | 14.2861 | 23.9506 | 9.4374 | 12.3838 | 16.9945 | 8.7931 | 17.1931
ASHP +HPWH | 2031 | 57.56% | 18.7608 | 14.1151 | 15.0275 | 25.6388 | 9.6304 | 12.8237 | 17.8659 | 8.7931 | 17.1931
ASHP +HPWH | 2032 | 63.63% | 19.8254 | 14.7803 | 15.769 | 27.327 | 9.8233 | 13.2637 | 18.7373 | 8.7931 | 17.1931
ASHP +HPWH | 2033 | 69.7% | 20.89 | 15.4455 | 16.5104 | 29.0153 | 10.0163 | 13.7037 | 19.6086 | 8.7931 | 17.1931
ASHP +HPWH | 2034 | 75.77% | 21.9547 | 16.1108 | 17.2518 | 30.7035 | 10.2092 | 14.1437 | 20.48 | 8.7931 | 17.1931
ASHP +HPWH | 2035 | 81.84% | 23.0193 | 16.776 | 17.9933 | 32.3917 | 10.4021 | 14.5837 | 21.3514 | 8.7931 | 17.1931
ASHP +HPWH | 2036 | 87.91% | 24.0839 | 17.4413 | 18.7347 | 34.0799 | 10.5951 | 15.0237 | 22.2228 | 8.7931 | 17.1931
ASHP +HPWH | 2037 | 93.98% | 25.1486 | 18.1065 | 19.4761 | 35.7681 | 10.788 | 15.4636 | 23.0941 | 8.7931 | 17.1931
ASHP + HPWH | 2038 | 100% | 26.2044 | 18.7663 | 20.2114 | 37.4424 | 10.9187 | 15.7617 | 23.6844 | 8.7931 | 17.1931
Ontario increased peak hour power draw for space and water heating (GW) from 2023 levels at afternoon maximum
condition | year | % adoption | no tech | with tech in 50% of homes | no tech morning | with tech in 50% of homes | extreme with tech
100% gas and electric |  | 0% | 7.8068 | 7.8068 | 8.6652 | 8.6652 | 9.63
current mix | 2023 | 9% | 8.7931 | 8.0868 | 10.2437 | 9.3039 | 10.8949
ASHP +HPWH | 2024 | 15.2% | 9.4726 | 8.2798 | 11.3083 | 9.7439 | 11.7663
ASHP +HPWH | 2025 | 21.4% | 10.1521 | 8.4727 | 12.373 | 10.1838 | 12.6377
ASHP +HPWH | 2026 | 27.6% | 10.8316 | 8.6657 | 13.4376 | 10.6238 | 13.509
ASHP +HPWH | 2027 | 33.8% | 11.5111 | 8.8586 | 14.5022 | 11.0638 | 14.3804
ASHP +HPWH | 2028 | 40% | 12.1906 | 9.0515 | 15.5669 | 11.5038 | 15.2518
ASHP +HPWH | 2029 | 46.2% | 12.8701 | 9.2445 | 16.6315 | 11.9438 | 16.1232
ASHP +HPWH | 2030 | 52.4% | 13.5495 | 9.4374 | 17.6961 | 12.3838 | 16.9945
ASHP +HPWH | 2031 | 58.6% | 14.229 | 9.6304 | 18.7608 | 12.8237 | 17.8659
ASHP +HPWH | 2032 | 64.8% | 14.9085 | 9.8233 | 19.8254 | 13.2637 | 18.7373
ASHP +HPWH | 2033 | 71% | 15.588 | 10.0163 | 20.89 | 13.7037 | 19.6086
ASHP +HPWH | 2034 | 77.2% | 16.2675 | 10.2092 | 21.9547 | 14.1437 | 20.48
ASHP +HPWH | 2035 | 83.4% | 16.947 | 10.4021 | 23.0193 | 14.5837 | 21.3514
ASHP +HPWH | 2036 | 89.6% | 17.6265 | 10.5951 | 24.0839 | 15.0237 | 22.2228
ASHP +HPWH | 2037 | 95.8% | 18.306 | 10.788 | 25.1486 | 15.4636 | 23.0941
ASHP + HPWH | 2038 | 102% | 18.7663 | 10.9187 | 26.2044 | 15.7617 | 23.6844
| Ontario single home weighted average power draw (kW) |  |  |  |  | weighted change to ON power draw (electric/furnace subtracted
| at local morning miniumu | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp) |  | at local morning miniumu | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp)
ASHP +HPWH | 6.985 | 5.0023 | 5.3875 | 9.9806 |  | 4.2545 | 2.6584 | 2.9629 | 6.7464
ASHP with ETS for peak hours + HPWH | 1.0245 | 1.0245 | 1.0245 | 1.0245 |  | -1.1696 | -0.96138 | -1.0075 | -1.4037
ASHP/HPWH powered with batteries | 2.0944 | 0.13833 | 0.49693 | 4.9806 |  | -0.19598 | -1.7678 | -1.4876 | 2.1964
ASHP/HPWH powered with EV battery | 0.11024 | 0 | 0 | 0.73507 |  | -2.0016 | -1.8937 | -1.9398 | -1.667
GSHP/EWH | 2.4421 | 2.1118 | 2.1738 | 3.8437 |  | 0.12041 | 0.028024 | 0.038424 | 1.1619
NG space and water heater | 0.672 | 0.672 | 0.672 | 0.672
electric resistance space and water heating | 10.6079 | 9.2197 | 9.527 | 12.1682
Ontario increased peak hour power draw for space and water heating (GW)
| % adoption | at local morning miniumu | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp)
ASHP +HPWH | 100% | 15.9607 | 9.9731 | 11.1153 | 25.3092
ASHP with ETS for peak hours + HPWH | 100% | -4.3878 | -3.6066 | -3.7796 | -5.2658
ASHP/HPWH powered with batteries | 100% | -0.73521 | -6.6319 | -5.5806 | 8.2399
ASHP/HPWH powered with EV battery | 100% | -7.509 | -7.1042 | -7.2771 | -6.2539
GSHP/EWH | 100% | 0.45173 | 0.10513 | 0.14415 | 4.3587

## ON 2024 peak (hidden)
100% cASHP adoption with and without other tech at projected winter 2023/2024 peak
winter peak is projected to occur at afternoon maximum
Need to ID available capacity!
[10 empty] | At extreme cold temperature |  |  |  | At morning minimum
At local afternoon maximum | [5 empty] | utility savings by investing in peak mitigation technologies
current heating/water heating power draw | 8.7931 | [8 empty] | current heating/water heating power draw | 12.1331 |  |  | current heating/water heating power draw | 10.2437
| % adoption | power draw | net increase |  |  |  | decreased power draw | cost ($M) | cost savings ($M) |  | % adoption | power draw | net increase |  | % adoption | power draw | net increase
existing mix of space and water heating systems |  | 8.7931 |  |  |  | ASHP/HPWH | 0 | 0 |  | ASHP +HPWH |  | 37.4424 | 25.3092 | ASHP +HPWH |  | 26.2044 | 15.9607
100% of homes have ASHPs and HPWHs |  | 18.7663 | 9.9731 |  |  | ASHP/HPWH + ETS | 14.9228 | 9013.3993 | 5150.7357 | ASHP with ETS for peak hours + HPWH | 100% | 3.8434 | -8.2897 | ASHP with ETS for peak hours + HPWH | 100% | 3.8434 | -6.4003
ASHP/HPWH + ETS | 100% | 3.8434 | -4.9497 |  |  | ASHP/HPWH + home batteries | 18.2473 | 11021.3878 | 62.6081 | ASHP/HPWH powered with batteries | 100% | 18.6848 | 6.5517 | ASHP/HPWH powered with batteries | 100% | 7.8573 | -2.3865
ASHP/HPWH + home batteries | 100% | 0.51894 | -8.2742 |  |  | ASHP/HPWH + EV battery | 18.7663 | 11334.8261 | 7491.4759 | ASHP/HPWH powered with EV battery | 100% | 2.7576 | -9.3755 | ASHP/HPWH powered with EV battery | 100% | 0.41358 | -9.8301
ASHP/HPWH + EV battery | 100% | 0 | -8.7931 | -0.087317 |  | ASHP/HPWH and GSHP/HPWH | 10.844 | 6549.7593 | 4531.8787 | ASHP/HPWH + GSHP/EWH (high adoption) | 100% | 14.4198 | 2.2867 | ASHP/HPWH + GSHP/EWH (high adoption) | 100% | 9.1616 | -1.0821
100% of homes have GSHPs and HPWHs | 100% | 7.9223 | -0.87083 |  |  | ASHP/HPWH and GSHP/HPWH (low adoption) | 10.844 | 6549.7593 | 4531.8787 | ASHP/HPWH + GSHP/EWH (low adoption) | 100% | 14.4198 | 2.2867 | ASHP/HPWH + GSHP/EWH (low adoption) | 100% | 9.1616 | -1.0821
100% of homes have GSHPs and HPWHs | 100% | 7.9223 | -0.87083 | 0.21313 |  | ASHP/HPWH + all tech | 7.8476 | 4739.9216 | -5601.4154 | half of IESO BAU+ combined |  | 23.6844 | 11.5513 | half of IESO BAU+ combined |  | 15.7617 | 5.518 | 0.34572
ASHP/HPWH + all tech |  | 10.9187 | 2.1256 |  |  | all combined | 15.6951 | 9479.8431 |  | all combined |  | 9.9264 | -2.2067 | all combined |  | 5.319 | -4.9248
all combined |  | 3.0712 | -5.722
% of homes that must adopt a tech to reach no new increase |  | 0.85936 | [7 empty] | % of homes that must adopt a tech to reach no new increase |  | 0.79044 |  | % of homes that must adopt a tech to reach no new increase |  | 0.83127
| % adoption | power draw | 10% |  |  | 30%
ASHP/HPWH |  | 18.7663 | 9.9731
ASHP/HPWH + ETS | 10% | 17.274 | 8.4809 | 30% | 14.2894 | 5.4963
ASHP/HPWH + home batteries | 10% | 16.9415 | 8.1484 | 30% | 13.2921 | 4.4989
ASHP/HPWH + EV battery | 10% | 16.8896 | 8.0965 | 30% | 13.1364 | 4.3433
ASHP/HPWH and GSHP/EWH | 10% | 17.6819 | 8.8887 | 30% | 15.5131 | 6.72
all together |  | 12.4882 | 3.6951
0.46589
| Ontario single home weighted average power draw (kW) |  |  |  |  | weighted change to ON power draw (electric/furnace subtracted
| at local morning miniumu | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp) |  | at local morning miniumu | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp)
ASHP +HPWH | 6.985 | 5.0023 | 5.3875 | 9.9806 |  | 4.2545 | 2.6584 | 2.9629 | 6.7464
ASHP with ETS for peak hours + HPWH | 1.0245 | 1.0245 | 1.0245 | 1.0245 |  | -1.1696 | -0.96138 | -1.0075 | -1.4037
ASHP/HPWH powered with batteries | 2.0944 | 0.13833 | 0.49693 | 4.9806 |  | -0.19598 | -1.7678 | -1.4876 | 2.1964
ASHP/HPWH powered with EV battery | 0.11024 | 0 | 0 | 0.73507 |  | -2.0016 | -1.8937 | -1.9398 | -1.667
GSHP/EWH | 2.4421 | 2.1118 | 2.1738 | 3.8437 |  | 0.12041 | 0.028024 | 0.038424 | 1.1619
NG space and water heater | 0.672 | 0.672 | 0.672 | 0.672
electric resistance space and water heating | 10.6079 | 9.2197 | 9.527 | 12.1682
Ontario increased peak hour power draw for space and water heating (GW)
| % adoption | at local morning miniumu | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp)
ASHP +HPWH | 100% | 15.9607 | 9.9731 | 11.1153 | 25.3092
ASHP with ETS for peak hours + HPWH | 100% | -4.3878 | -3.6066 | -3.7796 | -5.2658
ASHP/HPWH powered with batteries | 100% | -0.73521 | -6.6319 | -5.5806 | 8.2399
ASHP/HPWH powered with EV battery | 100% | -7.509 | -7.1042 | -7.2771 | -6.2539
GSHP/EWH | 100% | 0.45173 | 0.10513 | 0.14415 | 4.3587

## using available capacity (hidden)
| kW | hours of charging | kWh | hours to offset | 1 hour offset - % adoption before using up capacity | 2 hour offset | 4 hour offset | 6 hour offset |  | adoption | % of tech | power draw to charge | kWh use at 50% of IESO BAU+ adoption
ETS charging average | 5.6773 | 10.989 | 62.3881 | 13.3712 | 324.7% | 159.3% | 73.81% | 42.22%
ETS charging morning minimum | 9.7079 | 10.989 | 106.68 | 13.3712 | 189.9% | 93.18% | 43.16% | 24.69%
ETS charging afternoon maximum | 8.3197 | 10.989 | 91.4255 | 13.3712 | 221.5% | 108.7% | 50.37% | 28.81% |  | 24% | 29.27% | 49.9183 | 22.4723
ETS charging evenign minimum | 8.627 | 10.989 | 94.8024 | 13.3712 | 213.6% | 104.9% | 48.57% | 27.79%
ETS chargign extreme cold | 11.2682 | 10.989 | 123.8261 | 13.3712 | 163.6% | 80.28% | 37.19% | 21.27%
battery charging | 5.5556 | 2.2222 | 12.3457 | 2 | 331.8% | 162.8% | na | na |  | 27% | 32.93% | 11.1111 | 5.6273
EV charging | 11.52 | 4.8 | 55.296 | 4 | 160% | 78.52% | 36.37% | na |  | 31% | 37.8% | 46.08 | 26.7948
assumes charged only enough for the offset time | [12 empty] | 54.8944 | This is less than available GWh in 24 hours before peak
Available GWh in 24 hours before peak (ie difference between the hourly demand and the peak demand
69.146 | 1 hour
67.87 | 2 hours
62.88 | 4 hours
53.955 | 6 hours
| Ontario single home weighted average power draw (kW) |  |  |  |  | weighted change to ON power draw (electric/furnace subtracted
| at local morning miniumu | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp) |  | at local morning miniumu | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp)
ASHP +HPWH | 6.985 | 5.0023 | 5.3875 | 9.9806 |  | 4.2545 | 2.6584 | 2.9629 | 6.7464
ASHP with ETS for peak hours + HPWH | 1.0245 | 1.0245 | 1.0245 | 1.0245 |  | -1.1696 | -0.96138 | -1.0075 | -1.4037
ASHP/HPWH powered with batteries | 2.0944 | 0.13833 | 0.49693 | 4.9806 |  | -0.19598 | -1.7678 | -1.4876 | 2.1964
ASHP/HPWH powered with EV battery | 0.11024 | 0 | 0 | 0.73507 |  | -2.0016 | -1.8937 | -1.9398 | -1.667
GSHP/EWH | 2.4421 | 2.1118 | 2.1738 | 3.8437 |  | 0.12041 | 0.028024 | 0.038424 | 1.1619
NG space and water heater | 0.672 | 0.672 | 0.672 | 0.672
electric resistance space and water heating | 10.6079 | 9.2197 | 9.527 | 12.1682
Ontario increased peak hour power draw for space and water heating (GW)
| % adoption | at local morning miniumu | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp)
ASHP +HPWH | 100% | 15.9607 | 9.9731 | 11.1153 | 25.3092
ASHP with ETS for peak hours + HPWH | 100% | -4.3878 | -3.6066 | -3.7796 | -5.2658
ASHP/HPWH powered with batteries | 100% | -0.73521 | -6.6319 | -5.5806 | 8.2399
ASHP/HPWH powered with EV battery | 100% | -7.509 | -7.1042 | -7.2771 | -6.2539
GSHP/EWH | 100% | 0.45173 | 0.10513 | 0.14415 | 4.3587

## full adoption (hidden)
| Ontario single home weighted average power draw (kW) |  |  |  |  | weighted change to ON power draw (electric/furnace subtracted
| at local morning miniumu | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp) |  | at local morning miniumu | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp)
ASHP +HPWH | 6.985 | 5.0023 | 5.3875 | 9.9806 |  | 4.2545 | 2.6584 | 2.9629 | 6.7464
ASHP with ETS for peak hours + HPWH | 1.0245 | 1.0245 | 1.0245 | 1.0245 |  | -1.1696 | -0.96138 | -1.0075 | -1.4037
ASHP/HPWH powered with batteries | 2.0944 | 0.13833 | 0.49693 | 4.9806 |  | -0.19598 | -1.7678 | -1.4876 | 2.1964
ASHP/HPWH powered with EV battery | 0.11024 | 0 | 0 | 0.73507 |  | -2.0016 | -1.8937 | -1.9398 | -1.667
GSHP/EWH | 2.4421 | 2.1118 | 2.1738 | 3.8437 |  | 0.12041 | 0.028024 | 0.038424 | 1.1619
NG space and water heater | 0.672 | 0.672 | 0.672 | 0.672
electric resistance space and water heating | 10.6079 | 9.2197 | 9.527 | 12.1682
Ontario increased peak hour power draw for space and water heating (GW)
| % adoption | at local morning miniumu | at local afternoon maximum | at local evening minimum | extreme cold (5'C below design temp)
ASHP +HPWH | 100% | 15.9607 | 9.9731 | 11.1153 | 25.3092
ASHP with ETS for peak hours + HPWH | 100% | -4.3878 | -3.6066 | -3.7796 | -5.2658
ASHP/HPWH powered with batteries | 100% | -0.73521 | -6.6319 | -5.5806 | 8.2399
ASHP/HPWH powered with EV battery | 100% | -7.509 | -7.1042 | -7.2771 | -6.2539
GSHP/EWH | 100% | 0.45173 | 0.10513 | 0.14415 | 4.3587
ASHP +HPWH | 100% | 15.9607 | 9.9731 | 11.1153 | 25.3092
with ETS for peak hours + HPWH | 24% | 11.0771 | 6.714 | 7.5405 | 17.9712
with batteries | 27% | 11.4528 | 5.4898 | 6.6074 | 20.7005
with EV battery | 31% | 8.6851 | 4.6792 | 5.4137 | 15.5247
GSHP/EWH (100%) | 100% | 0.45173 | 0.10513 | 0.14415 | 4.3587
GSHP/EWH high adoption | 30% | 11.308 | 7.0127 | 7.824 | 19.0241
GSHP/EWH low adoption | 10% | 14.4098 | 8.9863 | 10.0182 | 23.2142
Ontario increased peak hour power draw analysis for space and water heating (GW)
condition | % adoption | at -10'C | at -13.5'C | at -15'C | at -20'C | at -25'C | at -30 |  | at local morning miniumu | at local afternoon maximum | at local evening minimum
ASHP +HPWH | 100% | 7.2624 | 9.0966 | 10.1196 | 14.8195 | 22.0241 | 32.2045 |  | can't do this easily because Toronto and Windsor and TB+ K and NB are combined on regional outomes
with ETS for peak hours + HPWH | 24% | 4.1363 | 5.328 | 6.0188 | 9.3019 | 14.4885 | 21.9368
with batteries | 27% | 2.8177 | 3.943 | 4.6835 | 9.3454 | 16.6321 | 27.018
with EV battery | 31% | 2.3101 | 3.3468 | 3.9545 | 6.8704 | 11.5145 | 21.0971
GSHP/EWH (100%) | 100% | -0.3185 | -0.2067 | 0.16131 | 0.32414 | 3.9773 | 6.4301
GSHP/EWH high adoption | 30% | 4.9881 | 6.3056 | 7.1321 | 10.4709 | 16.6101 | 24.4722
GSHP/EWH low adoption | 10% | 6.5043 | 8.1662 | 9.1237 | 13.3699 | 20.2194 | 29.6271

## by region (hidden)
At local afternoon maximum
| Toronto |  |  | Windsor |  |  | Ottawa |  |  | Thunder Bay |  |  | North Bay |  |  | Kapuskasing
| afternoon max | morning min | afternoon min | afternoon max | morning min | afternoon min | afternoon max | morning min | afternoon min | afternoon max | morning min | afternoon min | afternoon max | morning min | afternoon min | afternoon max | morning min | afternoon min
ASHP + HPWH | 4.7489 | 6.7747 | 5.1194 | 4.0391 | 4.0391 | 4.0391 | 4.8475 | 8.3181 | 6.1799 | 4.8475 | 8.3181 | 8.3181 | 6.1799 | 11.792 | 8.3181 | 6.1799 | 11.792 | 8.3181
temperature | -13.5 | -18.5 | -15 | -8.9 | -11.6 | -11.5 | -17.2 | -24 | -19.7 | -15.9 | -23.8 | -25.2 | -22.1 | -28.5 | -25 | -21.1 | -31.6 | -24.7
afternoon max
| Toronto | Windsor | Ottawa | Thunder Bay | North Bay | Kapuskasing
ASHP+HPWH at afternoon max | 4.7489 | 4.0391 | 4.8475 | 4.8475 | 6.1799 | 6.1799
ASHP+HPWH at morning min | 6.7747 | 4.0391 | 8.3181 | 8.3181 | 11.792 | 11.792
ASHP+HPWH at afternoon min | 5.1194 | 4.0391 | 6.1799 | 8.3181 | 8.3181 | 11.792

## hourly demand (hidden)
2022 APO hourly demand forecast - grid
source: https://www.ieso.ca/en/Sector-Participants/Planning-and-Forecasting/Annual-Planning-Outlook
[6 empty] | Winter maximum |  |  |  | 21963 | 22833 | 23135 | 23723 | 23551 | 24243 | 24840 | 25280 | 25271 | 25671 | 26316 | 27348 | 28109 | 28458 | 29173 | 29766 | 29930 | 30502 | 30693 | 30691 | capacity used | capacity available
[10 empty] | 20687 | [18 empty] | 29629 | 17191 | 1451
[10 empty] | 19990 | [18 empty] | 28937 | 16755 | 1887
[10 empty] | 18946 | [18 empty] | 28529 | 16544 | 2098
[10 empty] | 17810 | [18 empty] | 27984 | 16548 | 2094
[10 empty] | 17191 | [18 empty] | 27710 | 16711 | 1931
[10 empty] | 16755 | [18 empty] | 26989 | 17305 | 1337
[10 empty] | 16544 | [18 empty] | 26160 | 18594 | 48
[10 empty] | 16548 | [18 empty] | 25759 | 20164 | -1522
[10 empty] | 16711 | [18 empty] | 26347 | 20358 | -1716
[10 empty] | 17305 | [18 empty] | 27404 | 20048 | -1406
[10 empty] | 18594 | [18 empty] | 27424 | 19600 | -958
[10 empty] | 20164 | [18 empty] | 27309 | 19328 | -686
[10 empty] | 20358 | [18 empty] | 26606 | 18974 | -332
[10 empty] | 20048 | [18 empty] | 26099 | 18850 | -208
[10 empty] | 19600 | [18 empty] | 25357 | 18860 | -218
[10 empty] | 19328 | [18 empty] | 24962 | 19292 | -650
[10 empty] | 18974 | [18 empty] | 24760 | 20124 | -1482
[10 empty] | 18850 | [18 empty] | 24946 | 21394 | -2752
[10 empty] | 18860 | [18 empty] | 25531 | 21930 | -3288
[10 empty] | 19292 | [18 empty] | 26584 | 21963 | -3321
[10 empty] | 20124 | [18 empty] | 27596 | 21819 | -3177
[10 empty] | 21394 | [18 empty] | 28821 | 21068 | -2426
[10 empty] | 21930 | [18 empty] | 30055 | 19866 | -1224
[6 empty] | available MWh |  |  | 1 hour peak mitigation | 69146 | [18 empty] | 84395 | 18642 | 0
[9 empty] | 2 hour peak mitigation | 67870
[9 empty] | 4 hour peak mitigation | 62880
[9 empty] | 6 hour peak mitigation | 53955
23236
Ontario | [8 empty] | Hourly Demand (MW) | Year
[10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
# | Hour of Year | Day of Year | Non-Leap Year |  |  | Leap Year |  |  | Hour of Day | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
|  |  | Month of Year | Day of Month | Season | Month of Year | Day of Month | Season |  | Leap Year | Non-Leap Year | Non-Leap Year | Non-Leap Year | Leap Year | Non-Leap Year | Non-Leap Year | Non-Leap Year | Leap Year | Non-Leap Year | Non-Leap Year | Non-Leap Year | Leap Year | Non-Leap Year | Non-Leap Year | Non-Leap Year | Leap Year | Non-Leap Year | Non-Leap Year | Non-Leap Year
1 | 1 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 1 | 16081 | 16738 | 17426 | 17893 | 18323 | 18974 | 19629 | 20213 | 20868 | 21667 | 22358 | 23126 | 23811 | 24421 | 25010 | 25507 | 25951 | 26274 | 26519 | 26721
2 | 2 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 2 | 15639 | 16308 | 17008 | 17464 | 17928 | 18588 | 19238 | 19846 | 20504 | 21276 | 21958 | 22701 | 23368 | 23965 | 24535 | 25017 | 25448 | 25764 | 26005 | 26203
3 | 3 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 3 | 15384 | 16052 | 16778 | 17254 | 17747 | 18431 | 19100 | 19728 | 20396 | 21159 | 21811 | 22524 | 23171 | 23737 | 24285 | 24745 | 25163 | 25472 | 25707 | 25900
4 | 4 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 4 | 15249 | 15911 | 16633 | 17095 | 17567 | 18229 | 18867 | 19449 | 20060 | 20760 | 21338 | 21978 | 22559 | 23063 | 23565 | 23978 | 24358 | 24641 | 24860 | 25043
5 | 5 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 5 | 15172 | 15867 | 16531 | 16968 | 17405 | 18025 | 18609 | 19126 | 19704 | 20277 | 20772 | 21372 | 21872 | 22310 | 22744 | 23112 | 23448 | 23694 | 23892 | 24062
6 | 6 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 6 | 15203 | 15937 | 16533 | 16932 | 17366 | 17887 | 18407 | 18880 | 19367 | 19795 | 20244 | 20756 | 21157 | 21517 | 21885 | 22197 | 22487 | 22695 | 22862 | 23017
7 | 7 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 7 | 15462 | 16167 | 16774 | 17077 | 17510 | 17961 | 18370 | 18811 | 19158 | 19507 | 19933 | 20310 | 20627 | 20925 | 21241 | 21508 | 21762 | 21937 | 22081 | 22225
8 | 8 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 8 | 16042 | 16681 | 17314 | 17583 | 18075 | 18427 | 18801 | 19160 | 19461 | 19939 | 20277 | 20483 | 20760 | 21024 | 21312 | 21683 | 21918 | 21950 | 22084 | 22222
9 | 9 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 9 | 16660 | 17229 | 17840 | 18139 | 18567 | 18919 | 19340 | 19632 | 19908 | 20415 | 20668 | 20848 | 21102 | 21348 | 21623 | 21982 | 22207 | 22241 | 22376 | 22515
10 | 10 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 10 | 17136 | 17707 | 18319 | 18614 | 19044 | 19409 | 19843 | 20147 | 20431 | 20947 | 21210 | 21404 | 21672 | 21930 | 22216 | 22585 | 22813 | 22857 | 23005 | 23149
11 | 11 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 11 | 17422 | 17985 | 18556 | 18810 | 19207 | 19556 | 19968 | 20257 | 20518 | 21025 | 21300 | 21508 | 21789 | 22060 | 22358 | 22736 | 22972 | 23027 | 23178 | 23326
12 | 12 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 12 | 17565 | 18122 | 18653 | 18864 | 19218 | 19534 | 19910 | 20170 | 20400 | 20888 | 21168 | 21381 | 21666 | 21941 | 22241 | 22622 | 22860 | 22919 | 23066 | 23221
13 | 13 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 13 | 17621 | 18173 | 18680 | 18869 | 19200 | 19495 | 19850 | 20092 | 20303 | 20778 | 21058 | 21270 | 21551 | 21825 | 22123 | 22502 | 22739 | 22796 | 22948 | 23096
14 | 14 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 14 | 17563 | 18115 | 18623 | 18806 | 19131 | 19418 | 19764 | 19997 | 20199 | 20664 | 20937 | 21142 | 21414 | 21681 | 21972 | 22346 | 22578 | 22631 | 22780 | 22928
15 | 15 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 15 | 17580 | 18129 | 18635 | 18821 | 19147 | 19432 | 19775 | 20005 | 20203 | 20662 | 20927 | 21124 | 21388 | 21648 | 21932 | 22300 | 22527 | 22576 | 22721 | 22866
16 | 16 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 16 | 17845 | 18398 | 18918 | 19107 | 19431 | 19710 | 20046 | 20266 | 20453 | 20899 | 21146 | 21325 | 21569 | 21814 | 22085 | 22441 | 22659 | 22701 | 22829 | 22986
17 | 17 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 17 | 18658 | 19146 | 19754 | 19957 | 20288 | 20565 | 20900 | 21125 | 21242 | 21775 | 22035 | 22138 | 22397 | 22649 | 22924 | 23286 | 23507 | 23550 | 23679 | 23839
18 | 18 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 18 | 19646 | 20173 | 20820 | 21071 | 21340 | 21685 | 22023 | 22190 | 22439 | 23008 | 23255 | 23491 | 23821 | 24110 | 24415 | 24802 | 25039 | 25096 | 25231 | 25393
19 | 19 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 19 | 19480 | 20022 | 20604 | 20955 | 21252 | 21520 | 21957 | 22161 | 22466 | 23104 | 23436 | 23753 | 24163 | 24518 | 24879 | 25314 | 25589 | 25658 | 25798 | 25967
20 | 20 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 20 | 19007 | 19655 | 20268 | 20578 | 20996 | 21303 | 21713 | 22060 | 22446 | 23096 | 23605 | 24024 | 24511 | 24942 | 25374 | 25872 | 26193 | 26284 | 26447 | 26618
21 | 21 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 21 | 18638 | 19310 | 19950 | 20298 | 20765 | 21135 | 21609 | 22038 | 22518 | 23272 | 23888 | 24416 | 25005 | 25524 | 26028 | 26593 | 26971 | 27091 | 27287 | 27479
22 | 22 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 22 | 18068 | 18756 | 19417 | 19795 | 20296 | 20723 | 21256 | 21749 | 22295 | 23108 | 23788 | 24382 | 25035 | 25616 | 26159 | 26758 | 27174 | 27335 | 27544 | 27746
23 | 23 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 23 | 17299 | 17977 | 18681 | 19083 | 19607 | 20067 | 20638 | 21172 | 21746 | 22620 | 23333 | 23951 | 24633 | 25242 | 25801 | 26430 | 26869 | 27043 | 27260 | 27467
24 | 24 | 1 | 1 | 1 | Winter | 1 | 1 | Winter | 24 | 16594 | 17271 | 18008 | 18453 | 18874 | 19527 | 20152 | 20723 | 21371 | 22168 | 22873 | 23642 | 24343 | 24967 | 25545 | 26060 | 26508 | 26817 | 27046 | 27256
25 | 25 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 1 | 15963 | 16948 | 17940 | 18083 | 17693 | 19246 | 20023 | 20776 | 21504 | 20670 | 20651 | 23356 | 24371 | 25544 | 25335 | 24093 | 23791 | 26910 | 27368 | 27934
26 | 26 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 2 | 15553 | 16550 | 17454 | 17631 | 17249 | 18871 | 19633 | 20373 | 21048 | 20249 | 20322 | 22951 | 23918 | 24877 | 24843 | 23571 | 23399 | 26380 | 26873 | 27193
27 | 27 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 3 | 15392 | 16395 | 17282 | 17474 | 17100 | 18848 | 19600 | 20340 | 20987 | 20185 | 20221 | 22928 | 23809 | 24568 | 24694 | 23352 | 23161 | 26185 | 26661 | 26808
28 | 28 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 4 | 15338 | 16356 | 17154 | 17308 | 16937 | 18723 | 19441 | 20139 | 20653 | 19861 | 19837 | 22494 | 23285 | 23890 | 24008 | 22728 | 22516 | 25464 | 25881 | 25937
29 | 29 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 5 | 15469 | 16445 | 17164 | 17235 | 16837 | 18787 | 19374 | 20052 | 20374 | 19470 | 19473 | 22160 | 22782 | 23232 | 23237 | 21992 | 21806 | 24708 | 25035 | 25058
30 | 30 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 6 | 15943 | 16890 | 17489 | 17340 | 16834 | 19184 | 19661 | 20279 | 20355 | 19171 | 19239 | 22140 | 22615 | 22783 | 22500 | 21281 | 21269 | 24281 | 24490 | 24404
31 | 31 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 7 | 17027 | 18056 | 18406 | 17775 | 17193 | 20037 | 20603 | 21233 | 21084 | 19372 | 19247 | 22561 | 23167 | 23112 | 22336 | 21180 | 21144 | 24628 | 24985 | 24606
32 | 32 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 8 | 18327 | 19511 | 19668 | 18617 | 17821 | 21209 | 21927 | 22622 | 22324 | 19943 | 19611 | 23456 | 24237 | 24123 | 23006 | 21689 | 21435 | 25568 | 26050 | 25562
33 | 33 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 9 | 18661 | 19832 | 20113 | 19207 | 18389 | 21584 | 22280 | 22957 | 22729 | 20506 | 19870 | 23750 | 24425 | 24445 | 23471 | 22199 | 21604 | 25667 | 26300 | 25855
34 | 34 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 10 | 18715 | 19827 | 20174 | 19587 | 18838 | 21769 | 22369 | 22952 | 22796 | 20987 | 20308 | 24069 | 24593 | 24592 | 23940 | 22804 | 22157 | 25879 | 26441 | 26033
35 | 35 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 11 | 18689 | 19788 | 20135 | 19433 | 18875 | 21807 | 22354 | 22736 | 22585 | 20922 | 20405 | 24175 | 24602 | 24407 | 23648 | 23226 | 22731 | 25932 | 26272 | 25881
36 | 36 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 12 | 18577 | 19780 | 20057 | 19271 | 18841 | 21518 | 22177 | 22526 | 22320 | 20743 | 20345 | 23784 | 24362 | 23955 | 23197 | 23265 | 22886 | 25710 | 25856 | 25445
37 | 37 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 13 | 18518 | 19603 | 19954 | 19122 | 18806 | 21418 | 22090 | 22267 | 22139 | 20633 | 20340 | 23632 | 24241 | 23751 | 22821 | 23307 | 23000 | 25578 | 25500 | 25249
38 | 38 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 14 | 18477 | 19540 | 19857 | 18900 | 18720 | 21254 | 22147 | 22111 | 22003 | 20502 | 20223 | 23383 | 24250 | 23476 | 22437 | 23308 | 23012 | 25555 | 25162 | 24953
39 | 39 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 15 | 18530 | 19522 | 19717 | 18893 | 18769 | 21166 | 22081 | 22075 | 21824 | 20528 | 20249 | 23187 | 24109 | 23175 | 22352 | 23015 | 22710 | 25397 | 25063 | 24618
40 | 40 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 16 | 18841 | 19503 | 19702 | 19147 | 19108 | 21528 | 22223 | 21941 | 21666 | 20784 | 20365 | 23540 | 24124 | 23258 | 22545 | 22854 | 22408 | 25372 | 24978 | 24634
41 | 41 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 17 | 19492 | 20092 | 20238 | 19915 | 19964 | 22063 | 22751 | 22452 | 22187 | 21706 | 21025 | 24050 | 24635 | 23940 | 23423 | 23555 | 22937 | 25908 | 25477 | 25329
42 | 42 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 18 | 20255 | 21308 | 21195 | 21042 | 21337 | 22644 | 23398 | 23788 | 23271 | 23055 | 22324 | 24594 | 25437 | 25192 | 24967 | 25018 | 24158 | 26838 | 26636 | 26693
43 | 43 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 19 | 19963 | 21319 | 21032 | 20885 | 21380 | 22421 | 23243 | 24023 | 23212 | 23235 | 22400 | 24744 | 25689 | 25692 | 25305 | 25542 | 24532 | 27316 | 27289 | 27355
44 | 44 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 20 | 19628 | 21173 | 20693 | 20462 | 21087 | 22299 | 23149 | 24065 | 23199 | 23153 | 22590 | 25090 | 26148 | 26206 | 25564 | 25747 | 25007 | 28059 | 28078 | 28057
45 | 45 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 21 | 19279 | 21005 | 20387 | 20156 | 20848 | 22149 | 22973 | 24164 | 23226 | 23208 | 22808 | 25464 | 26558 | 26777 | 26107 | 26228 | 25593 | 28767 | 29094 | 28886
46 | 46 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 22 | 18585 | 20270 | 19824 | 19624 | 20258 | 21628 | 22505 | 23566 | 22883 | 22829 | 22543 | 25298 | 26470 | 26730 | 26113 | 26088 | 25530 | 28881 | 29278 | 29001
47 | 47 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 23 | 17651 | 19261 | 19008 | 18946 | 19545 | 20799 | 21762 | 22743 | 22277 | 22303 | 22105 | 24707 | 25959 | 26217 | 25772 | 25720 | 25246 | 28471 | 29028 | 28591
48 | 48 | 2 | 1 | 2 | Winter | 1 | 2 | Winter | 24 | 16642 | 18103 | 18100 | 18167 | 18783 | 19943 | 20988 | 21865 | 21671 | 21756 | 21635 | 24046 | 25363 | 25675 | 25361 | 25236 | 24796 | 27933 | 28402 | 28110
49 | 49 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 1 | 16051 | 17277 | 17735 | 17396 | 17202 | 19442 | 20229 | 20923 | 21248 | 20155 | 22379 | 23748 | 24716 | 24836 | 23745 | 23490 | 25842 | 27205 | 27822 | 27179
50 | 50 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 2 | 15647 | 16824 | 17312 | 16979 | 16914 | 19059 | 19874 | 20520 | 20878 | 19903 | 21997 | 23335 | 24268 | 24370 | 23261 | 23131 | 25347 | 26734 | 27103 | 26657
51 | 51 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 3 | 15444 | 16578 | 17085 | 16766 | 16717 | 18973 | 19788 | 20405 | 20782 | 19777 | 21888 | 23235 | 24147 | 24219 | 23042 | 22886 | 25170 | 26511 | 26698 | 26440
52 | 52 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 4 | 15372 | 16466 | 16931 | 16607 | 16536 | 18837 | 19629 | 20125 | 20455 | 19443 | 21476 | 22776 | 23615 | 23594 | 22451 | 22269 | 24475 | 25748 | 25843 | 25632
53 | 53 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 5 | 15453 | 16478 | 16866 | 16518 | 16410 | 18806 | 19596 | 19914 | 20122 | 19131 | 21161 | 22340 | 23047 | 22875 | 21744 | 21584 | 23861 | 24910 | 24965 | 24690
54 | 54 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 6 | 15941 | 16825 | 17004 | 16548 | 16463 | 19155 | 19901 | 19994 | 19881 | 18966 | 21104 | 22250 | 22765 | 22193 | 21072 | 21072 | 23482 | 24379 | 24309 | 23799
55 | 55 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 7 | 17067 | 17757 | 17472 | 16923 | 16759 | 20150 | 20922 | 20807 | 20057 | 19034 | 21576 | 22861 | 23381 | 22064 | 20991 | 20957 | 23568 | 24874 | 24508 | 23534
56 | 56 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 8 | 18420 | 19015 | 18333 | 17553 | 17228 | 21500 | 22345 | 22094 | 20921 | 19439 | 22641 | 23977 | 24592 | 22753 | 21510 | 21254 | 24352 | 25951 | 25468 | 24165
57 | 57 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 9 | 18797 | 19454 | 18942 | 18133 | 17519 | 21868 | 22705 | 22531 | 21584 | 19735 | 23099 | 24207 | 24854 | 23240 | 22048 | 21449 | 24709 | 26220 | 25771 | 24617
58 | 58 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 10 | 18859 | 19560 | 19367 | 18631 | 17968 | 21941 | 22760 | 22657 | 22062 | 20243 | 23522 | 24364 | 24913 | 23701 | 22648 | 21998 | 25150 | 26364 | 25954 | 25129
59 | 59 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 11 | 18821 | 19692 | 19432 | 18913 | 18410 | 21873 | 22878 | 22808 | 22148 | 20729 | 23846 | 24313 | 24637 | 23355 | 23015 | 22521 | 25082 | 26147 | 25753 | 24824
60 | 60 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 12 | 18835 | 19766 | 19445 | 19066 | 18672 | 21746 | 22889 | 22778 | 22030 | 20904 | 23699 | 24090 | 24235 | 22934 | 23075 | 22689 | 24555 | 25744 | 25338 | 24401
61 | 61 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 13 | 18702 | 19659 | 19328 | 19069 | 18804 | 21587 | 22695 | 22678 | 21853 | 20996 | 23585 | 23895 | 23856 | 22488 | 23038 | 22745 | 24263 | 25313 | 25063 | 23925
62 | 62 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 14 | 18766 | 19650 | 19203 | 19102 | 18892 | 21643 | 22695 | 22712 | 21745 | 21079 | 23503 | 23917 | 23582 | 22110 | 23052 | 22767 | 23868 | 24980 | 24771 | 23510
63 | 63 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 15 | 18727 | 19365 | 19037 | 18958 | 18750 | 21549 | 22408 | 22262 | 21411 | 20800 | 23170 | 23761 | 23517 | 22008 | 22731 | 22441 | 23805 | 24856 | 24410 | 23381
64 | 64 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 16 | 19048 | 19332 | 19244 | 19220 | 18865 | 21822 | 22133 | 21945 | 21351 | 20702 | 23271 | 23922 | 23673 | 22331 | 22690 | 22266 | 24492 | 24899 | 24559 | 23663
65 | 65 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 17 | 19749 | 19820 | 19939 | 19991 | 19498 | 22442 | 22498 | 22300 | 21919 | 21151 | 23709 | 24493 | 24499 | 23274 | 23460 | 22849 | 25285 | 25467 | 25308 | 24626
66 | 66 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 18 | 20594 | 20686 | 20942 | 21244 | 20562 | 23187 | 23658 | 23178 | 23013 | 22205 | 24412 | 25263 | 25819 | 24820 | 24925 | 24075 | 26162 | 26637 | 26684 | 26253
67 | 67 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 19 | 20378 | 20500 | 20740 | 21255 | 20341 | 23005 | 23848 | 23048 | 22994 | 22195 | 24459 | 25429 | 26407 | 25079 | 25396 | 24401 | 26624 | 27266 | 27329 | 26671
68 | 68 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 20 | 20027 | 20142 | 20281 | 20942 | 20254 | 22859 | 23830 | 22945 | 22680 | 22300 | 24745 | 25818 | 26906 | 25278 | 25563 | 24851 | 27339 | 28056 | 28035 | 27049
69 | 69 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 21 | 19651 | 19819 | 19949 | 20670 | 20107 | 22615 | 23846 | 22878 | 22670 | 22433 | 25054 | 26121 | 27505 | 25754 | 25990 | 25405 | 28090 | 29049 | 28853 | 27771
70 | 70 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 22 | 18933 | 19229 | 19376 | 20043 | 19577 | 22066 | 23170 | 22448 | 22318 | 22102 | 24797 | 25946 | 27193 | 25686 | 25794 | 25294 | 28128 | 29196 | 28935 | 27862
71 | 71 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 23 | 17994 | 18423 | 18698 | 19332 | 19008 | 21295 | 22331 | 21830 | 21837 | 21673 | 24158 | 25409 | 26615 | 25347 | 25421 | 25006 | 27640 | 28941 | 28530 | 27610
72 | 72 | 3 | 1 | 3 | Winter | 1 | 3 | Winter | 24 | 16964 | 17463 | 17863 | 18537 | 18313 | 20458 | 21387 | 21149 | 21302 | 21189 | 23467 | 24786 | 25854 | 24909 | 24931 | 24545 | 27010 | 28295 | 28039 | 27230
73 | 73 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 1 | 16346 | 17020 | 17021 | 16856 | 18550 | 19587 | 20336 | 20636 | 20136 | 21755 | 23064 | 24018 | 25044 | 23266 | 23095 | 25464 | 26714 | 27623 | 27023 | 25319
74 | 74 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 2 | 15997 | 16583 | 16588 | 16543 | 18146 | 19218 | 19920 | 20249 | 19763 | 21385 | 22629 | 23591 | 24409 | 22796 | 22747 | 24974 | 26187 | 26904 | 26502 | 24800
75 | 75 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 3 | 15847 | 16348 | 16385 | 16361 | 18059 | 19169 | 19852 | 20202 | 19716 | 21369 | 22557 | 23514 | 24121 | 22607 | 22529 | 24817 | 25934 | 26524 | 26300 | 24561
76 | 76 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 4 | 15836 | 16231 | 16260 | 16219 | 17949 | 19076 | 19655 | 19966 | 19471 | 21062 | 22189 | 23063 | 23521 | 22077 | 21966 | 24175 | 25240 | 25701 | 25517 | 23881
77 | 77 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 5 | 15950 | 16208 | 16217 | 16141 | 18019 | 19118 | 19535 | 19734 | 19159 | 20849 | 21793 | 22603 | 22951 | 21444 | 21345 | 23624 | 24463 | 24865 | 24619 | 23074
78 | 78 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 6 | 16383 | 16337 | 16250 | 16195 | 18329 | 19439 | 19661 | 19554 | 18896 | 20835 | 21674 | 22395 | 22553 | 20796 | 20846 | 23260 | 23965 | 24203 | 23706 | 22253
79 | 79 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 7 | 17542 | 16796 | 16636 | 16486 | 19139 | 20464 | 20508 | 19780 | 19126 | 21349 | 22271 | 23082 | 22924 | 20741 | 20749 | 23372 | 24319 | 24398 | 23438 | 22097
80 | 80 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 8 | 18997 | 17629 | 17261 | 16923 | 20397 | 21869 | 21797 | 20645 | 19700 | 22437 | 23448 | 24330 | 23972 | 21267 | 21059 | 24178 | 25341 | 25363 | 24070 | 22588
81 | 81 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 9 | 19329 | 18248 | 17847 | 17202 | 20926 | 22225 | 22240 | 21334 | 20296 | 22922 | 23843 | 24615 | 24327 | 21815 | 21263 | 24546 | 25558 | 25671 | 24520 | 23107
82 | 82 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 10 | 19331 | 18654 | 18318 | 17613 | 21129 | 22230 | 22304 | 21745 | 20782 | 23261 | 24021 | 24672 | 24471 | 22414 | 21816 | 24985 | 25876 | 25858 | 25029 | 23748
83 | 83 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 11 | 19298 | 18601 | 18437 | 17846 | 21039 | 22059 | 22126 | 21469 | 20712 | 23156 | 23932 | 24453 | 24296 | 22845 | 22406 | 24977 | 26334 | 25729 | 24788 | 24213
84 | 84 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 12 | 19191 | 18422 | 18372 | 17861 | 20644 | 21744 | 21731 | 20965 | 20352 | 22561 | 23568 | 24003 | 23809 | 22864 | 22533 | 24406 | 26391 | 25270 | 24325 | 24233
85 | 85 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 13 | 19015 | 18312 | 18366 | 17979 | 20514 | 21496 | 21564 | 20718 | 20247 | 22355 | 23377 | 23696 | 23599 | 22904 | 22660 | 24183 | 26358 | 25059 | 23920 | 24251
86 | 86 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 14 | 18924 | 18069 | 18233 | 17889 | 20274 | 21278 | 21357 | 20357 | 20036 | 22006 | 23292 | 23398 | 23300 | 22891 | 22654 | 23761 | 26476 | 24731 | 23474 | 24207
87 | 87 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 15 | 18893 | 18074 | 18280 | 17971 | 20337 | 21258 | 21203 | 20340 | 20080 | 22014 | 23290 | 23339 | 22980 | 22575 | 22334 | 23706 | 26111 | 24374 | 23347 | 23872
88 | 88 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 16 | 19032 | 18487 | 18811 | 18410 | 20907 | 21413 | 21361 | 20801 | 20653 | 22664 | 23581 | 23430 | 23121 | 22465 | 22080 | 24318 | 25695 | 24442 | 23548 | 23734
89 | 89 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 17 | 19719 | 19337 | 19784 | 19286 | 21725 | 22091 | 22051 | 21725 | 21758 | 23481 | 24417 | 24236 | 23849 | 23209 | 22644 | 25094 | 26183 | 25190 | 24494 | 24504
90 | 90 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 18 | 20803 | 20293 | 20986 | 20324 | 22485 | 23243 | 22890 | 22762 | 22876 | 24110 | 25166 | 25472 | 25060 | 24628 | 23822 | 25913 | 27141 | 26533 | 26090 | 25986
91 | 91 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 19 | 20765 | 20029 | 20948 | 20054 | 22318 | 23387 | 22690 | 22654 | 22964 | 24032 | 25339 | 25975 | 25465 | 25037 | 24095 | 26321 | 27619 | 27158 | 26488 | 26515
92 | 92 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 20 | 20626 | 19583 | 20638 | 19977 | 22130 | 23371 | 22571 | 22304 | 22848 | 24257 | 25633 | 26408 | 25928 | 25168 | 24527 | 27014 | 28410 | 27875 | 26882 | 26801
93 | 93 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 21 | 20438 | 19250 | 20340 | 19806 | 21972 | 23326 | 22427 | 22209 | 22820 | 24471 | 25871 | 26903 | 26405 | 25536 | 25027 | 27725 | 29106 | 28671 | 27594 | 27369
94 | 94 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 22 | 19711 | 18696 | 19724 | 19293 | 21393 | 22645 | 21975 | 21835 | 22401 | 24193 | 25701 | 26556 | 26301 | 25330 | 24907 | 27741 | 29227 | 28761 | 27703 | 27288
95 | 95 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 23 | 18663 | 17957 | 18947 | 18666 | 20468 | 21718 | 21266 | 21262 | 21823 | 23481 | 25163 | 25894 | 25732 | 24895 | 24570 | 27196 | 28851 | 28303 | 27407 | 26923
96 | 96 | 4 | 1 | 4 | Winter | 1 | 4 | Winter | 24 | 17494 | 17112 | 18101 | 17942 | 19529 | 20723 | 20531 | 20665 | 21238 | 22782 | 24539 | 25118 | 25175 | 24407 | 24104 | 26560 | 28303 | 27788 | 27020 | 26470
97 | 97 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 1 | 16555 | 16226 | 16392 | 18132 | 18916 | 19711 | 20082 | 19651 | 19626 | 22465 | 23322 | 24148 | 24101 | 22422 | 24819 | 26086 | 26766 | 26611 | 24974 | 24439
98 | 98 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 2 | 16032 | 15717 | 15991 | 17618 | 18393 | 19175 | 19563 | 19137 | 19223 | 21901 | 22771 | 23520 | 23637 | 22072 | 24329 | 25561 | 26284 | 26076 | 24438 | 24044
99 | 99 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 3 | 15774 | 15431 | 15729 | 17437 | 18206 | 19001 | 19402 | 18963 | 19046 | 21734 | 22600 | 23279 | 23540 | 21893 | 24207 | 25341 | 26106 | 25897 | 24211 | 23812
100 | 100 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 4 | 15668 | 15294 | 15560 | 17313 | 18067 | 18807 | 19175 | 18731 | 18763 | 21402 | 22190 | 22722 | 22954 | 21333 | 23573 | 24655 | 25353 | 25100 | 23520 | 23121
101 | 101 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 5 | 15710 | 15245 | 15490 | 17402 | 18051 | 18728 | 18999 | 18474 | 18533 | 21080 | 21812 | 22229 | 22325 | 20757 | 23060 | 23912 | 24557 | 24208 | 22711 | 22376
102 | 102 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 6 | 16069 | 15319 | 15595 | 17771 | 18419 | 18921 | 18918 | 18309 | 18421 | 21063 | 21721 | 21949 | 21713 | 20322 | 22762 | 23477 | 24051 | 23343 | 21917 | 21797
103 | 103 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 7 | 16984 | 15674 | 15897 | 18616 | 19412 | 19783 | 19194 | 18592 | 18492 | 21711 | 22462 | 22379 | 21617 | 20234 | 22898 | 23855 | 24551 | 23072 | 21746 | 21627
104 | 104 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 8 | 18235 | 16325 | 16346 | 19917 | 20754 | 21089 | 20100 | 19214 | 18902 | 22946 | 23751 | 23472 | 22344 | 20571 | 23752 | 24908 | 25648 | 23719 | 22255 | 21946
105 | 105 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 9 | 18660 | 16924 | 16634 | 20436 | 21180 | 21532 | 20803 | 19836 | 19224 | 23379 | 24056 | 23851 | 22857 | 20793 | 24137 | 25145 | 25922 | 24186 | 22779 | 22123
106 | 106 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 10 | 18699 | 17359 | 17004 | 20561 | 21227 | 21545 | 21154 | 20268 | 19612 | 23496 | 24047 | 23931 | 23265 | 21290 | 24515 | 25412 | 26021 | 24638 | 23366 | 22646
107 | 107 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 11 | 18497 | 17318 | 17077 | 20274 | 21000 | 21195 | 20695 | 20023 | 19495 | 23191 | 23605 | 23536 | 22776 | 21668 | 24290 | 25657 | 25668 | 24186 | 23624 | 23049
108 | 108 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 12 | 18412 | 17354 | 17198 | 19976 | 20857 | 20887 | 20271 | 19746 | 19292 | 22858 | 23186 | 23098 | 22360 | 21852 | 23765 | 25759 | 25282 | 23771 | 23692 | 23228
109 | 109 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 13 | 18283 | 17327 | 17310 | 19838 | 20692 | 20702 | 20017 | 19628 | 19274 | 22642 | 22861 | 22862 | 21952 | 21955 | 23515 | 25697 | 24879 | 23340 | 23683 | 23310
110 | 110 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 14 | 18160 | 17212 | 17254 | 19637 | 20675 | 20513 | 19676 | 19431 | 19100 | 22567 | 22578 | 22596 | 21572 | 21985 | 23124 | 25842 | 24536 | 22920 | 23659 | 23308
111 | 111 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 15 | 18013 | 17250 | 17316 | 19687 | 20635 | 20316 | 19608 | 19416 | 19084 | 22495 | 22455 | 22327 | 21517 | 21708 | 23116 | 25521 | 24453 | 22836 | 23369 | 23005
112 | 112 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 16 | 18246 | 17845 | 17832 | 20327 | 21035 | 20585 | 20182 | 20102 | 19654 | 22926 | 22694 | 22542 | 21825 | 21516 | 23790 | 25163 | 24470 | 23091 | 23284 | 22782
113 | 113 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 17 | 18958 | 18883 | 18781 | 21233 | 21938 | 21373 | 21202 | 21302 | 20592 | 23876 | 23610 | 23314 | 22796 | 22122 | 24607 | 25696 | 25071 | 24086 | 24099 | 23415
114 | 114 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 18 | 19853 | 20146 | 19878 | 22130 | 22768 | 22355 | 22363 | 22532 | 21745 | 24722 | 24944 | 24494 | 24308 | 23296 | 25439 | 26654 | 26244 | 25711 | 25611 | 24673
115 | 115 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 19 | 19706 | 20168 | 19674 | 22030 | 22775 | 22244 | 22340 | 22697 | 21790 | 24947 | 25508 | 24853 | 24516 | 23557 | 25829 | 27120 | 26873 | 26133 | 26170 | 25056
116 | 116 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 20 | 19365 | 19858 | 19593 | 21808 | 22720 | 22117 | 21968 | 22553 | 21916 | 25191 | 25901 | 25207 | 24642 | 23928 | 26445 | 27849 | 27644 | 26497 | 26417 | 25550
117 | 117 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 21 | 19036 | 19567 | 19406 | 21619 | 22480 | 21932 | 21819 | 22478 | 21994 | 25347 | 26316 | 25579 | 25026 | 24363 | 27095 | 28486 | 28601 | 27184 | 26980 | 26180
118 | 118 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 22 | 18471 | 18952 | 18879 | 21002 | 21945 | 21441 | 21390 | 22013 | 21657 | 25124 | 25906 | 25428 | 24944 | 24226 | 27083 | 28586 | 28741 | 27283 | 26904 | 26158
119 | 119 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 23 | 17634 | 18159 | 18232 | 20050 | 21152 | 20679 | 20764 | 21374 | 21121 | 24514 | 25177 | 24870 | 24590 | 23907 | 26561 | 28238 | 28461 | 27022 | 26581 | 25900
120 | 120 | 5 | 1 | 5 | Winter | 1 | 5 | Winter | 24 | 16650 | 17283 | 17451 | 19062 | 20233 | 19867 | 20090 | 20707 | 20578 | 23850 | 24355 | 24280 | 24126 | 23432 | 25911 | 27676 | 27808 | 26620 | 26126 | 25452
121 | 121 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 1 | 16299 | 15680 | 17679 | 18444 | 18873 | 19377 | 19041 | 18967 | 21007 | 22459 | 23223 | 23567 | 22747 | 24435 | 25756 | 26472 | 27295 | 24927 | 24430 | 26638
122 | 122 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 2 | 15873 | 15374 | 17263 | 18018 | 18509 | 18979 | 18661 | 18709 | 20654 | 22091 | 22780 | 23151 | 22302 | 23984 | 25270 | 26026 | 26602 | 24419 | 24066 | 26147
123 | 123 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 3 | 15604 | 15105 | 17099 | 17857 | 18416 | 18868 | 18555 | 18614 | 20620 | 22051 | 22676 | 23040 | 22114 | 23843 | 25028 | 25823 | 26214 | 24155 | 23797 | 25942
124 | 124 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 4 | 15482 | 14951 | 17006 | 17748 | 18338 | 18690 | 18375 | 18392 | 20361 | 21742 | 22213 | 22535 | 21617 | 23275 | 24398 | 25129 | 25400 | 23492 | 23122 | 25212
125 | 125 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 5 | 15464 | 14911 | 17123 | 17769 | 18415 | 18568 | 18176 | 18228 | 20221 | 21460 | 21817 | 21991 | 21041 | 22821 | 23712 | 24382 | 24595 | 22711 | 22392 | 24573
126 | 126 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 6 | 15615 | 15006 | 17496 | 18166 | 18774 | 18529 | 18070 | 18183 | 20295 | 21460 | 21624 | 21462 | 20462 | 22570 | 23318 | 23907 | 23972 | 21925 | 21801 | 24119
127 | 127 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 7 | 16079 | 15347 | 18401 | 19205 | 19809 | 18854 | 18422 | 18330 | 20882 | 22294 | 22137 | 21450 | 20446 | 22763 | 23743 | 24446 | 24182 | 21775 | 21640 | 24141
128 | 128 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 8 | 16911 | 15785 | 19716 | 20552 | 21214 | 19756 | 19055 | 18760 | 22017 | 23615 | 23252 | 22199 | 21003 | 23632 | 24819 | 25548 | 25163 | 22276 | 21946 | 24912
129 | 129 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 9 | 17518 | 16053 | 20226 | 20966 | 21548 | 20438 | 19669 | 19086 | 22512 | 23925 | 23633 | 22721 | 21562 | 24019 | 25064 | 25816 | 25472 | 22788 | 22115 | 25260
130 | 130 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 10 | 17921 | 16471 | 20372 | 21047 | 21554 | 20821 | 20135 | 19512 | 22824 | 23938 | 23738 | 23156 | 22141 | 24420 | 25355 | 25946 | 25647 | 23407 | 22679 | 25723
131 | 131 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 11 | 17793 | 16695 | 20217 | 20963 | 21330 | 20504 | 20025 | 19538 | 22630 | 23589 | 23438 | 22766 | 22469 | 24288 | 25707 | 25695 | 25418 | 23768 | 23190 | 25652
132 | 132 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 12 | 17663 | 16864 | 19969 | 20872 | 21115 | 20151 | 19816 | 19418 | 22150 | 23214 | 23044 | 22283 | 22469 | 23694 | 25738 | 25240 | 24938 | 23769 | 23304 | 25076
133 | 133 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 13 | 17498 | 16951 | 19805 | 20665 | 20783 | 19849 | 19637 | 19335 | 21842 | 22804 | 22719 | 21878 | 22472 | 23444 | 25673 | 24834 | 24687 | 23758 | 23394 | 24811
134 | 134 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 14 | 17338 | 16999 | 19682 | 20716 | 20642 | 19590 | 19521 | 19249 | 21587 | 22608 | 22545 | 21543 | 22517 | 23097 | 25857 | 24526 | 24419 | 23772 | 23423 | 24421
135 | 135 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 15 | 17419 | 17132 | 19831 | 20767 | 20686 | 19632 | 19618 | 19351 | 21648 | 22616 | 22401 | 21543 | 22295 | 23143 | 25584 | 24497 | 24147 | 23528 | 23167 | 24433
136 | 136 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 16 | 17756 | 17469 | 20226 | 20959 | 20741 | 19976 | 20057 | 19660 | 22146 | 22595 | 22359 | 21808 | 22184 | 23772 | 25173 | 24464 | 24211 | 23380 | 22881 | 25013
137 | 137 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 17 | 18543 | 18281 | 20988 | 21702 | 21355 | 20822 | 21067 | 20396 | 22876 | 23298 | 22925 | 22700 | 22904 | 24511 | 25627 | 24995 | 24930 | 24121 | 23438 | 25770
138 | 138 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 18 | 19588 | 19366 | 21966 | 22608 | 22709 | 22067 | 22364 | 21594 | 23730 | 24668 | 24139 | 24155 | 24320 | 25319 | 26560 | 26145 | 26288 | 25636 | 24689 | 26659
139 | 139 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 19 | 19319 | 19079 | 21776 | 22506 | 22864 | 21925 | 22396 | 21477 | 23605 | 25017 | 24300 | 24285 | 24703 | 25649 | 26979 | 26739 | 26936 | 26189 | 25063 | 27156
140 | 140 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 20 | 18838 | 18923 | 21461 | 22350 | 22806 | 21458 | 22144 | 21475 | 23715 | 25230 | 24492 | 24325 | 24742 | 26196 | 27648 | 27461 | 27610 | 26433 | 25555 | 27926
141 | 141 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 21 | 18486 | 18706 | 21215 | 22044 | 22720 | 21222 | 21976 | 21454 | 23831 | 25509 | 24718 | 24615 | 25037 | 26771 | 28211 | 28355 | 28348 | 26968 | 26170 | 28727
142 | 142 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 22 | 17905 | 18157 | 20546 | 21450 | 21989 | 20725 | 21434 | 21040 | 23465 | 25012 | 24484 | 24447 | 24778 | 26689 | 28248 | 28442 | 28400 | 26852 | 26118 | 28815
143 | 143 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 23 | 17194 | 17514 | 19606 | 20668 | 21052 | 20108 | 20808 | 20518 | 22729 | 24314 | 23941 | 24051 | 24366 | 26143 | 27877 | 28150 | 27971 | 26528 | 25863 | 28369
144 | 144 | 6 | 1 | 6 | Winter | 1 | 6 | Winter | 24 | 16350 | 16735 | 18582 | 19733 | 19995 | 19410 | 20120 | 19954 | 21994 | 23504 | 23365 | 23567 | 23851 | 25483 | 27304 | 27473 | 27452 | 26057 | 25412 | 27748
145 | 145 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 1 | 15233 | 16604 | 17624 | 18044 | 18669 | 18138 | 18121 | 20061 | 21233 | 22152 | 22468 | 21812 | 21747 | 24834 | 25620 | 26496 | 26135 | 23891 | 26126 | 27182
146 | 146 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 2 | 14799 | 16163 | 17178 | 17655 | 18243 | 17735 | 17843 | 19694 | 20828 | 21727 | 22066 | 21368 | 21420 | 24341 | 25168 | 25796 | 25611 | 23498 | 25605 | 26632
147 | 147 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 3 | 14544 | 15985 | 17001 | 17543 | 18121 | 17603 | 17723 | 19644 | 20757 | 21641 | 21968 | 21234 | 21255 | 24157 | 25025 | 25468 | 25439 | 23272 | 25444 | 26379
148 | 148 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 4 | 14419 | 15891 | 16885 | 17466 | 17945 | 17420 | 17509 | 19405 | 20477 | 21225 | 21503 | 20786 | 20754 | 23563 | 24368 | 24683 | 24676 | 22607 | 24706 | 25631
149 | 149 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 5 | 14373 | 16006 | 16919 | 17571 | 17898 | 17251 | 17386 | 19325 | 20232 | 20911 | 21028 | 20266 | 20225 | 22928 | 23666 | 23914 | 23824 | 21885 | 24067 | 24781
150 | 150 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 6 | 14459 | 16402 | 17340 | 17993 | 18124 | 17203 | 17424 | 19495 | 20308 | 20843 | 20607 | 19770 | 19837 | 22599 | 23250 | 23339 | 22985 | 21314 | 23628 | 24226
151 | 151 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 7 | 14840 | 17362 | 18406 | 19075 | 19024 | 17605 | 17648 | 20190 | 21067 | 21462 | 20691 | 19814 | 19802 | 23077 | 23827 | 23577 | 22755 | 21164 | 23660 | 24530
152 | 152 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 8 | 15514 | 18738 | 19778 | 20500 | 20331 | 18268 | 18124 | 21410 | 22365 | 22652 | 21508 | 20402 | 20156 | 24198 | 24953 | 24578 | 23415 | 21480 | 24449 | 25529
153 | 153 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 9 | 16129 | 19264 | 20228 | 20853 | 20776 | 18902 | 18482 | 21959 | 22842 | 23082 | 22093 | 21006 | 20411 | 24490 | 25258 | 24921 | 23891 | 21677 | 24822 | 25746
154 | 154 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 10 | 16655 | 19433 | 20359 | 20916 | 20900 | 19426 | 18970 | 22330 | 23071 | 23251 | 22601 | 21590 | 20954 | 24791 | 25393 | 25103 | 24386 | 22250 | 25295 | 26091
155 | 155 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 11 | 17037 | 19593 | 20652 | 21111 | 21125 | 19803 | 19516 | 22678 | 23454 | 23514 | 22787 | 22019 | 21544 | 25236 | 25241 | 24976 | 24143 | 22861 | 25326 | 26581
156 | 156 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 12 | 17254 | 19587 | 20816 | 21178 | 21138 | 19917 | 19737 | 22557 | 23537 | 23467 | 22658 | 22083 | 21724 | 25328 | 24847 | 24548 | 23722 | 23045 | 24814 | 26691
157 | 157 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 13 | 17295 | 19548 | 20757 | 21025 | 21066 | 19949 | 19886 | 22494 | 23483 | 23405 | 22513 | 22098 | 21835 | 25272 | 24452 | 24306 | 23298 | 23140 | 24560 | 26625
158 | 158 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 14 | 17273 | 19501 | 20869 | 20973 | 21045 | 19953 | 19934 | 22401 | 23649 | 23411 | 22357 | 22099 | 21849 | 25407 | 24098 | 23995 | 22862 | 23114 | 24124 | 26738
159 | 159 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 15 | 17187 | 19448 | 20692 | 20769 | 20674 | 19759 | 19729 | 22129 | 23339 | 22905 | 21994 | 21800 | 21542 | 25054 | 23990 | 23644 | 22740 | 22779 | 24049 | 26367
160 | 160 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 16 | 17422 | 19613 | 20636 | 20539 | 20406 | 19838 | 19643 | 22157 | 23029 | 22388 | 21781 | 21697 | 21292 | 24647 | 23962 | 23714 | 22930 | 22487 | 24621 | 25926
161 | 161 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 17 | 18175 | 20240 | 21200 | 20942 | 20798 | 20591 | 20090 | 22575 | 23435 | 22593 | 22312 | 22401 | 21810 | 25084 | 24475 | 24430 | 23845 | 23030 | 25369 | 26393
162 | 162 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 18 | 19313 | 21082 | 21975 | 22109 | 21667 | 21704 | 21057 | 23192 | 24108 | 23496 | 23461 | 23720 | 22915 | 25942 | 25561 | 25722 | 25437 | 24244 | 26203 | 27368
163 | 163 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 19 | 19276 | 20866 | 21871 | 22251 | 21484 | 21746 | 20933 | 23043 | 24170 | 23592 | 23537 | 24047 | 23117 | 26307 | 26115 | 26328 | 25847 | 24617 | 26699 | 27903
164 | 164 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 20 | 18915 | 20521 | 21665 | 22150 | 21277 | 21449 | 20867 | 23058 | 24223 | 23657 | 23469 | 24023 | 23422 | 26901 | 26779 | 26959 | 26184 | 25098 | 27460 | 28737
165 | 165 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 21 | 18596 | 20240 | 21329 | 22038 | 21027 | 21240 | 20792 | 23083 | 24251 | 23780 | 23667 | 24247 | 23799 | 27399 | 27612 | 27658 | 26844 | 25711 | 28256 | 29485
166 | 166 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 22 | 17968 | 19567 | 20721 | 21304 | 20502 | 20677 | 20348 | 22665 | 23953 | 23499 | 23456 | 23953 | 23619 | 27409 | 27687 | 27701 | 26907 | 25665 | 28360 | 29680
167 | 167 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 23 | 17189 | 18606 | 19926 | 20352 | 19748 | 20034 | 19811 | 21895 | 23371 | 22943 | 23046 | 23505 | 23279 | 27007 | 27367 | 27243 | 26619 | 25398 | 27893 | 29363
168 | 168 | 7 | 1 | 7 | Winter | 1 | 7 | Winter | 24 | 16320 | 17571 | 18950 | 19269 | 18914 | 19303 | 19206 | 21122 | 22705 | 22369 | 22550 | 22980 | 22803 | 26432 | 26688 | 26719 | 26205 | 24946 | 27288 | 28834
169 | 169 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 1 | 14900 | 17144 | 17853 | 18507 | 18678 | 17850 | 19784 | 20869 | 21605 | 22045 | 21437 | 21442 | 23811 | 25395 | 26275 | 25971 | 24614 | 26180 | 27270 | 27717
170 | 170 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 2 | 14591 | 16718 | 17461 | 18068 | 18255 | 17561 | 19411 | 20460 | 21241 | 21670 | 21015 | 21140 | 23362 | 24909 | 25597 | 25460 | 24092 | 25671 | 26725 | 27220
171 | 171 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 3 | 14323 | 16511 | 17321 | 17913 | 18115 | 17413 | 19345 | 20377 | 21191 | 21600 | 20899 | 20992 | 23286 | 24786 | 25273 | 25306 | 23867 | 25510 | 26475 | 27013
172 | 172 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 4 | 14146 | 16407 | 17252 | 17751 | 17917 | 17210 | 19137 | 20139 | 20910 | 21193 | 20497 | 20533 | 22752 | 24181 | 24528 | 24567 | 23208 | 24776 | 25722 | 26215
173 | 173 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 5 | 14113 | 16458 | 17396 | 17748 | 17831 | 17133 | 19125 | 19978 | 20715 | 20809 | 20055 | 20075 | 22363 | 23566 | 23821 | 23761 | 22453 | 24164 | 24893 | 25366
174 | 174 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 6 | 14220 | 16894 | 17865 | 18021 | 17846 | 17211 | 19368 | 20134 | 20829 | 20479 | 19633 | 19760 | 22184 | 23203 | 23301 | 22965 | 21702 | 23748 | 24351 | 24806
175 | 175 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 7 | 14559 | 17955 | 18964 | 18922 | 18184 | 17435 | 20116 | 20930 | 21737 | 20608 | 19708 | 19754 | 22410 | 23744 | 23553 | 22735 | 21553 | 23777 | 24640 | 25273
176 | 176 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 8 | 15014 | 19355 | 20403 | 20229 | 19116 | 17914 | 21398 | 22277 | 23130 | 21479 | 20337 | 20144 | 23321 | 24956 | 24580 | 23420 | 22079 | 24591 | 25655 | 26388
177 | 177 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 9 | 15279 | 19779 | 20741 | 20640 | 19783 | 18239 | 21932 | 22754 | 23467 | 22078 | 20944 | 20400 | 23738 | 25207 | 24913 | 23893 | 22602 | 24947 | 25860 | 26651
178 | 178 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 10 | 15737 | 19908 | 20799 | 20752 | 20218 | 18710 | 22271 | 22965 | 23548 | 22576 | 21516 | 20932 | 24136 | 25286 | 25087 | 24380 | 23223 | 25408 | 26200 | 26801
179 | 179 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 11 | 16049 | 19961 | 20762 | 20743 | 20126 | 19018 | 22363 | 23107 | 23541 | 22525 | 21707 | 21288 | 23869 | 24879 | 24723 | 23902 | 23458 | 25202 | 26458 | 26441
180 | 180 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 12 | 16407 | 20120 | 20834 | 20759 | 20064 | 19237 | 22226 | 23180 | 23518 | 22374 | 21747 | 21446 | 23322 | 24471 | 24270 | 23454 | 23500 | 24667 | 26547 | 26028
181 | 181 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 13 | 16561 | 20001 | 20638 | 20642 | 19915 | 19346 | 22117 | 23080 | 23318 | 22183 | 21715 | 21520 | 23033 | 24082 | 23985 | 22991 | 23455 | 24365 | 26437 | 25590
182 | 182 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 14 | 16591 | 20034 | 20503 | 20534 | 19695 | 19318 | 21951 | 23165 | 23217 | 21966 | 21650 | 21470 | 22571 | 23680 | 23594 | 22491 | 23343 | 23859 | 26472 | 25143
183 | 183 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 15 | 16660 | 20015 | 20461 | 20330 | 19598 | 19277 | 21841 | 23010 | 23008 | 21739 | 21490 | 21306 | 22670 | 23739 | 23387 | 22503 | 23149 | 23921 | 26235 | 25145
184 | 184 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 16 | 16947 | 20130 | 20421 | 20259 | 19766 | 19384 | 22028 | 22893 | 22678 | 21689 | 21548 | 21219 | 23443 | 23920 | 23620 | 22847 | 23143 | 24643 | 25941 | 25220
185 | 185 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 17 | 17722 | 20819 | 20943 | 20779 | 20486 | 19963 | 22574 | 23418 | 23144 | 22311 | 22346 | 21825 | 24272 | 24807 | 24421 | 23857 | 23980 | 25492 | 26504 | 25848
186 | 186 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 18 | 18672 | 21655 | 22116 | 21677 | 21593 | 20991 | 23251 | 24137 | 24266 | 23423 | 23652 | 22907 | 25043 | 26167 | 25736 | 25452 | 25489 | 26357 | 27502 | 27030
187 | 187 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 19 | 18362 | 21515 | 22215 | 21450 | 21460 | 20847 | 23062 | 24130 | 24558 | 23400 | 23902 | 23041 | 25298 | 26818 | 26281 | 25819 | 26031 | 26838 | 28018 | 27678
188 | 188 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 20 | 18193 | 21274 | 22105 | 21239 | 20991 | 20779 | 23029 | 24126 | 24684 | 23264 | 23827 | 23305 | 25792 | 27403 | 26874 | 26144 | 26278 | 27600 | 28861 | 28489
189 | 189 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 21 | 17977 | 20916 | 21963 | 20957 | 20716 | 20657 | 22976 | 24054 | 24868 | 23352 | 23965 | 23601 | 26290 | 28087 | 27514 | 26744 | 26797 | 28377 | 29598 | 29514
190 | 190 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 22 | 17428 | 20276 | 21203 | 20401 | 20190 | 20165 | 22492 | 23678 | 24312 | 23075 | 23610 | 23362 | 26176 | 27835 | 27502 | 26769 | 26658 | 28448 | 29770 | 29682
191 | 191 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 23 | 16750 | 19384 | 20197 | 19599 | 19520 | 19568 | 21654 | 23024 | 23552 | 22598 | 23104 | 22964 | 25559 | 27251 | 26997 | 26442 | 26276 | 27939 | 29419 | 29413
192 | 192 | 8 | 1 | 8 | Winter | 1 | 8 | Winter | 24 | 15969 | 18354 | 19050 | 18716 | 18769 | 18909 | 20814 | 22299 | 22703 | 22084 | 22560 | 22465 | 24888 | 26497 | 26454 | 26012 | 25783 | 27312 | 28877 | 28760
193 | 193 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 1 | 16054 | 17148 | 18233 | 18446 | 17947 | 19100 | 20179 | 21217 | 22079 | 21061 | 22156 | 23064 | 24428 | 25916 | 25878 | 24575 | 25504 | 26937 | 27818 | 28410
194 | 194 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 2 | 15623 | 16792 | 17821 | 17961 | 17568 | 18713 | 19758 | 20889 | 21708 | 20729 | 21886 | 22641 | 23961 | 25458 | 25349 | 24166 | 25150 | 26400 | 27433 | 27877
195 | 195 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 3 | 15446 | 16636 | 17673 | 17790 | 17461 | 18647 | 19696 | 20869 | 21697 | 20730 | 21953 | 22572 | 23789 | 25282 | 25160 | 24102 | 25135 | 26144 | 27159 | 27632
196 | 196 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 4 | 15375 | 16602 | 17548 | 17616 | 17365 | 18495 | 19519 | 20683 | 21383 | 20493 | 21697 | 22108 | 23240 | 24600 | 24453 | 23603 | 24644 | 25410 | 26353 | 26757
197 | 197 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 5 | 15478 | 16724 | 17558 | 17532 | 17193 | 18503 | 19394 | 20532 | 21156 | 20084 | 21538 | 21763 | 22657 | 23905 | 23703 | 22906 | 24242 | 24575 | 25461 | 25840
198 | 198 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 6 | 15874 | 17213 | 17866 | 17596 | 17189 | 18793 | 19616 | 20733 | 21168 | 19754 | 21715 | 21662 | 22402 | 23447 | 23020 | 22224 | 24088 | 24062 | 24876 | 25169
199 | 199 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 7 | 16839 | 18312 | 18861 | 17953 | 17574 | 19586 | 20459 | 21676 | 21871 | 19881 | 22717 | 21972 | 22923 | 23881 | 22786 | 22133 | 24857 | 24378 | 25351 | 25472
200 | 200 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 8 | 18233 | 19788 | 20223 | 18796 | 18218 | 20871 | 21820 | 23135 | 23144 | 20515 | 24103 | 22942 | 24080 | 25028 | 23357 | 22638 | 26204 | 25405 | 26527 | 26566
201 | 201 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 9 | 18710 | 20103 | 20577 | 19512 | 18836 | 21378 | 22297 | 23447 | 23513 | 21177 | 24401 | 23374 | 24377 | 25332 | 23895 | 23137 | 26464 | 25613 | 26844 | 26858
202 | 202 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 10 | 18864 | 20140 | 20634 | 19912 | 19333 | 21672 | 22474 | 23474 | 23550 | 21700 | 24448 | 23799 | 24706 | 25510 | 24373 | 23705 | 26624 | 25990 | 27175 | 27054
203 | 203 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 11 | 18795 | 20111 | 20602 | 19763 | 19382 | 21600 | 22427 | 23240 | 23298 | 21627 | 24145 | 23739 | 25134 | 25793 | 24115 | 23648 | 26825 | 26462 | 27478 | 27361
204 | 204 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 12 | 18678 | 20071 | 20464 | 19528 | 19258 | 21243 | 22242 | 22914 | 22827 | 21287 | 23682 | 23241 | 25261 | 25682 | 23612 | 23383 | 26753 | 26610 | 27488 | 27240
205 | 205 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 13 | 18537 | 19816 | 20252 | 19332 | 19123 | 21034 | 22027 | 22566 | 22519 | 21071 | 23370 | 22970 | 25170 | 25492 | 23296 | 23018 | 26553 | 26516 | 27142 | 27048
206 | 206 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 14 | 18309 | 19615 | 19977 | 18970 | 18846 | 20665 | 21889 | 22270 | 22160 | 20722 | 23085 | 22495 | 25219 | 25309 | 22792 | 22623 | 26458 | 26537 | 26934 | 26838
207 | 207 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 15 | 18453 | 19620 | 19858 | 19003 | 18943 | 20746 | 21927 | 22233 | 22012 | 20811 | 23016 | 22517 | 24912 | 24778 | 22765 | 22612 | 26018 | 26204 | 26418 | 26264
208 | 208 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 16 | 18821 | 19680 | 19910 | 19343 | 19426 | 21233 | 22153 | 22300 | 22042 | 21315 | 23216 | 23077 | 24455 | 24078 | 23008 | 22944 | 25588 | 25701 | 25605 | 25499
209 | 209 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 17 | 19667 | 20297 | 20538 | 20214 | 20569 | 22040 | 22959 | 23036 | 22628 | 22506 | 23980 | 23836 | 24912 | 24380 | 23895 | 24099 | 25914 | 26197 | 25459 | 25818
210 | 210 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 18 | 20557 | 21472 | 21410 | 21301 | 21750 | 22763 | 23696 | 24163 | 23540 | 23767 | 24859 | 24570 | 25759 | 25463 | 25233 | 25810 | 26959 | 27177 | 26496 | 26998
211 | 211 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 19 | 20308 | 21594 | 21207 | 21090 | 21796 | 22550 | 23651 | 24448 | 23606 | 23952 | 25027 | 24772 | 26059 | 25945 | 25595 | 26237 | 27402 | 27703 | 27063 | 27655
212 | 212 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 20 | 19929 | 21465 | 20992 | 20549 | 21518 | 22452 | 23576 | 24501 | 23685 | 23787 | 25041 | 25149 | 26580 | 26468 | 25792 | 26512 | 27618 | 28510 | 27802 | 28414
213 | 213 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 21 | 19623 | 21298 | 20661 | 20267 | 21222 | 22341 | 23428 | 24569 | 23701 | 23760 | 25080 | 25556 | 26994 | 26989 | 26360 | 26896 | 28010 | 29221 | 28865 | 29197
214 | 214 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 22 | 18918 | 20535 | 20093 | 19728 | 20601 | 21807 | 22999 | 23939 | 23339 | 23341 | 24614 | 25372 | 26938 | 26910 | 26339 | 26697 | 27735 | 29368 | 29256 | 29254
215 | 215 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 23 | 17941 | 19453 | 19273 | 19032 | 19890 | 20944 | 22308 | 23035 | 22735 | 22809 | 23894 | 24733 | 26483 | 26496 | 25991 | 26281 | 27142 | 29019 | 29079 | 28936
216 | 216 | 9 | 1 | 9 | Winter | 1 | 9 | Winter | 24 | 16917 | 18283 | 18309 | 18270 | 19161 | 20075 | 21552 | 22144 | 22069 | 22337 | 23227 | 24076 | 25913 | 25915 | 25571 | 25881 | 26539 | 28494 | 28520 | 28406
217 | 217 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 1 | 16221 | 17356 | 17897 | 17463 | 18322 | 19468 | 20501 | 21311 | 21543 | 21469 | 22805 | 23667 | 24964 | 25228 | 24069 | 25040 | 26517 | 27496 | 28132 | 27606
218 | 218 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 2 | 15816 | 16925 | 17414 | 17065 | 18042 | 19050 | 20180 | 20947 | 21131 | 21237 | 22457 | 23223 | 24604 | 24704 | 23672 | 24696 | 26075 | 27117 | 27604 | 27024
219 | 219 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 3 | 15600 | 16714 | 17190 | 16895 | 17994 | 18929 | 20109 | 20883 | 21020 | 21278 | 22430 | 23077 | 24437 | 24533 | 23626 | 24694 | 26000 | 26849 | 27362 | 26789
220 | 220 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 4 | 15507 | 16596 | 17021 | 16788 | 17920 | 18762 | 19951 | 20605 | 20669 | 21055 | 22032 | 22592 | 23875 | 23876 | 23158 | 24229 | 25346 | 26056 | 26490 | 25962
221 | 221 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 5 | 15545 | 16622 | 16970 | 16646 | 18103 | 18697 | 19873 | 20464 | 20337 | 20968 | 21768 | 22095 | 23290 | 23201 | 22505 | 23867 | 24735 | 25201 | 25602 | 25062
222 | 222 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 6 | 15989 | 16980 | 17079 | 16680 | 18628 | 18985 | 20163 | 20587 | 20099 | 21218 | 21898 | 21921 | 22973 | 22576 | 21863 | 23740 | 24502 | 24631 | 24938 | 24226
223 | 223 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 7 | 17078 | 17994 | 17484 | 17093 | 19826 | 19902 | 21189 | 21384 | 20304 | 22297 | 22435 | 22499 | 23566 | 22383 | 21796 | 24516 | 24765 | 25113 | 25236 | 23895
224 | 224 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 8 | 18440 | 19341 | 18347 | 17732 | 21256 | 21280 | 22683 | 22708 | 21118 | 23722 | 23354 | 23687 | 24862 | 22957 | 22296 | 25855 | 25463 | 26284 | 26315 | 24416
225 | 225 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 9 | 18848 | 19693 | 19069 | 18351 | 21572 | 21762 | 23011 | 23105 | 21791 | 24053 | 23576 | 24007 | 25186 | 23509 | 22814 | 26126 | 25571 | 26601 | 26605 | 24914
226 | 226 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 10 | 18995 | 19778 | 19486 | 18871 | 21596 | 21951 | 23066 | 23176 | 22255 | 24140 | 23860 | 24295 | 25391 | 23948 | 23348 | 26252 | 25944 | 26900 | 26773 | 25404
227 | 227 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 11 | 19175 | 19891 | 19545 | 19162 | 21650 | 22200 | 23175 | 23297 | 22347 | 24237 | 24109 | 24638 | 25582 | 23604 | 23203 | 26377 | 26264 | 27130 | 26999 | 25097
228 | 228 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 12 | 19332 | 19914 | 19498 | 19262 | 21603 | 22287 | 23143 | 23145 | 22180 | 24104 | 23909 | 24692 | 25520 | 23028 | 22872 | 26217 | 26045 | 27062 | 26815 | 24519
229 | 229 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 13 | 19256 | 19827 | 19441 | 19276 | 21532 | 22232 | 22970 | 23042 | 22084 | 23992 | 23799 | 24636 | 25266 | 22759 | 22553 | 26067 | 25899 | 26753 | 26656 | 24229
230 | 230 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 14 | 19333 | 19744 | 19274 | 19223 | 21568 | 22347 | 22949 | 22977 | 21937 | 24026 | 23595 | 24758 | 25182 | 22323 | 22233 | 26043 | 25613 | 26618 | 26512 | 23757
231 | 231 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 15 | 19211 | 19475 | 19139 | 19114 | 21307 | 22129 | 22638 | 22532 | 21635 | 23623 | 23196 | 24448 | 24725 | 22296 | 22211 | 25598 | 25155 | 26095 | 25938 | 23709
232 | 232 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 16 | 19209 | 19339 | 19234 | 19295 | 21196 | 21971 | 22284 | 22097 | 21457 | 23296 | 23274 | 24088 | 24120 | 22640 | 22629 | 25259 | 25248 | 25373 | 25261 | 24004
233 | 233 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 17 | 19857 | 19811 | 19903 | 20209 | 21590 | 22503 | 22703 | 22338 | 22000 | 23664 | 23651 | 24563 | 24248 | 23540 | 23799 | 25606 | 25664 | 25231 | 25585 | 24920
234 | 234 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 18 | 20702 | 20688 | 20964 | 21382 | 22510 | 23287 | 23838 | 23235 | 23075 | 24505 | 24198 | 25392 | 25434 | 24857 | 25481 | 26646 | 26177 | 26260 | 26761 | 26324
235 | 235 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 19 | 20565 | 20450 | 20717 | 21404 | 22498 | 23227 | 24078 | 23246 | 22934 | 24599 | 24251 | 25608 | 25941 | 25148 | 25863 | 27049 | 26555 | 26809 | 27399 | 26774
236 | 236 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 20 | 20276 | 20206 | 20144 | 21114 | 22238 | 23097 | 24069 | 23230 | 22651 | 24520 | 24463 | 26053 | 26393 | 25296 | 26110 | 27244 | 27168 | 27555 | 28157 | 27100
237 | 237 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 21 | 19890 | 19855 | 19823 | 20780 | 21916 | 22860 | 24050 | 23131 | 22648 | 24470 | 24681 | 26355 | 27026 | 25778 | 26429 | 27585 | 27845 | 28580 | 28916 | 27841
238 | 238 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 22 | 19246 | 19285 | 19274 | 20159 | 21222 | 22386 | 23377 | 22715 | 22318 | 23969 | 24455 | 26256 | 26973 | 25734 | 26231 | 27315 | 27889 | 28979 | 28994 | 27956
239 | 239 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 23 | 18324 | 18435 | 18538 | 19404 | 20271 | 21638 | 22409 | 22050 | 21777 | 23211 | 23831 | 25748 | 26447 | 25350 | 25784 | 26689 | 27444 | 28772 | 28657 | 27652
240 | 240 | 10 | 1 | 10 | Winter | 1 | 10 | Winter | 24 | 17304 | 17446 | 17746 | 18655 | 19375 | 20834 | 21462 | 21324 | 21263 | 22535 | 23201 | 25162 | 25769 | 24927 | 25381 | 26087 | 26862 | 28227 | 28150 | 27285
241 | 241 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 1 | 16100 | 16965 | 16894 | 17748 | 18482 | 19672 | 20533 | 20751 | 20174 | 21980 | 22594 | 24198 | 25089 | 23427 | 24480 | 25958 | 26464 | 27753 | 27283 | 25529
242 | 242 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 2 | 15764 | 16493 | 16484 | 17453 | 18127 | 19348 | 20169 | 20338 | 19858 | 21660 | 22233 | 23805 | 24654 | 23047 | 24147 | 25535 | 25985 | 27238 | 26708 | 25104
243 | 243 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 3 | 15592 | 16222 | 16278 | 17372 | 18055 | 19262 | 20093 | 20216 | 19810 | 21657 | 22134 | 23677 | 24501 | 23013 | 24155 | 25469 | 25848 | 27000 | 26473 | 25030
244 | 244 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 4 | 15568 | 16077 | 16190 | 17319 | 17942 | 19151 | 19875 | 19933 | 19606 | 21340 | 21720 | 23199 | 23892 | 22598 | 23736 | 24853 | 25157 | 26164 | 25666 | 24476
245 | 245 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 5 | 15724 | 16045 | 16076 | 17533 | 18010 | 19134 | 19809 | 19687 | 19281 | 21164 | 21363 | 22723 | 23290 | 22003 | 23424 | 24286 | 24508 | 25298 | 24788 | 23707
246 | 246 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 6 | 16250 | 16175 | 16153 | 18101 | 18503 | 19486 | 20025 | 19558 | 19043 | 21393 | 21397 | 22507 | 22922 | 21421 | 23346 | 24103 | 24204 | 24663 | 23968 | 22955
247 | 247 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 7 | 17380 | 16592 | 16595 | 19313 | 19476 | 20545 | 20894 | 19843 | 19249 | 21997 | 22154 | 23128 | 23413 | 21386 | 24153 | 24404 | 24571 | 24974 | 23642 | 22824
248 | 248 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 8 | 18843 | 17483 | 17250 | 20740 | 20687 | 22056 | 22253 | 20690 | 19920 | 22984 | 23374 | 24526 | 24575 | 21892 | 25516 | 25135 | 25505 | 26039 | 24162 | 23298
249 | 249 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 9 | 19197 | 18214 | 17914 | 21080 | 20970 | 22419 | 22689 | 21424 | 20645 | 23266 | 23585 | 24864 | 24930 | 22457 | 25837 | 25285 | 25571 | 26363 | 24713 | 23839
250 | 250 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 10 | 19270 | 18683 | 18468 | 21132 | 21125 | 22501 | 22785 | 21910 | 21240 | 23566 | 23763 | 25036 | 25101 | 23015 | 25989 | 25670 | 25727 | 26567 | 25223 | 24435
251 | 251 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 11 | 19482 | 18874 | 18889 | 21312 | 21349 | 22733 | 23028 | 22119 | 21688 | 23926 | 23954 | 25325 | 25418 | 22990 | 26228 | 26106 | 25461 | 26921 | 25039 | 24440
252 | 252 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 12 | 19567 | 18877 | 19027 | 21306 | 21240 | 22731 | 22920 | 21982 | 21707 | 23738 | 23850 | 25283 | 25268 | 22673 | 26095 | 25912 | 24943 | 26762 | 24479 | 24119
253 | 253 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 13 | 19392 | 18779 | 19015 | 21217 | 21127 | 22527 | 22775 | 21858 | 21662 | 23600 | 23776 | 25057 | 25087 | 22321 | 25906 | 25733 | 24646 | 26569 | 24156 | 23745
254 | 254 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 14 | 19349 | 18581 | 18931 | 21227 | 20971 | 22481 | 22682 | 21683 | 21603 | 23385 | 23800 | 24987 | 24954 | 21985 | 25865 | 25433 | 24361 | 26402 | 23664 | 23374
255 | 255 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 15 | 19230 | 18492 | 18864 | 21015 | 20780 | 22214 | 22281 | 21423 | 21382 | 23015 | 23577 | 24579 | 24434 | 21985 | 25442 | 24994 | 24411 | 25846 | 23628 | 23354
256 | 256 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 16 | 19086 | 18586 | 19045 | 20914 | 20975 | 21874 | 21858 | 21255 | 21326 | 23060 | 23405 | 24002 | 23800 | 22375 | 25075 | 25056 | 24825 | 25138 | 23889 | 23718
257 | 257 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 17 | 19480 | 19186 | 19887 | 21247 | 21448 | 22237 | 22032 | 21729 | 22055 | 23340 | 23706 | 24314 | 24030 | 23455 | 25331 | 25388 | 25456 | 25382 | 24717 | 24823
258 | 258 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 18 | 20606 | 20208 | 21019 | 22155 | 22049 | 23360 | 22888 | 22753 | 23276 | 23815 | 24406 | 25686 | 25054 | 25099 | 26320 | 25875 | 26345 | 26537 | 26103 | 26546
259 | 259 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 19 | 20730 | 19967 | 21042 | 22126 | 21788 | 23607 | 22884 | 22577 | 23443 | 23800 | 24432 | 26304 | 25483 | 25463 | 26708 | 26230 | 26778 | 27193 | 26575 | 27027
260 | 260 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 20 | 20583 | 19383 | 20721 | 21840 | 21588 | 23558 | 22788 | 22214 | 23197 | 23909 | 24633 | 26626 | 25933 | 25653 | 26857 | 26781 | 27416 | 27918 | 26889 | 27363
261 | 261 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 21 | 20394 | 19042 | 20373 | 21511 | 21335 | 23483 | 22615 | 22132 | 23076 | 24041 | 24806 | 27084 | 26365 | 25921 | 27158 | 27420 | 28075 | 28667 | 27624 | 27825
262 | 262 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 22 | 19643 | 18488 | 19735 | 20809 | 20752 | 22772 | 22144 | 21740 | 22614 | 23757 | 24531 | 26698 | 26242 | 25681 | 26848 | 27437 | 28107 | 28725 | 27724 | 27708
263 | 263 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 23 | 18562 | 17767 | 18965 | 19845 | 19912 | 21776 | 21447 | 21167 | 22039 | 23107 | 23882 | 25939 | 25805 | 25229 | 26228 | 26984 | 27603 | 28391 | 27434 | 27323
264 | 264 | 11 | 1 | 11 | Winter | 1 | 11 | Winter | 24 | 17367 | 16943 | 18147 | 18895 | 19030 | 20762 | 20649 | 20580 | 21535 | 22453 | 23238 | 25171 | 25191 | 24802 | 25603 | 26377 | 27025 | 27860 | 27049 | 26942
265 | 265 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 1 | 16629 | 16362 | 17501 | 18220 | 18486 | 20070 | 20353 | 19824 | 20873 | 22087 | 22240 | 24569 | 24712 | 24172 | 25689 | 26221 | 26171 | 27258 | 25561 | 26279
266 | 266 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 2 | 16222 | 15956 | 17218 | 17868 | 18131 | 19719 | 19953 | 19517 | 20665 | 21774 | 21882 | 24176 | 24235 | 23876 | 25301 | 25770 | 25702 | 26710 | 25170 | 25942
267 | 267 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 3 | 15979 | 15690 | 17092 | 17754 | 17994 | 19610 | 19806 | 19437 | 20693 | 21691 | 21745 | 24036 | 24071 | 23889 | 25236 | 25633 | 25522 | 26465 | 25068 | 25906
268 | 268 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 4 | 15859 | 15563 | 17014 | 17629 | 17848 | 19399 | 19537 | 19252 | 20501 | 21322 | 21317 | 23464 | 23458 | 23479 | 24628 | 24956 | 24804 | 25640 | 24495 | 25360
269 | 269 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 5 | 15911 | 15471 | 17246 | 17731 | 17890 | 19385 | 19359 | 18989 | 20489 | 21051 | 20929 | 22949 | 22862 | 23215 | 24111 | 24352 | 24062 | 24797 | 23747 | 24932
270 | 270 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 6 | 16295 | 15550 | 17831 | 18250 | 18335 | 19637 | 19299 | 18820 | 20815 | 21158 | 20868 | 22668 | 22312 | 23169 | 23964 | 24079 | 23571 | 23988 | 22991 | 24737
271 | 271 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 7 | 17310 | 15967 | 19050 | 19252 | 19387 | 20516 | 19635 | 19078 | 21929 | 21968 | 21692 | 23211 | 22162 | 23986 | 24278 | 24467 | 24112 | 23660 | 22840 | 25472
272 | 272 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 8 | 18649 | 16651 | 20468 | 20487 | 20775 | 21886 | 20509 | 19781 | 23387 | 23233 | 23027 | 24421 | 22767 | 25361 | 25039 | 25427 | 25262 | 24182 | 23323 | 26807
273 | 273 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 9 | 19006 | 17287 | 20784 | 20731 | 21099 | 22290 | 21225 | 20499 | 23745 | 23451 | 23421 | 24774 | 23349 | 25667 | 25185 | 25482 | 25530 | 24705 | 23824 | 27076
274 | 274 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 10 | 19088 | 17815 | 20794 | 20813 | 21140 | 22342 | 21654 | 21042 | 23811 | 23575 | 23598 | 24890 | 23767 | 25771 | 25523 | 25589 | 25697 | 25166 | 24379 | 27213
275 | 275 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 11 | 19290 | 18199 | 20941 | 20976 | 21205 | 22550 | 21818 | 21451 | 23991 | 23722 | 23719 | 25162 | 23504 | 25970 | 25915 | 25283 | 25372 | 24943 | 24350 | 27438
276 | 276 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 12 | 19355 | 18393 | 20986 | 20914 | 21176 | 22476 | 21711 | 21503 | 23900 | 23630 | 23575 | 25021 | 22959 | 25856 | 25725 | 24780 | 24825 | 24397 | 24047 | 27317
277 | 277 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 13 | 19280 | 18419 | 20941 | 20844 | 21151 | 22368 | 21628 | 21497 | 23801 | 23594 | 23458 | 24882 | 22692 | 25708 | 25584 | 24521 | 24472 | 24113 | 23722 | 27148
278 | 278 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 14 | 19180 | 18323 | 20948 | 20700 | 21164 | 22265 | 21447 | 21426 | 23815 | 23624 | 23448 | 24752 | 22243 | 25678 | 25291 | 24238 | 24144 | 23627 | 23347 | 27080
279 | 279 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 15 | 18921 | 18253 | 20749 | 20541 | 21050 | 21880 | 21197 | 21217 | 23431 | 23392 | 23197 | 24235 | 22225 | 25243 | 24850 | 24277 | 24153 | 23579 | 23317 | 26617
280 | 280 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 16 | 18800 | 18495 | 20716 | 20790 | 21139 | 21538 | 21101 | 21231 | 23126 | 23264 | 22973 | 23652 | 22574 | 24914 | 24949 | 24727 | 24494 | 23873 | 23709 | 26261
281 | 281 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 17 | 19228 | 19349 | 21092 | 21313 | 21585 | 21775 | 21625 | 22005 | 23451 | 23587 | 23466 | 23906 | 23413 | 25189 | 25308 | 25385 | 25398 | 24730 | 24832 | 26565
282 | 282 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 18 | 20061 | 20485 | 21982 | 21961 | 22358 | 22663 | 22655 | 23215 | 24246 | 24252 | 24473 | 24885 | 24688 | 26172 | 25786 | 26263 | 26630 | 26125 | 26559 | 27621
283 | 283 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 19 | 19804 | 20474 | 21921 | 21648 | 22170 | 22608 | 22416 | 23297 | 24295 | 24163 | 24682 | 25212 | 24918 | 26498 | 26070 | 26625 | 27093 | 26568 | 27014 | 28072
284 | 284 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 20 | 19534 | 20134 | 21637 | 21420 | 21883 | 22487 | 22010 | 23000 | 24162 | 24275 | 24674 | 25586 | 24996 | 26615 | 26587 | 27231 | 27583 | 26874 | 27351 | 28319
285 | 285 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 21 | 19181 | 19783 | 21285 | 21116 | 21551 | 22247 | 21849 | 22811 | 24024 | 24338 | 24872 | 25902 | 25391 | 26847 | 27156 | 27824 | 28250 | 27584 | 27808 | 28748
286 | 286 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 22 | 18593 | 19131 | 20552 | 20493 | 20906 | 21725 | 21390 | 22292 | 23464 | 23993 | 24542 | 25712 | 25282 | 26496 | 27125 | 27812 | 28207 | 27655 | 27672 | 28512
287 | 287 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 23 | 17748 | 18344 | 19548 | 19628 | 20010 | 20979 | 20771 | 21678 | 22670 | 23304 | 23968 | 25225 | 24881 | 25849 | 26645 | 27284 | 27802 | 27349 | 27286 | 27922
288 | 288 | 12 | 1 | 12 | Winter | 1 | 12 | Winter | 24 | 16757 | 17507 | 18567 | 18713 | 19114 | 20135 | 20141 | 21126 | 21962 | 22653 | 23368 | 24605 | 24435 | 25227 | 26038 | 26710 | 27282 | 26957 | 26909 | 27350
289 | 289 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 1 | 16418 | 16732 | 17737 | 18015 | 17845 | 19728 | 19315 | 20330 | 21466 | 21529 | 22597 | 24025 | 23147 | 25125 | 25727 | 25731 | 26629 | 25370 | 26113 | 27450
290 | 290 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 2 | 15958 | 16409 | 17350 | 17618 | 17493 | 19287 | 18964 | 20084 | 21143 | 21165 | 22165 | 23556 | 22782 | 24738 | 25288 | 25260 | 26063 | 24960 | 25761 | 27002
291 | 291 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 3 | 15730 | 16308 | 17263 | 17517 | 17409 | 19187 | 18939 | 20175 | 21211 | 21137 | 22096 | 23449 | 22780 | 24723 | 25199 | 25122 | 25896 | 24896 | 25758 | 26928
292 | 292 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 4 | 15611 | 16294 | 17196 | 17435 | 17339 | 18998 | 18836 | 20077 | 20980 | 20842 | 21700 | 22933 | 22418 | 24199 | 24596 | 24475 | 25181 | 24367 | 25249 | 26245
293 | 293 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 5 | 15590 | 16524 | 17317 | 17506 | 17348 | 18866 | 18621 | 20122 | 20880 | 20541 | 21331 | 22412 | 21879 | 23735 | 24039 | 23772 | 24450 | 23624 | 24826 | 25576
294 | 294 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 6 | 15716 | 17129 | 17841 | 17981 | 17772 | 18847 | 18506 | 20512 | 21164 | 20568 | 21343 | 21954 | 21342 | 23641 | 23816 | 23321 | 24000 | 22884 | 24634 | 25280
295 | 295 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 7 | 16144 | 18347 | 18899 | 19078 | 18971 | 19227 | 18822 | 21691 | 21835 | 21473 | 22077 | 21903 | 21363 | 24035 | 24272 | 23916 | 24373 | 22774 | 25389 | 25524
296 | 296 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 8 | 17025 | 19724 | 20126 | 20444 | 20319 | 20062 | 19497 | 23130 | 22815 | 22798 | 23327 | 22520 | 21881 | 24797 | 25230 | 25063 | 25518 | 23239 | 26708 | 26178
297 | 297 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 9 | 17706 | 20045 | 20369 | 20765 | 20690 | 20760 | 20213 | 23496 | 23081 | 23205 | 23655 | 23112 | 22431 | 24944 | 25300 | 25332 | 25820 | 23735 | 26974 | 26278
298 | 298 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 10 | 18066 | 19973 | 20345 | 20703 | 20708 | 21073 | 20635 | 23439 | 23197 | 23237 | 23650 | 23472 | 22889 | 25221 | 25352 | 25444 | 25867 | 24231 | 27061 | 26614
299 | 299 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 11 | 18033 | 19921 | 20248 | 20479 | 20454 | 20869 | 20639 | 23184 | 23041 | 22852 | 23401 | 23198 | 22823 | 25598 | 25037 | 25111 | 25650 | 24196 | 27283 | 27047
300 | 300 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 12 | 17881 | 19795 | 19983 | 20210 | 20080 | 20460 | 20352 | 22728 | 22472 | 22268 | 22936 | 22627 | 22498 | 25381 | 24506 | 24529 | 25171 | 23867 | 27145 | 26841
301 | 301 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 13 | 17751 | 19680 | 19832 | 20091 | 19858 | 20258 | 20214 | 22486 | 22213 | 21995 | 22649 | 22366 | 22174 | 25240 | 24246 | 24173 | 24806 | 23541 | 26974 | 26683
302 | 302 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 14 | 17511 | 19658 | 19632 | 20009 | 19728 | 19949 | 19996 | 22337 | 21830 | 21804 | 22463 | 21979 | 21894 | 25015 | 24025 | 23901 | 24549 | 23225 | 26965 | 26407
303 | 303 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 15 | 17603 | 19671 | 19726 | 20162 | 19885 | 20020 | 20130 | 22321 | 21830 | 21948 | 22390 | 22020 | 21938 | 24635 | 24117 | 23969 | 24402 | 23246 | 26554 | 25987
304 | 304 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 16 | 18047 | 19989 | 20340 | 20717 | 20396 | 20492 | 20750 | 22673 | 22583 | 22431 | 22471 | 22446 | 22422 | 24817 | 24634 | 24380 | 24410 | 23695 | 26246 | 26112
305 | 305 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 17 | 18773 | 20489 | 21019 | 21363 | 21182 | 21277 | 21805 | 23305 | 23222 | 23257 | 23006 | 23207 | 23458 | 25106 | 25219 | 25213 | 24945 | 24760 | 26481 | 26418
306 | 306 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 18 | 19753 | 21345 | 21684 | 22146 | 22008 | 22314 | 22989 | 24060 | 23683 | 24197 | 23842 | 24408 | 25064 | 25537 | 26056 | 26414 | 26080 | 26470 | 27514 | 26929
307 | 307 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 19 | 19462 | 21263 | 21349 | 21926 | 21909 | 22046 | 23038 | 24048 | 23572 | 24291 | 24065 | 24569 | 25348 | 25768 | 26374 | 26838 | 26644 | 26921 | 27958 | 27329
308 | 308 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 20 | 18880 | 20959 | 21087 | 21595 | 21622 | 21615 | 22704 | 23856 | 23610 | 24183 | 24154 | 24554 | 25474 | 26212 | 26907 | 27272 | 27073 | 27241 | 28200 | 27970
309 | 309 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 21 | 18531 | 20596 | 20762 | 21231 | 21378 | 21406 | 22472 | 23665 | 23647 | 24290 | 24422 | 24873 | 25694 | 26723 | 27459 | 27901 | 27826 | 27695 | 28627 | 28728
310 | 310 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 22 | 17949 | 19844 | 20101 | 20541 | 20735 | 20900 | 21900 | 23055 | 23281 | 23892 | 24082 | 24694 | 25390 | 26629 | 27396 | 27828 | 27762 | 27534 | 28377 | 28803
311 | 311 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 23 | 17253 | 18860 | 19234 | 19648 | 19928 | 20276 | 21279 | 22258 | 22618 | 23320 | 23537 | 24280 | 24943 | 26153 | 26881 | 27424 | 27380 | 27171 | 27823 | 28421
312 | 312 | 13 | 1 | 13 | Winter | 1 | 13 | Winter | 24 | 16421 | 17810 | 18255 | 18699 | 19010 | 19574 | 20654 | 21466 | 21921 | 22683 | 22877 | 23790 | 24489 | 25523 | 26269 | 26887 | 26824 | 26770 | 27239 | 27846
313 | 313 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 1 | 15736 | 16971 | 17572 | 17441 | 18205 | 18826 | 19895 | 20927 | 21439 | 21962 | 21892 | 22588 | 23731 | 25190 | 25265 | 26221 | 25655 | 25959 | 27317 | 27589
314 | 314 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 2 | 15308 | 16598 | 17174 | 17078 | 17800 | 18462 | 19643 | 20605 | 21114 | 21555 | 21445 | 22245 | 23436 | 24763 | 24808 | 25666 | 25082 | 25606 | 26878 | 27099
315 | 315 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 3 | 15080 | 16466 | 17047 | 16972 | 17705 | 18418 | 19726 | 20680 | 21139 | 21538 | 21362 | 22245 | 23477 | 24677 | 24672 | 25497 | 24865 | 25585 | 26793 | 26946
316 | 316 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 4 | 14991 | 16409 | 16986 | 16928 | 17620 | 18344 | 19674 | 20513 | 20905 | 21237 | 20872 | 21928 | 23141 | 24113 | 24063 | 24813 | 24047 | 25086 | 26095 | 26204
317 | 317 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 5 | 14915 | 16548 | 17095 | 16991 | 17721 | 18192 | 19797 | 20515 | 20749 | 20998 | 20401 | 21446 | 22919 | 23608 | 23405 | 24118 | 23140 | 24671 | 25430 | 25488
318 | 318 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 6 | 14990 | 17080 | 17578 | 17461 | 18189 | 18116 | 20250 | 20878 | 20928 | 21116 | 19998 | 20976 | 22914 | 23437 | 22999 | 23701 | 22311 | 24485 | 25136 | 25097
319 | 319 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 7 | 15410 | 18198 | 18671 | 18667 | 19173 | 18439 | 21464 | 21609 | 21792 | 21908 | 20030 | 21040 | 23781 | 23929 | 23617 | 24087 | 22102 | 25242 | 25363 | 25410
320 | 320 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 8 | 16102 | 19462 | 20055 | 20030 | 20557 | 19130 | 22931 | 22647 | 23058 | 23208 | 20704 | 21611 | 25194 | 24948 | 24817 | 25267 | 22645 | 26583 | 26051 | 26307
321 | 321 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 9 | 16723 | 19697 | 20376 | 20376 | 20924 | 19826 | 23288 | 22928 | 23280 | 23546 | 21316 | 22172 | 25508 | 25034 | 25089 | 25570 | 23192 | 26843 | 26155 | 26317
322 | 322 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 10 | 17241 | 19725 | 20377 | 20448 | 20965 | 20299 | 23279 | 23087 | 23328 | 23580 | 21752 | 22679 | 25613 | 25134 | 25249 | 25670 | 23681 | 26982 | 26538 | 26462
323 | 323 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 11 | 17433 | 19642 | 20194 | 20231 | 20839 | 20328 | 23042 | 22938 | 22989 | 23299 | 21687 | 22620 | 25821 | 24825 | 24922 | 25461 | 23670 | 27216 | 26985 | 26194
324 | 324 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 12 | 17519 | 19497 | 20056 | 19995 | 20687 | 20185 | 22726 | 22530 | 22605 | 22951 | 21440 | 22332 | 25708 | 24328 | 24372 | 25025 | 23329 | 27113 | 26810 | 25707
325 | 325 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 13 | 17485 | 19360 | 19952 | 19784 | 20427 | 20028 | 22455 | 22232 | 22346 | 22594 | 21177 | 22074 | 25620 | 24134 | 24080 | 24718 | 23134 | 27006 | 26714 | 25496
326 | 326 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 14 | 17352 | 19213 | 19887 | 19675 | 20319 | 19832 | 22323 | 21883 | 22207 | 22430 | 20870 | 21806 | 25650 | 23923 | 23818 | 24468 | 22751 | 26999 | 26451 | 25253
327 | 327 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 15 | 17400 | 19263 | 19965 | 19752 | 20190 | 19876 | 22222 | 21794 | 22256 | 22261 | 20737 | 21816 | 25234 | 23978 | 23849 | 24284 | 22612 | 26552 | 25987 | 25287
328 | 328 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 16 | 17786 | 19621 | 20320 | 20059 | 20128 | 20277 | 22354 | 22268 | 22585 | 22121 | 20792 | 22180 | 24839 | 24373 | 24138 | 24170 | 22712 | 26114 | 25979 | 25644
329 | 329 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 17 | 18702 | 20274 | 20925 | 20799 | 20510 | 21277 | 22921 | 22835 | 23168 | 22572 | 21260 | 23226 | 25066 | 24967 | 24985 | 24718 | 23345 | 26360 | 26300 | 26271
330 | 330 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 18 | 19855 | 21031 | 21843 | 21718 | 21464 | 22618 | 23825 | 23471 | 23984 | 23538 | 22389 | 24761 | 25980 | 25751 | 26145 | 25811 | 24406 | 27380 | 26788 | 27154
331 | 331 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 19 | 19797 | 20678 | 21582 | 21556 | 21366 | 22621 | 23754 | 23272 | 23774 | 23629 | 22537 | 24966 | 26224 | 25999 | 26502 | 26324 | 24918 | 27803 | 27165 | 27578
332 | 332 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 20 | 19462 | 20423 | 21237 | 21268 | 21104 | 22293 | 23541 | 23262 | 23820 | 23638 | 22565 | 25050 | 26300 | 26491 | 26908 | 26730 | 25331 | 28057 | 27829 | 28289
333 | 333 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 21 | 19122 | 20055 | 20840 | 20997 | 20898 | 22019 | 23299 | 23206 | 23797 | 23798 | 22830 | 25194 | 26488 | 26972 | 27488 | 27434 | 26066 | 28477 | 28572 | 29031
334 | 334 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 22 | 18483 | 19385 | 20140 | 20356 | 20283 | 21432 | 22669 | 22805 | 23409 | 23415 | 22695 | 24868 | 26115 | 26887 | 27396 | 27372 | 26206 | 28243 | 28666 | 29127
335 | 335 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 23 | 17674 | 18460 | 19177 | 19476 | 19424 | 20728 | 21780 | 22033 | 22652 | 22782 | 22366 | 24361 | 25451 | 26313 | 26946 | 26943 | 26083 | 27654 | 28246 | 28641
336 | 336 | 14 | 1 | 14 | Winter | 1 | 14 | Winter | 24 | 16804 | 17468 | 18196 | 18537 | 18525 | 20069 | 20950 | 21298 | 21954 | 22134 | 22074 | 23901 | 24799 | 25708 | 26398 | 26389 | 25867 | 27065 | 27688 | 28108
337 | 337 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 1 | 16018 | 16744 | 16910 | 17699 | 17640 | 19290 | 20316 | 20768 | 20839 | 21182 | 20465 | 23114 | 24582 | 24643 | 25687 | 25195 | 23633 | 27074 | 27386 | 27099
338 | 338 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 2 | 15711 | 16340 | 16550 | 17291 | 17214 | 19040 | 20002 | 20452 | 20509 | 20778 | 20052 | 22835 | 24216 | 24208 | 25140 | 24633 | 23119 | 26635 | 26895 | 26591
339 | 339 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 3 | 15587 | 16166 | 16404 | 17147 | 17074 | 19076 | 20043 | 20446 | 20489 | 20709 | 19976 | 22899 | 24213 | 24097 | 24988 | 24438 | 22931 | 26552 | 26749 | 26405
340 | 340 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 4 | 15561 | 16081 | 16352 | 17057 | 16846 | 19017 | 19889 | 20240 | 20251 | 20264 | 19590 | 22597 | 23716 | 23522 | 24340 | 23635 | 22279 | 25853 | 26003 | 25645
341 | 341 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 5 | 15810 | 16221 | 16448 | 17198 | 16724 | 19183 | 19962 | 20167 | 20083 | 19889 | 19141 | 22445 | 23319 | 22935 | 23707 | 22780 | 21564 | 25218 | 25306 | 24840
342 | 342 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 6 | 16417 | 16729 | 16957 | 17711 | 16725 | 19673 | 20394 | 20424 | 20205 | 19576 | 18581 | 22511 | 23282 | 22593 | 23343 | 21995 | 20730 | 24946 | 24921 | 24288
343 | 343 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 7 | 17617 | 17861 | 18208 | 18732 | 17151 | 20922 | 21215 | 21367 | 21177 | 19694 | 18545 | 23431 | 23717 | 23253 | 23769 | 21812 | 20425 | 25190 | 25243 | 24824
344 | 344 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 8 | 18990 | 19251 | 19564 | 20116 | 18014 | 22379 | 22313 | 22672 | 22547 | 20415 | 19335 | 24848 | 24533 | 24451 | 24955 | 22350 | 21071 | 25876 | 26126 | 25943
345 | 345 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 9 | 19302 | 19589 | 19923 | 20479 | 18663 | 22728 | 22605 | 22927 | 22965 | 21060 | 19962 | 25185 | 24698 | 24740 | 25273 | 22909 | 21622 | 25991 | 26154 | 26198
346 | 346 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 10 | 19302 | 19629 | 20023 | 20554 | 19092 | 22750 | 22787 | 23018 | 23098 | 21548 | 20522 | 25271 | 25002 | 24878 | 25353 | 23381 | 22236 | 26353 | 26281 | 26370
347 | 347 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 11 | 19405 | 19626 | 20030 | 20693 | 19391 | 22843 | 22987 | 23076 | 23119 | 21903 | 20858 | 25409 | 25314 | 24476 | 25073 | 23297 | 22621 | 26728 | 25947 | 25996
348 | 348 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 12 | 19493 | 19650 | 19994 | 20766 | 19515 | 22802 | 22852 | 22995 | 22966 | 21955 | 20919 | 25301 | 25131 | 23923 | 24626 | 22955 | 22687 | 26551 | 25458 | 25455
349 | 349 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 13 | 19423 | 19596 | 19865 | 20615 | 19466 | 22680 | 22717 | 22917 | 22811 | 21878 | 20887 | 25136 | 24964 | 23551 | 24238 | 22674 | 22638 | 26375 | 25166 | 25085
350 | 350 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 14 | 19517 | 19631 | 19882 | 20646 | 19390 | 22733 | 22577 | 22993 | 22868 | 21815 | 20862 | 25170 | 24756 | 23290 | 23991 | 22294 | 22570 | 26110 | 24917 | 24802
351 | 351 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 15 | 19438 | 19678 | 19908 | 20448 | 19201 | 22524 | 22362 | 22890 | 22739 | 21498 | 20768 | 24835 | 24411 | 23401 | 23889 | 22228 | 22446 | 25722 | 25024 | 24882
352 | 352 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 16 | 19452 | 19878 | 20045 | 20185 | 19081 | 22387 | 22514 | 22884 | 22621 | 21175 | 20698 | 24517 | 24524 | 23765 | 23850 | 22396 | 22315 | 25777 | 25440 | 25184
353 | 353 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 17 | 19766 | 20359 | 20581 | 20347 | 19368 | 22681 | 22777 | 23135 | 23005 | 21255 | 21182 | 24738 | 24828 | 24610 | 24392 | 23037 | 22760 | 26099 | 26066 | 26053
354 | 354 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 18 | 20559 | 21154 | 21318 | 21120 | 20158 | 23382 | 23175 | 23686 | 23812 | 22021 | 22209 | 25608 | 25227 | 25758 | 25484 | 24091 | 23991 | 26603 | 26958 | 27290
355 | 355 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 19 | 20456 | 20884 | 21151 | 21006 | 19977 | 23308 | 22958 | 23432 | 23810 | 22096 | 22288 | 25810 | 25393 | 26070 | 25958 | 24577 | 24444 | 26985 | 27386 | 27775
356 | 356 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 20 | 20152 | 20491 | 20827 | 20698 | 19639 | 23057 | 22874 | 23389 | 23621 | 22008 | 22268 | 25816 | 25788 | 26408 | 26290 | 24950 | 24736 | 27628 | 28081 | 28295
357 | 357 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 21 | 19774 | 20108 | 20529 | 20455 | 19422 | 22765 | 22732 | 23263 | 23619 | 22155 | 22438 | 25919 | 26205 | 26894 | 26927 | 25614 | 25282 | 28341 | 28796 | 29043
358 | 358 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 22 | 19029 | 19372 | 19858 | 19815 | 18974 | 22094 | 22260 | 22795 | 23167 | 21956 | 22175 | 25497 | 26083 | 26754 | 26818 | 25721 | 25234 | 28410 | 28874 | 29055
359 | 359 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 23 | 18019 | 18381 | 18962 | 18957 | 18456 | 21195 | 21470 | 22016 | 22522 | 21618 | 21736 | 24795 | 25553 | 26283 | 26367 | 25575 | 24907 | 27977 | 28386 | 28689
360 | 360 | 15 | 1 | 15 | Winter | 1 | 15 | Winter | 24 | 16973 | 17368 | 17982 | 18031 | 17901 | 20331 | 20686 | 21276 | 21874 | 21329 | 21325 | 24147 | 24931 | 25735 | 25818 | 25357 | 24547 | 27413 | 27862 | 28209
361 | 361 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 1 | 16059 | 16049 | 17090 | 17098 | 16823 | 19578 | 20053 | 20069 | 21066 | 19792 | 20966 | 23823 | 24497 | 24986 | 24618 | 23175 | 24105 | 27057 | 26813 | 27495
362 | 362 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 2 | 15696 | 15638 | 16667 | 16646 | 16373 | 19241 | 19721 | 19727 | 20680 | 19393 | 20711 | 23468 | 24074 | 24449 | 24063 | 22663 | 23769 | 26562 | 26306 | 26884
363 | 363 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 3 | 15539 | 15471 | 16492 | 16474 | 16234 | 19251 | 19705 | 19697 | 20644 | 19344 | 20833 | 23485 | 24019 | 24319 | 23886 | 22488 | 23792 | 26433 | 26124 | 26681
364 | 364 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 4 | 15480 | 15430 | 16419 | 16268 | 16067 | 19131 | 19543 | 19521 | 20391 | 19022 | 20669 | 23059 | 23498 | 23724 | 23128 | 21870 | 23376 | 25691 | 25377 | 25895
365 | 365 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 5 | 15647 | 15545 | 16594 | 16186 | 15923 | 19257 | 19542 | 19438 | 20258 | 18650 | 20504 | 22746 | 23084 | 23166 | 22340 | 21199 | 22912 | 25036 | 24594 | 25114
366 | 366 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 6 | 16189 | 16090 | 17156 | 16238 | 15730 | 19752 | 19883 | 19669 | 20478 | 18172 | 20660 | 22795 | 22993 | 22875 | 21617 | 20406 | 22753 | 24685 | 24058 | 24612
367 | 367 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 7 | 17339 | 17339 | 18198 | 16679 | 15902 | 20620 | 20878 | 20710 | 21351 | 18183 | 21710 | 23293 | 23532 | 23333 | 21462 | 20111 | 23654 | 25018 | 24585 | 24932
368 | 368 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 8 | 18612 | 18716 | 19591 | 17543 | 16771 | 21750 | 22227 | 22133 | 22713 | 19009 | 23256 | 24160 | 24578 | 24550 | 22023 | 20770 | 25134 | 25931 | 25718 | 26081
369 | 369 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 9 | 18819 | 19030 | 19939 | 18165 | 17459 | 22008 | 22473 | 22541 | 23049 | 19644 | 23674 | 24339 | 24678 | 24857 | 22562 | 21306 | 25427 | 25942 | 25955 | 26361
370 | 370 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 10 | 18821 | 19084 | 19990 | 18565 | 17922 | 22132 | 22520 | 22636 | 23099 | 20169 | 23798 | 24598 | 24732 | 24908 | 22999 | 21886 | 25617 | 26041 | 26093 | 26425
371 | 371 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 11 | 18698 | 18923 | 19973 | 18701 | 18039 | 22141 | 22399 | 22485 | 23076 | 20336 | 23804 | 24733 | 24183 | 24456 | 22744 | 22103 | 25670 | 25536 | 25555 | 26002
372 | 372 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 12 | 18599 | 18819 | 19976 | 18747 | 18063 | 21927 | 22224 | 22239 | 22934 | 20287 | 23618 | 24455 | 23575 | 23907 | 22299 | 22062 | 25467 | 24940 | 24910 | 25447
373 | 373 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 13 | 18521 | 18736 | 19855 | 18733 | 18082 | 21823 | 22174 | 22117 | 22796 | 20284 | 23429 | 24316 | 23324 | 23547 | 22049 | 22045 | 25250 | 24672 | 24566 | 25088
374 | 374 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 14 | 18498 | 18748 | 19887 | 18658 | 18049 | 21697 | 22259 | 22175 | 22871 | 20275 | 23436 | 24124 | 23126 | 23310 | 21684 | 21990 | 25210 | 24441 | 24288 | 24826
375 | 375 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 15 | 18537 | 18791 | 19709 | 18489 | 18060 | 21516 | 22167 | 22064 | 22532 | 20178 | 23215 | 23788 | 23246 | 23208 | 21616 | 21861 | 24939 | 24537 | 24362 | 24696
376 | 376 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 16 | 18835 | 19047 | 19574 | 18493 | 18258 | 21794 | 22283 | 22077 | 22114 | 20206 | 23133 | 23974 | 23797 | 23263 | 21877 | 21822 | 24791 | 25038 | 24755 | 24690
377 | 377 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 17 | 19466 | 19746 | 19901 | 18950 | 18989 | 22228 | 22703 | 22624 | 22339 | 20816 | 23750 | 24411 | 24533 | 23947 | 22655 | 22404 | 25466 | 25803 | 25757 | 25390
378 | 378 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 18 | 20194 | 20517 | 20721 | 19821 | 20076 | 22751 | 23343 | 23467 | 23061 | 21859 | 24727 | 24843 | 25374 | 25074 | 23765 | 23696 | 26669 | 26771 | 27065 | 26631
379 | 379 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 19 | 19847 | 20338 | 20592 | 19618 | 20032 | 22518 | 23072 | 23411 | 23088 | 21866 | 24947 | 24941 | 25565 | 25498 | 24211 | 24119 | 27089 | 27190 | 27551 | 27223
380 | 380 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 20 | 19554 | 20008 | 20246 | 19249 | 19652 | 22372 | 22956 | 23141 | 22977 | 21760 | 24859 | 25248 | 25970 | 25774 | 24531 | 24374 | 27372 | 27869 | 28066 | 27688
381 | 381 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 21 | 19152 | 19714 | 19980 | 19002 | 19459 | 22173 | 22747 | 23052 | 23033 | 21853 | 24897 | 25577 | 26349 | 26337 | 25138 | 24883 | 27782 | 28563 | 28805 | 28511
382 | 382 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 22 | 18447 | 19018 | 19322 | 18538 | 18950 | 21645 | 22223 | 22541 | 22575 | 21548 | 24331 | 25395 | 26206 | 26186 | 25210 | 24813 | 27410 | 28622 | 28813 | 28506
383 | 383 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 23 | 17552 | 18117 | 18450 | 18006 | 18327 | 20834 | 21412 | 21858 | 21952 | 21098 | 23582 | 24845 | 25620 | 25724 | 25058 | 24490 | 26766 | 28133 | 28456 | 28144
384 | 384 | 16 | 1 | 16 | Winter | 1 | 16 | Winter | 24 | 16562 | 17085 | 17476 | 17398 | 17664 | 19994 | 20613 | 21145 | 21259 | 20666 | 22830 | 24194 | 25003 | 25151 | 24811 | 24106 | 26064 | 27580 | 27963 | 27630
385 | 385 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 1 | 15772 | 16189 | 16539 | 16368 | 17270 | 19301 | 19355 | 20292 | 20257 | 20313 | 22530 | 23712 | 23874 | 23955 | 22677 | 23653 | 26111 | 26504 | 27217 | 26342
386 | 386 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 2 | 15353 | 15754 | 16072 | 15892 | 16979 | 18942 | 18993 | 19886 | 19833 | 20052 | 22121 | 23314 | 23449 | 23422 | 22182 | 23331 | 25585 | 26001 | 26614 | 25743
387 | 387 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 3 | 15188 | 15557 | 15880 | 15738 | 17024 | 18918 | 18969 | 19859 | 19788 | 20220 | 22088 | 23286 | 23363 | 23269 | 22026 | 23369 | 25402 | 25826 | 26415 | 25519
388 | 388 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 4 | 15122 | 15489 | 15706 | 15589 | 17062 | 18798 | 18850 | 19677 | 19429 | 20127 | 21742 | 22838 | 22863 | 22572 | 21448 | 22982 | 24746 | 25109 | 25646 | 24641
389 | 389 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 5 | 15278 | 15664 | 15636 | 15454 | 17162 | 18834 | 18817 | 19609 | 19132 | 20015 | 21466 | 22495 | 22351 | 21831 | 20810 | 22541 | 24113 | 24337 | 24868 | 23683
390 | 390 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 6 | 15797 | 16233 | 15722 | 15287 | 17690 | 19229 | 19122 | 19923 | 18912 | 20235 | 21582 | 22477 | 22086 | 21161 | 20051 | 22410 | 23818 | 23810 | 24365 | 22782
391 | 391 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 7 | 16948 | 17330 | 16211 | 15486 | 19053 | 20286 | 20232 | 20881 | 19094 | 21356 | 22241 | 23101 | 22812 | 21069 | 19803 | 23353 | 24135 | 24364 | 24717 | 22550
392 | 392 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 8 | 18311 | 18675 | 17079 | 16318 | 20562 | 21622 | 21636 | 22236 | 19820 | 22881 | 23203 | 24172 | 24033 | 21636 | 20458 | 24800 | 24983 | 25484 | 25845 | 23065
393 | 393 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 9 | 18613 | 18994 | 17691 | 16984 | 20930 | 21854 | 22043 | 22575 | 20444 | 23305 | 23474 | 24280 | 24296 | 22164 | 20987 | 25089 | 25209 | 25702 | 26101 | 23585
394 | 394 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 10 | 18577 | 19002 | 18026 | 17371 | 20908 | 21796 | 22040 | 22523 | 20793 | 23318 | 23676 | 24292 | 24366 | 22561 | 21530 | 25237 | 25572 | 25811 | 26140 | 24026
395 | 395 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 11 | 18158 | 18733 | 17878 | 17153 | 20490 | 21249 | 21434 | 22008 | 20455 | 22774 | 23511 | 23691 | 23748 | 22256 | 21699 | 25241 | 25998 | 25235 | 25670 | 23771
396 | 396 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 12 | 17909 | 18580 | 17734 | 16958 | 20095 | 20786 | 20860 | 21516 | 20014 | 22159 | 22966 | 23076 | 23074 | 21807 | 21654 | 25035 | 25865 | 24574 | 25118 | 23330
397 | 397 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 13 | 17778 | 18377 | 17609 | 16849 | 19806 | 20580 | 20560 | 21193 | 19766 | 21766 | 22658 | 22797 | 22707 | 21536 | 21615 | 24798 | 25715 | 24213 | 24734 | 23045
398 | 398 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 14 | 17635 | 18209 | 17304 | 16572 | 19555 | 20379 | 20312 | 20945 | 19371 | 21432 | 22298 | 22522 | 22376 | 21088 | 21484 | 24671 | 25542 | 23848 | 24392 | 22563
399 | 399 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 15 | 17785 | 18159 | 17298 | 16761 | 19656 | 20517 | 20454 | 20882 | 19343 | 21504 | 22165 | 22634 | 22471 | 21015 | 21337 | 24394 | 25049 | 23909 | 24242 | 22458
400 | 400 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 16 | 18405 | 18389 | 17716 | 17423 | 20257 | 21198 | 21079 | 21126 | 19796 | 22119 | 22660 | 23287 | 23021 | 21382 | 21387 | 24336 | 24889 | 24390 | 24329 | 22764
401 | 401 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 17 | 19291 | 18995 | 18480 | 18508 | 21338 | 22049 | 22077 | 21832 | 20517 | 23240 | 23418 | 24086 | 24071 | 22221 | 22032 | 25074 | 25243 | 25464 | 25087 | 23607
402 | 402 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 18 | 20264 | 19918 | 19452 | 19724 | 22356 | 22887 | 23075 | 22683 | 21505 | 24329 | 23987 | 24957 | 25321 | 23370 | 23359 | 26315 | 25955 | 26832 | 26377 | 24839
403 | 403 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 19 | 19970 | 19742 | 19185 | 19628 | 22337 | 22566 | 22953 | 22631 | 21483 | 24444 | 24244 | 25055 | 25533 | 23722 | 23721 | 26690 | 26562 | 27272 | 26932 | 25352
404 | 404 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 20 | 19553 | 19378 | 18786 | 19238 | 22070 | 22407 | 22630 | 22448 | 21312 | 24280 | 24505 | 25371 | 25786 | 23972 | 23929 | 26941 | 27126 | 27773 | 27387 | 25787
405 | 405 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 21 | 19146 | 19080 | 18495 | 18994 | 21748 | 22110 | 22445 | 22396 | 21347 | 24230 | 24724 | 25628 | 26173 | 24483 | 24371 | 27294 | 27802 | 28464 | 28179 | 26563
406 | 406 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 22 | 18402 | 18452 | 18024 | 18489 | 20978 | 21538 | 21896 | 21895 | 21105 | 23637 | 24434 | 25437 | 25993 | 24527 | 24283 | 26907 | 27768 | 28472 | 28191 | 26754
407 | 407 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 23 | 17406 | 17576 | 17479 | 17850 | 20041 | 20694 | 21170 | 21224 | 20748 | 22863 | 23766 | 24815 | 25518 | 24361 | 23946 | 26265 | 27263 | 28110 | 27829 | 26681
408 | 408 | 17 | 1 | 17 | Winter | 1 | 17 | Winter | 24 | 16404 | 16590 | 16833 | 17178 | 19066 | 19861 | 20415 | 20487 | 20416 | 22129 | 23079 | 24196 | 24959 | 24123 | 23580 | 25574 | 26665 | 27623 | 27334 | 26507
409 | 409 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 1 | 14995 | 15589 | 15777 | 16691 | 18274 | 18481 | 19448 | 19407 | 18879 | 21673 | 22373 | 22959 | 24096 | 21991 | 23053 | 25505 | 26049 | 26787 | 25968 | 24035
410 | 410 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 2 | 14581 | 15135 | 15303 | 16388 | 17884 | 18122 | 19049 | 18990 | 18476 | 21294 | 21932 | 22566 | 23594 | 21522 | 22751 | 25004 | 25516 | 26201 | 25383 | 23512
411 | 411 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 3 | 14432 | 14899 | 15117 | 16393 | 17792 | 18078 | 19009 | 18932 | 18454 | 21291 | 21848 | 22513 | 23490 | 21385 | 22804 | 24835 | 25270 | 26009 | 25158 | 23321
412 | 412 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 4 | 14406 | 14737 | 14973 | 16433 | 17697 | 17986 | 18869 | 18625 | 18191 | 21011 | 21432 | 22077 | 22964 | 20848 | 22457 | 24211 | 24518 | 25257 | 24292 | 22637
413 | 413 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 5 | 14520 | 14676 | 14852 | 16550 | 17816 | 17999 | 18862 | 18401 | 17870 | 20811 | 21149 | 21648 | 22471 | 20257 | 22055 | 23616 | 23806 | 24498 | 23340 | 21870
414 | 414 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 6 | 15102 | 14784 | 14747 | 17137 | 18370 | 18384 | 19285 | 18306 | 17487 | 21036 | 21275 | 21510 | 22278 | 19574 | 21992 | 23389 | 23527 | 24042 | 22480 | 21015
415 | 415 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 7 | 16335 | 15243 | 14944 | 18483 | 19344 | 19493 | 20274 | 18538 | 17525 | 21734 | 22119 | 22277 | 22780 | 19325 | 22923 | 23709 | 24128 | 24371 | 22219 | 20666
416 | 416 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 8 | 17646 | 16127 | 15786 | 19975 | 20542 | 20890 | 21651 | 19294 | 18329 | 22748 | 23332 | 23521 | 24008 | 19982 | 24376 | 24567 | 25176 | 25503 | 22723 | 21294
417 | 417 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 9 | 17967 | 16769 | 16499 | 20377 | 20886 | 21335 | 22043 | 19979 | 19008 | 23090 | 23372 | 23846 | 24353 | 20562 | 24707 | 24830 | 25072 | 25799 | 23281 | 21847
418 | 418 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 10 | 17894 | 17066 | 16834 | 20300 | 20893 | 21274 | 21932 | 20265 | 19364 | 23217 | 23229 | 23844 | 24300 | 21037 | 24782 | 25125 | 25059 | 25777 | 23660 | 22366
419 | 419 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 11 | 17515 | 17008 | 16695 | 19958 | 20779 | 20737 | 21480 | 19987 | 19033 | 23070 | 22781 | 23244 | 23827 | 21231 | 24813 | 25573 | 25174 | 25341 | 23432 | 22596
420 | 420 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 12 | 17282 | 16933 | 16579 | 19650 | 20477 | 20236 | 21048 | 19611 | 18620 | 22545 | 22309 | 22589 | 23285 | 21207 | 24634 | 25474 | 25134 | 24812 | 23012 | 22575
421 | 421 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 13 | 17147 | 16847 | 16529 | 19420 | 20301 | 19989 | 20775 | 19419 | 18456 | 22270 | 21983 | 22266 | 22945 | 21211 | 24440 | 25367 | 24986 | 24463 | 22768 | 22570
422 | 422 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 14 | 16979 | 16577 | 16268 | 19193 | 20092 | 19763 | 20545 | 19045 | 18120 | 21930 | 21823 | 21957 | 22635 | 21092 | 24325 | 25208 | 25045 | 24121 | 22295 | 22423
423 | 423 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 15 | 17144 | 16578 | 16462 | 19308 | 20050 | 19913 | 20497 | 19030 | 18317 | 21818 | 21815 | 22067 | 22535 | 20960 | 24057 | 24727 | 24702 | 23985 | 22203 | 22274
424 | 424 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 16 | 17702 | 16929 | 17071 | 19855 | 20448 | 20502 | 20710 | 19449 | 18990 | 22289 | 22161 | 22603 | 22666 | 20985 | 23974 | 24551 | 24370 | 24040 | 22477 | 22272
425 | 425 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 17 | 18644 | 17691 | 18140 | 20929 | 21127 | 21499 | 21411 | 20160 | 20102 | 23038 | 22900 | 23646 | 23410 | 21624 | 24705 | 24887 | 24793 | 24791 | 23324 | 22934
426 | 426 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 18 | 19421 | 18563 | 19256 | 21859 | 21777 | 22429 | 22173 | 21041 | 21214 | 23472 | 23849 | 24749 | 24495 | 22851 | 25848 | 25496 | 25765 | 25998 | 24469 | 24230
427 | 427 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 19 | 19225 | 18297 | 19151 | 21828 | 21791 | 22303 | 22097 | 20977 | 21154 | 23654 | 24268 | 24910 | 24834 | 23183 | 26197 | 26082 | 26551 | 26569 | 24992 | 24678
428 | 428 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 20 | 18910 | 17907 | 18749 | 21568 | 21653 | 21972 | 21878 | 20746 | 21006 | 23834 | 24769 | 25098 | 25038 | 23363 | 26423 | 26617 | 27455 | 27028 | 25437 | 24997
429 | 429 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 21 | 18618 | 17632 | 18506 | 21252 | 21420 | 21751 | 21767 | 20711 | 21020 | 23979 | 25104 | 25407 | 25517 | 23766 | 26750 | 27269 | 28286 | 27822 | 26220 | 25606
430 | 430 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 22 | 17913 | 17150 | 17981 | 20473 | 20787 | 21160 | 21211 | 20406 | 20684 | 23639 | 24836 | 25164 | 25320 | 23643 | 26346 | 27217 | 28320 | 27819 | 26410 | 25608
431 | 431 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 23 | 17020 | 16607 | 17333 | 19534 | 19873 | 20402 | 20510 | 20024 | 20216 | 22948 | 24033 | 24663 | 24856 | 23304 | 25706 | 26697 | 27681 | 27461 | 26351 | 25332
432 | 432 | 18 | 1 | 18 | Winter | 1 | 18 | Winter | 24 | 15987 | 15897 | 16599 | 18516 | 18953 | 19586 | 19708 | 19622 | 19764 | 22250 | 23186 | 24077 | 24277 | 22921 | 25000 | 26086 | 26905 | 26942 | 26170 | 24992
433 | 433 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 1 | 15242 | 15141 | 16328 | 17900 | 18258 | 18818 | 18857 | 18398 | 19544 | 21741 | 22597 | 23424 | 23243 | 22625 | 25100 | 25676 | 26399 | 25794 | 23937 | 24650
434 | 434 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 2 | 14845 | 14689 | 16031 | 17515 | 17855 | 18433 | 18453 | 18007 | 19314 | 21346 | 22181 | 22964 | 22760 | 22356 | 24631 | 25176 | 25888 | 25237 | 23436 | 24342
435 | 435 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 3 | 14640 | 14453 | 15995 | 17384 | 17735 | 18363 | 18373 | 17959 | 19477 | 21289 | 22109 | 22883 | 22622 | 22423 | 24473 | 24937 | 25652 | 25014 | 23235 | 24366
436 | 436 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 4 | 14576 | 14312 | 16037 | 17304 | 17605 | 18257 | 18112 | 17743 | 19429 | 20949 | 21697 | 22430 | 21988 | 22109 | 23895 | 24224 | 24894 | 24162 | 22568 | 23923
437 | 437 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 5 | 14748 | 14178 | 16148 | 17434 | 17648 | 18279 | 17936 | 17464 | 19360 | 20734 | 21367 | 22005 | 21303 | 21738 | 23332 | 23539 | 24213 | 23223 | 21794 | 23383
438 | 438 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 6 | 15325 | 14066 | 16731 | 17996 | 18118 | 18719 | 17895 | 17131 | 19647 | 20913 | 21333 | 21879 | 20709 | 21691 | 23122 | 23272 | 23810 | 22358 | 20915 | 23175
439 | 439 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 7 | 16416 | 14280 | 18113 | 19027 | 19388 | 19750 | 18204 | 17248 | 20797 | 21835 | 22155 | 22467 | 20649 | 22661 | 23489 | 23919 | 24312 | 22120 | 20578 | 24049
440 | 440 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 8 | 17734 | 15151 | 19618 | 20262 | 20852 | 21139 | 19000 | 18098 | 22339 | 23098 | 23570 | 23737 | 21247 | 24141 | 24377 | 24996 | 25565 | 22641 | 21218 | 25512
441 | 441 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 9 | 18084 | 15866 | 20023 | 20586 | 20981 | 21522 | 19682 | 18788 | 22816 | 23165 | 23836 | 24096 | 21828 | 24474 | 24656 | 24909 | 25754 | 23187 | 21765 | 25825
442 | 442 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 10 | 17940 | 16104 | 19853 | 20464 | 20673 | 21311 | 19855 | 19035 | 22659 | 22908 | 23721 | 23926 | 22051 | 24437 | 24835 | 24785 | 25804 | 23455 | 22174 | 25833
443 | 443 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 11 | 17677 | 15980 | 19520 | 20328 | 20277 | 20862 | 19560 | 18698 | 22126 | 22413 | 23271 | 23405 | 21730 | 24423 | 25236 | 24856 | 25929 | 23183 | 22366 | 25858
444 | 444 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 12 | 17575 | 15928 | 19283 | 20102 | 20017 | 20501 | 19234 | 18340 | 21585 | 21953 | 22792 | 22877 | 21303 | 24248 | 25138 | 24826 | 25877 | 22771 | 22355 | 25681
445 | 445 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 13 | 17413 | 15873 | 19066 | 19942 | 19762 | 20233 | 19051 | 18183 | 21231 | 21617 | 22456 | 22532 | 21064 | 24050 | 25031 | 24676 | 25692 | 22519 | 22342 | 25465
446 | 446 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 14 | 17400 | 15771 | 19000 | 19907 | 19811 | 20154 | 18830 | 17995 | 21061 | 21606 | 22316 | 22373 | 20770 | 24088 | 25022 | 24880 | 25754 | 22190 | 22332 | 25469
447 | 447 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 15 | 17349 | 15941 | 19098 | 19870 | 19796 | 20096 | 18807 | 18182 | 21132 | 21589 | 22305 | 22270 | 20702 | 23816 | 24534 | 24526 | 25386 | 22088 | 22175 | 25166
448 | 448 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 16 | 17567 | 16540 | 19633 | 20252 | 20146 | 20317 | 19231 | 18856 | 21715 | 21957 | 22604 | 22430 | 21058 | 23749 | 24376 | 24208 | 24979 | 22373 | 22180 | 25067
449 | 449 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 17 | 18188 | 17606 | 20708 | 20950 | 20950 | 21040 | 19956 | 19974 | 22843 | 22704 | 23344 | 23187 | 21912 | 24497 | 24728 | 24645 | 25227 | 23240 | 22857 | 25833
450 | 450 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 18 | 18992 | 18705 | 21597 | 21622 | 21936 | 21812 | 20817 | 21053 | 23826 | 23596 | 24416 | 24201 | 22940 | 25598 | 25311 | 25581 | 26421 | 24379 | 24146 | 27024
451 | 451 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 19 | 18842 | 18591 | 21575 | 21632 | 22038 | 21739 | 20741 | 20967 | 23922 | 23942 | 24654 | 24486 | 23261 | 25928 | 25865 | 26336 | 27093 | 24921 | 24609 | 27481
452 | 452 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 20 | 18454 | 18144 | 21277 | 21426 | 22075 | 21459 | 20432 | 20731 | 23694 | 24319 | 24867 | 24580 | 23430 | 26092 | 26330 | 27190 | 27725 | 25326 | 24898 | 27771
453 | 453 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 21 | 18155 | 17886 | 20920 | 21128 | 21877 | 21271 | 20309 | 20657 | 23567 | 24534 | 25012 | 24939 | 23874 | 26342 | 26904 | 27943 | 28327 | 26075 | 25479 | 28212
454 | 454 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 22 | 17543 | 17345 | 20141 | 20466 | 21242 | 20688 | 19959 | 20281 | 22943 | 24218 | 24626 | 24691 | 23871 | 25910 | 26817 | 27949 | 28214 | 26252 | 25485 | 27890
455 | 455 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 23 | 16691 | 16690 | 19188 | 19548 | 20227 | 19960 | 19540 | 19788 | 22158 | 23392 | 23970 | 24205 | 23707 | 25263 | 26294 | 27311 | 27694 | 26194 | 25224 | 27298
456 | 456 | 19 | 1 | 19 | Winter | 1 | 19 | Winter | 24 | 15685 | 15918 | 18112 | 18578 | 19116 | 19090 | 19070 | 19268 | 21373 | 22520 | 23235 | 23589 | 23427 | 24534 | 25666 | 26508 | 27049 | 25981 | 24873 | 26616
457 | 457 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 1 | 14786 | 15494 | 17314 | 17705 | 18191 | 18095 | 17779 | 18888 | 20902 | 21767 | 22609 | 22435 | 21462 | 24429 | 25088 | 25846 | 26482 | 23633 | 24385 | 26712
458 | 458 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 2 | 14335 | 15162 | 16890 | 17254 | 17752 | 17645 | 17344 | 18614 | 20515 | 21340 | 22134 | 21939 | 20993 | 23950 | 24561 | 25312 | 25899 | 23098 | 24038 | 26172
459 | 459 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 3 | 14104 | 15089 | 16739 | 17118 | 17650 | 17551 | 17289 | 18768 | 20520 | 21308 | 22030 | 21841 | 20880 | 23825 | 24354 | 25098 | 25663 | 22917 | 24071 | 25983
460 | 460 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 4 | 13954 | 15104 | 16657 | 16996 | 17523 | 17310 | 17094 | 18747 | 20291 | 20964 | 21594 | 21263 | 20386 | 23282 | 23683 | 24378 | 24882 | 22250 | 23624 | 25273
461 | 461 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 5 | 13903 | 15239 | 16816 | 17083 | 17583 | 17194 | 16878 | 18749 | 20162 | 20736 | 21153 | 20673 | 19851 | 22788 | 23062 | 23753 | 24031 | 21514 | 23106 | 24581
462 | 462 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 6 | 14013 | 15861 | 17421 | 17620 | 18011 | 17235 | 16638 | 19140 | 20464 | 20832 | 21021 | 20201 | 19224 | 22661 | 22874 | 23417 | 23462 | 20679 | 22931 | 24250
463 | 463 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 7 | 14495 | 17251 | 18503 | 18932 | 19113 | 17588 | 16817 | 20360 | 21252 | 21739 | 21684 | 20222 | 19034 | 23077 | 23568 | 23951 | 23866 | 20356 | 23809 | 24516
464 | 464 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 8 | 15420 | 18798 | 19786 | 20427 | 20648 | 18401 | 17694 | 21941 | 22331 | 23204 | 22902 | 20861 | 19735 | 24007 | 24672 | 25214 | 24941 | 21007 | 25278 | 25339
465 | 465 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 9 | 16041 | 19192 | 20103 | 20549 | 20991 | 19059 | 18375 | 22421 | 22673 | 23474 | 23299 | 21445 | 20310 | 24286 | 24591 | 25395 | 25211 | 21539 | 25577 | 25577
466 | 466 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 10 | 16431 | 19208 | 20154 | 20426 | 21008 | 19410 | 18800 | 22449 | 22865 | 23521 | 23320 | 21843 | 20858 | 24638 | 24648 | 25622 | 25298 | 22129 | 25773 | 25980
467 | 467 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 11 | 16566 | 19120 | 20253 | 20278 | 20893 | 19355 | 18695 | 22157 | 22895 | 23261 | 23016 | 21721 | 21217 | 25229 | 24921 | 25951 | 25074 | 22525 | 26000 | 26635
468 | 468 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 12 | 16626 | 19042 | 20196 | 20192 | 20736 | 19190 | 18489 | 21773 | 22526 | 22887 | 22587 | 21403 | 21313 | 25256 | 25001 | 26017 | 24762 | 22624 | 25937 | 26658
469 | 469 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 13 | 16529 | 18840 | 20055 | 19953 | 20489 | 19023 | 18346 | 21435 | 22252 | 22560 | 22262 | 21165 | 21306 | 25141 | 24848 | 25833 | 24329 | 22605 | 25717 | 26527
470 | 470 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 14 | 16331 | 18701 | 19961 | 19926 | 20342 | 18731 | 18083 | 21193 | 21985 | 22342 | 22032 | 20795 | 21242 | 25057 | 24971 | 25809 | 24063 | 22511 | 25637 | 26396
471 | 471 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 15 | 16333 | 18797 | 19942 | 19913 | 20381 | 18719 | 18278 | 21274 | 21878 | 22352 | 21959 | 20743 | 21112 | 24587 | 24628 | 25458 | 23886 | 22362 | 25345 | 25889
472 | 472 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 16 | 16584 | 19233 | 20168 | 20157 | 20636 | 19049 | 18855 | 21760 | 22262 | 22582 | 22023 | 21029 | 21063 | 24356 | 24229 | 24974 | 23693 | 22277 | 25154 | 25599
473 | 473 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 17 | 17102 | 20029 | 20603 | 20698 | 21095 | 19517 | 19710 | 22618 | 22768 | 23054 | 22551 | 21620 | 21456 | 24452 | 24402 | 24960 | 24184 | 22695 | 25665 | 25722
474 | 474 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 18 | 17849 | 20833 | 21239 | 21629 | 22020 | 20324 | 20705 | 23498 | 23103 | 23997 | 23372 | 22509 | 22561 | 24924 | 25235 | 26064 | 25448 | 23904 | 26765 | 26277
475 | 475 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 19 | 17555 | 20760 | 21202 | 21668 | 22024 | 20200 | 20561 | 23518 | 23214 | 24104 | 23586 | 22732 | 22826 | 25399 | 25919 | 26658 | 25942 | 24338 | 27187 | 26915
476 | 476 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 20 | 17125 | 20433 | 20945 | 21647 | 21744 | 19844 | 20273 | 23218 | 23268 | 24195 | 23612 | 22802 | 22911 | 25786 | 26687 | 27223 | 26490 | 24609 | 27467 | 27500
477 | 477 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 21 | 16834 | 20079 | 20623 | 21412 | 21458 | 19675 | 20151 | 23027 | 23308 | 24254 | 23770 | 23161 | 23248 | 26300 | 27387 | 27787 | 27115 | 25186 | 27912 | 28260
478 | 478 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 22 | 16351 | 19299 | 19919 | 20729 | 20757 | 19265 | 19718 | 22344 | 22901 | 23793 | 23557 | 23087 | 23084 | 26157 | 27342 | 27632 | 27181 | 25167 | 27576 | 28283
479 | 479 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 23 | 15808 | 18317 | 18968 | 19683 | 19846 | 18802 | 19183 | 21520 | 22178 | 23107 | 23027 | 22880 | 22726 | 25606 | 26683 | 27105 | 26783 | 24891 | 26980 | 27817
480 | 480 | 20 | 1 | 20 | Winter | 1 | 20 | Winter | 24 | 15066 | 17211 | 17957 | 18535 | 18844 | 18284 | 18618 | 20684 | 21425 | 22357 | 22436 | 22580 | 22319 | 24962 | 25877 | 26449 | 26292 | 24532 | 26298 | 27224
481 | 481 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 1 | 14322 | 16471 | 17163 | 17672 | 18109 | 17164 | 18322 | 20215 | 20820 | 21808 | 21236 | 20822 | 21976 | 24457 | 25289 | 25969 | 24943 | 24137 | 26477 | 26810
482 | 482 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 2 | 13901 | 16102 | 16769 | 17278 | 17744 | 16782 | 18101 | 19893 | 20470 | 21428 | 20729 | 20420 | 21734 | 23996 | 24817 | 25445 | 24294 | 23838 | 25980 | 26286
483 | 483 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 3 | 13638 | 15892 | 16568 | 17107 | 17561 | 16657 | 18184 | 19841 | 20384 | 21307 | 20601 | 20305 | 21803 | 23786 | 24600 | 25195 | 24027 | 23846 | 25773 | 26003
484 | 484 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 4 | 13520 | 15835 | 16480 | 17019 | 17440 | 16503 | 18213 | 19677 | 20115 | 20966 | 20115 | 19891 | 21559 | 23184 | 23943 | 24477 | 23215 | 23433 | 25094 | 25221
485 | 485 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 5 | 13399 | 15995 | 16583 | 17103 | 17383 | 16317 | 18256 | 19613 | 19990 | 20613 | 19506 | 19414 | 21250 | 22617 | 23364 | 23663 | 22224 | 22925 | 24407 | 24428
486 | 486 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 6 | 13320 | 16617 | 17126 | 17570 | 17740 | 16110 | 18702 | 19983 | 20273 | 20578 | 18957 | 18859 | 21280 | 22485 | 23075 | 23132 | 21223 | 22761 | 24081 | 24075
487 | 487 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 7 | 13539 | 17728 | 18450 | 18696 | 18786 | 16316 | 19977 | 20854 | 21278 | 21326 | 18918 | 18714 | 22280 | 23217 | 23630 | 23550 | 20837 | 23641 | 24339 | 24620
488 | 488 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 8 | 14445 | 19063 | 19970 | 20243 | 20112 | 17219 | 21610 | 22007 | 22616 | 22615 | 19818 | 19447 | 23789 | 24365 | 24921 | 24645 | 21652 | 25112 | 25174 | 25658
489 | 489 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 9 | 15154 | 19388 | 20109 | 20581 | 20502 | 17894 | 22100 | 22377 | 22703 | 23035 | 20522 | 20046 | 24135 | 24322 | 25125 | 24928 | 22311 | 25423 | 25417 | 25529
490 | 490 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 10 | 15649 | 19489 | 20065 | 20669 | 20585 | 18399 | 22213 | 22654 | 22729 | 23146 | 21026 | 20617 | 24309 | 24403 | 25373 | 25044 | 22879 | 25640 | 25856 | 25655
491 | 491 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 11 | 16049 | 19897 | 20300 | 20977 | 20830 | 18783 | 22447 | 23235 | 23028 | 23414 | 21326 | 21058 | 24590 | 24759 | 25784 | 24903 | 23236 | 25957 | 26595 | 26051
492 | 492 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 12 | 16249 | 20021 | 20426 | 21073 | 20839 | 18884 | 22380 | 23223 | 23046 | 23339 | 21261 | 21109 | 24481 | 24784 | 25800 | 24560 | 23181 | 25853 | 26569 | 26086
493 | 493 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 13 | 16322 | 20039 | 20352 | 21020 | 20770 | 18952 | 22263 | 23192 | 22966 | 23267 | 21181 | 21158 | 24336 | 24683 | 25672 | 24177 | 23084 | 25676 | 26488 | 25969
494 | 494 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 14 | 16149 | 19978 | 20366 | 20944 | 20695 | 18796 | 22146 | 23083 | 23025 | 23215 | 21027 | 21005 | 24188 | 24714 | 25557 | 23819 | 22876 | 25497 | 26268 | 25971
495 | 495 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 15 | 16101 | 19751 | 20100 | 20712 | 20371 | 18670 | 21891 | 22615 | 22631 | 22752 | 20693 | 20784 | 23835 | 24277 | 25114 | 23550 | 22497 | 25114 | 25661 | 25517
496 | 496 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 16 | 16300 | 19639 | 19971 | 20552 | 20037 | 18739 | 21834 | 22368 | 22280 | 22179 | 20381 | 20692 | 23629 | 23831 | 24585 | 23311 | 22092 | 24874 | 25318 | 25036
497 | 497 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 17 | 16952 | 19911 | 20321 | 20786 | 20298 | 19305 | 22358 | 22519 | 22374 | 22292 | 20736 | 21114 | 24147 | 24033 | 24605 | 23831 | 22484 | 25411 | 25476 | 25273
498 | 498 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 18 | 17928 | 20533 | 21267 | 21682 | 20921 | 20281 | 23173 | 22806 | 23100 | 22977 | 21480 | 22195 | 25168 | 24865 | 25707 | 25093 | 23531 | 26551 | 26050 | 26212
499 | 499 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 19 | 17784 | 20541 | 21316 | 21680 | 20876 | 20152 | 23185 | 22892 | 23369 | 23117 | 21731 | 22424 | 25439 | 25513 | 26286 | 25580 | 24136 | 26991 | 26714 | 27044
500 | 500 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 20 | 17331 | 20266 | 21271 | 21378 | 20593 | 19855 | 22861 | 22890 | 23655 | 23054 | 21736 | 22467 | 25558 | 26252 | 26825 | 26114 | 24452 | 27287 | 27322 | 28003
501 | 501 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 21 | 17075 | 19918 | 21000 | 21066 | 20285 | 19689 | 22620 | 22839 | 23774 | 23107 | 21983 | 22728 | 25757 | 26872 | 27327 | 26685 | 25162 | 27724 | 28068 | 28890
502 | 502 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 22 | 16474 | 19167 | 20251 | 20313 | 19715 | 19179 | 21860 | 22329 | 23340 | 22779 | 21885 | 22483 | 25241 | 26751 | 27108 | 26695 | 25345 | 27339 | 28052 | 28951
503 | 503 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 23 | 15803 | 18184 | 19178 | 19382 | 18948 | 18615 | 21008 | 21551 | 22471 | 22222 | 21675 | 22096 | 24570 | 26063 | 26563 | 26281 | 25297 | 26741 | 27578 | 28358
504 | 504 | 21 | 1 | 21 | Winter | 1 | 21 | Winter | 24 | 15006 | 17132 | 17991 | 18348 | 18084 | 18003 | 20120 | 20759 | 21567 | 21635 | 21340 | 21671 | 23833 | 25236 | 25888 | 25777 | 25060 | 26048 | 26987 | 27594
505 | 505 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 1 | 14614 | 16280 | 17059 | 17522 | 16979 | 17642 | 19515 | 20053 | 20812 | 20419 | 19882 | 21279 | 23701 | 24579 | 25337 | 24391 | 23061 | 26134 | 26494 | 26998
506 | 506 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 2 | 14314 | 15855 | 16636 | 17113 | 16464 | 17377 | 19159 | 19672 | 20437 | 19913 | 19520 | 21028 | 23260 | 24099 | 24803 | 23729 | 22575 | 25619 | 25952 | 26449
507 | 507 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 3 | 14210 | 15645 | 16458 | 16918 | 16330 | 17450 | 19113 | 19599 | 20386 | 19842 | 19466 | 21139 | 23160 | 23925 | 24590 | 23504 | 22434 | 25439 | 25698 | 26196
508 | 508 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 4 | 14229 | 15560 | 16366 | 16799 | 16104 | 17479 | 18970 | 19368 | 20110 | 19408 | 19081 | 20929 | 22678 | 23310 | 23910 | 22713 | 21790 | 24767 | 24913 | 25394
509 | 509 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 5 | 14359 | 15674 | 16471 | 16771 | 15918 | 17554 | 18963 | 19313 | 19959 | 18882 | 18647 | 20682 | 22244 | 22792 | 23150 | 21759 | 20996 | 24094 | 24143 | 24660
510 | 510 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 6 | 14960 | 16231 | 16967 | 17163 | 15808 | 18025 | 19393 | 19663 | 20126 | 18410 | 18223 | 20773 | 22165 | 22553 | 22660 | 20787 | 20244 | 23778 | 23783 | 24218
511 | 511 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 7 | 16328 | 17560 | 18114 | 18224 | 16041 | 19310 | 20327 | 20717 | 21094 | 18428 | 18209 | 21820 | 22608 | 23138 | 23104 | 20413 | 20040 | 24038 | 24329 | 24674
512 | 512 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 8 | 17870 | 19068 | 19644 | 19524 | 17041 | 20913 | 21506 | 22075 | 22598 | 19346 | 18977 | 23326 | 23550 | 24427 | 24190 | 21219 | 20693 | 24859 | 25347 | 25902
513 | 513 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 9 | 18276 | 19236 | 19991 | 19910 | 17800 | 21397 | 21888 | 22192 | 22894 | 20090 | 19695 | 23688 | 23865 | 24641 | 24488 | 21894 | 21334 | 25116 | 25229 | 26089
514 | 514 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 10 | 18350 | 19198 | 20069 | 19982 | 18219 | 21490 | 22132 | 22200 | 23025 | 20580 | 20296 | 23846 | 24232 | 24869 | 24589 | 22449 | 21912 | 25536 | 25341 | 26378
515 | 515 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 11 | 18364 | 19233 | 20176 | 20021 | 18248 | 21511 | 22486 | 22285 | 23142 | 20665 | 20591 | 23915 | 24701 | 25066 | 24237 | 22595 | 21752 | 26069 | 25530 | 26602
516 | 516 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 12 | 18372 | 19321 | 20247 | 20002 | 18198 | 21416 | 22444 | 22264 | 23089 | 20545 | 20638 | 23767 | 24623 | 25030 | 23838 | 22493 | 21393 | 25989 | 25520 | 26569
517 | 517 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 13 | 18231 | 19178 | 20124 | 19865 | 18067 | 21236 | 22339 | 22104 | 22935 | 20389 | 20630 | 23551 | 24491 | 24833 | 23386 | 22321 | 21188 | 25839 | 25333 | 26360
518 | 518 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 14 | 18317 | 19397 | 20252 | 19998 | 18127 | 21328 | 22447 | 22373 | 23096 | 20461 | 20696 | 23630 | 24536 | 24939 | 23242 | 22335 | 20952 | 25836 | 25549 | 26437
519 | 519 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 15 | 18243 | 19204 | 20092 | 19756 | 17970 | 21149 | 22056 | 22048 | 22775 | 20177 | 20550 | 23334 | 24020 | 24552 | 23032 | 22004 | 21075 | 25280 | 25142 | 26017
520 | 520 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 16 | 18462 | 19184 | 20048 | 19543 | 17952 | 21203 | 21896 | 21815 | 22460 | 19957 | 20560 | 23214 | 23814 | 24116 | 22885 | 21684 | 21621 | 25018 | 24738 | 25518
521 | 521 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 17 | 19139 | 19589 | 20349 | 19880 | 18388 | 21810 | 22121 | 21979 | 22582 | 20343 | 21017 | 23760 | 23990 | 24174 | 23449 | 22116 | 22634 | 25212 | 25012 | 25591
522 | 522 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 18 | 19926 | 20537 | 21255 | 20538 | 19195 | 22677 | 22462 | 22744 | 23451 | 21042 | 22063 | 24752 | 24472 | 25277 | 24718 | 23168 | 23920 | 25811 | 25967 | 26780
523 | 523 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 19 | 19890 | 20597 | 21263 | 20491 | 19213 | 22708 | 22535 | 22996 | 23548 | 21236 | 22315 | 24987 | 24940 | 25821 | 25168 | 23764 | 24459 | 26492 | 26807 | 27495
524 | 524 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 20 | 19559 | 20486 | 20907 | 20148 | 18845 | 22343 | 22454 | 23179 | 23535 | 21131 | 22448 | 25026 | 25273 | 26269 | 25622 | 24028 | 24918 | 27068 | 27729 | 28163
525 | 525 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 21 | 19209 | 20197 | 20574 | 19815 | 18623 | 22065 | 22337 | 23207 | 23501 | 21275 | 22617 | 25151 | 25699 | 26707 | 26138 | 24699 | 25472 | 27792 | 28613 | 28838
526 | 526 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 22 | 18442 | 19441 | 19845 | 19269 | 18258 | 21316 | 21810 | 22754 | 22985 | 21169 | 22383 | 24636 | 25533 | 26496 | 26160 | 24889 | 25465 | 27802 | 28715 | 28765
527 | 527 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 23 | 17425 | 18319 | 18850 | 18449 | 17753 | 20393 | 20960 | 21796 | 22217 | 20880 | 21973 | 23896 | 24908 | 25882 | 25689 | 24773 | 25188 | 27280 | 28077 | 28257
528 | 528 | 22 | 1 | 22 | Winter | 1 | 22 | Winter | 24 | 16330 | 17131 | 17792 | 17570 | 17203 | 19482 | 20132 | 20857 | 21453 | 20558 | 21521 | 23175 | 24276 | 25220 | 25196 | 24554 | 24769 | 26711 | 27333 | 27657
529 | 529 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 1 | 15717 | 16391 | 17136 | 16669 | 16419 | 19007 | 19567 | 20257 | 21010 | 19410 | 20964 | 23158 | 23880 | 24845 | 24022 | 22804 | 24394 | 26395 | 26923 | 27328
530 | 530 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 2 | 15344 | 15948 | 16729 | 16148 | 16051 | 18650 | 19191 | 19888 | 20622 | 19080 | 20663 | 22749 | 23423 | 24340 | 23386 | 22338 | 23869 | 25861 | 26388 | 26756
531 | 531 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 3 | 15151 | 15741 | 16503 | 15984 | 15933 | 18573 | 19108 | 19825 | 20524 | 19051 | 20778 | 22669 | 23265 | 24153 | 23178 | 22208 | 23754 | 25615 | 26147 | 26489
532 | 532 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 4 | 15099 | 15676 | 16417 | 15793 | 15780 | 18480 | 18937 | 19625 | 20256 | 18745 | 20634 | 22272 | 22729 | 23541 | 22450 | 21613 | 23360 | 24864 | 25367 | 25685
533 | 533 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 5 | 15267 | 15798 | 16417 | 15640 | 15602 | 18521 | 18951 | 19554 | 19992 | 18383 | 20504 | 21916 | 22238 | 22849 | 21552 | 20857 | 22983 | 24116 | 24649 | 24770
534 | 534 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 6 | 15865 | 16289 | 16828 | 15548 | 15456 | 18983 | 19354 | 19797 | 20016 | 18008 | 20599 | 21891 | 22141 | 22401 | 20608 | 20115 | 22833 | 23759 | 24190 | 24109
535 | 535 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 7 | 17002 | 17471 | 17940 | 15820 | 15766 | 19988 | 20487 | 20859 | 20840 | 18065 | 21542 | 22423 | 22930 | 22903 | 20286 | 19945 | 23533 | 24336 | 24662 | 24482
536 | 536 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 8 | 18340 | 18994 | 19253 | 16831 | 16684 | 21207 | 21887 | 22406 | 22150 | 18878 | 23078 | 23431 | 24097 | 24025 | 21116 | 20618 | 24913 | 25390 | 25907 | 25537
537 | 537 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 9 | 18651 | 19339 | 19632 | 17575 | 17420 | 21567 | 22008 | 22713 | 22582 | 19615 | 23486 | 23755 | 24067 | 24325 | 21800 | 21256 | 25232 | 25266 | 26079 | 25804
538 | 538 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 10 | 18539 | 19237 | 19519 | 17805 | 17767 | 21593 | 21815 | 22644 | 22486 | 20023 | 23511 | 23918 | 23949 | 24231 | 22161 | 21642 | 25307 | 25188 | 26176 | 25738
539 | 539 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 11 | 18714 | 19326 | 19557 | 17830 | 18003 | 21915 | 21881 | 22749 | 22536 | 20309 | 23495 | 24369 | 24087 | 23865 | 22297 | 21474 | 25333 | 25368 | 26396 | 25400
540 | 540 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 12 | 18804 | 19437 | 19570 | 17807 | 18126 | 21896 | 21885 | 22716 | 22427 | 20358 | 23345 | 24295 | 24069 | 23469 | 22199 | 21121 | 25178 | 25362 | 26368 | 25008
541 | 541 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 13 | 18696 | 19274 | 19378 | 17618 | 18077 | 21736 | 21658 | 22506 | 22221 | 20289 | 23073 | 24103 | 23834 | 22958 | 21967 | 20849 | 24885 | 25113 | 26094 | 24498
542 | 542 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 14 | 18845 | 19402 | 19491 | 17659 | 18110 | 21832 | 21912 | 22650 | 22366 | 20348 | 23101 | 24145 | 24074 | 22810 | 21975 | 20604 | 24841 | 25324 | 26160 | 24323
543 | 543 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 15 | 18702 | 19262 | 19286 | 17538 | 18089 | 21492 | 21612 | 22364 | 21987 | 20215 | 22876 | 23654 | 23694 | 22618 | 21657 | 20731 | 24456 | 24923 | 25751 | 24093
544 | 544 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 16 | 18657 | 19205 | 19098 | 17539 | 18259 | 21347 | 21391 | 22073 | 21508 | 20214 | 22774 | 23414 | 23313 | 22461 | 21327 | 21262 | 24363 | 24495 | 25231 | 23875
545 | 545 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 17 | 19084 | 19660 | 19575 | 18120 | 19020 | 21727 | 21697 | 22336 | 21792 | 20769 | 23365 | 23696 | 23665 | 23130 | 21871 | 22387 | 24981 | 24882 | 25419 | 24550
546 | 546 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 18 | 19842 | 20663 | 20325 | 19043 | 20157 | 22228 | 22594 | 23282 | 22585 | 21855 | 24386 | 24270 | 24579 | 24477 | 22990 | 23754 | 26338 | 25920 | 26704 | 25990
547 | 547 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 19 | 19875 | 20650 | 20254 | 19032 | 20122 | 22286 | 22808 | 23311 | 22678 | 22028 | 24628 | 24662 | 25191 | 24883 | 23539 | 24268 | 27077 | 26760 | 27416 | 26567
548 | 548 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 20 | 19557 | 20296 | 19891 | 18656 | 19997 | 22169 | 22956 | 23243 | 22516 | 22100 | 24753 | 24922 | 25854 | 25282 | 23771 | 24724 | 27569 | 27699 | 28100 | 27188
549 | 549 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 21 | 19239 | 20002 | 19580 | 18446 | 19848 | 22033 | 22945 | 23169 | 22524 | 22244 | 24741 | 25312 | 26443 | 25779 | 24428 | 25288 | 27952 | 28602 | 28819 | 27933
550 | 550 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 22 | 18469 | 19225 | 18966 | 18018 | 19325 | 21407 | 22380 | 22543 | 22137 | 21926 | 24213 | 25035 | 26264 | 25704 | 24533 | 25209 | 27614 | 28628 | 28697 | 28016
551 | 551 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 23 | 17477 | 18228 | 18158 | 17522 | 18759 | 20555 | 21412 | 21762 | 21538 | 21516 | 23489 | 24415 | 25540 | 25241 | 24436 | 24950 | 26909 | 28007 | 28210 | 27643
552 | 552 | 23 | 1 | 23 | Winter | 1 | 23 | Winter | 24 | 16417 | 17150 | 17225 | 16922 | 18058 | 19668 | 20410 | 20936 | 20916 | 21044 | 22778 | 23744 | 24715 | 24720 | 24192 | 24510 | 26207 | 27236 | 27586 | 27179
553 | 553 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 1 | 15532 | 16209 | 16109 | 15940 | 17264 | 18829 | 19534 | 20221 | 19687 | 20279 | 22473 | 23083 | 23992 | 23348 | 22283 | 23908 | 26232 | 26577 | 27018 | 25685
554 | 554 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 2 | 15107 | 15772 | 15566 | 15533 | 16892 | 18420 | 19140 | 19808 | 19177 | 19976 | 22071 | 22628 | 23521 | 22708 | 21808 | 23376 | 25582 | 26026 | 26430 | 24982
555 | 555 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 3 | 14876 | 15499 | 15345 | 15362 | 16890 | 18292 | 19040 | 19674 | 19082 | 20094 | 22022 | 22477 | 23346 | 22497 | 21672 | 23250 | 25288 | 25765 | 26149 | 24702
556 | 556 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 4 | 14810 | 15403 | 15160 | 15204 | 16921 | 18140 | 18873 | 19452 | 18722 | 19994 | 21717 | 21998 | 22799 | 21806 | 21098 | 22868 | 24688 | 25001 | 25345 | 23848
557 | 557 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 5 | 14944 | 15425 | 15032 | 15049 | 17069 | 18206 | 18865 | 19267 | 18281 | 19931 | 21421 | 21590 | 22362 | 20970 | 20387 | 22525 | 24036 | 24306 | 24445 | 22796
558 | 558 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 6 | 15513 | 15874 | 14999 | 14955 | 17523 | 18690 | 19205 | 19413 | 17893 | 20117 | 21463 | 21596 | 22195 | 20106 | 19706 | 22424 | 23725 | 23884 | 23811 | 21714
559 | 559 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 7 | 16874 | 17011 | 15309 | 15281 | 18662 | 19882 | 20330 | 20320 | 17998 | 21112 | 22187 | 22452 | 22843 | 19828 | 19565 | 23141 | 24178 | 24371 | 24183 | 21296
560 | 560 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 8 | 18360 | 18306 | 16315 | 16167 | 20212 | 21284 | 21879 | 21636 | 18937 | 22642 | 23360 | 23639 | 24158 | 20657 | 20222 | 24508 | 25145 | 25597 | 25216 | 22067
561 | 561 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 9 | 18521 | 18663 | 17059 | 16888 | 20676 | 21401 | 22186 | 22077 | 19684 | 23067 | 23773 | 23627 | 24371 | 21336 | 20865 | 24834 | 25410 | 25764 | 25481 | 22716
562 | 562 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 10 | 18393 | 18641 | 17376 | 17319 | 20718 | 21276 | 22192 | 22058 | 20063 | 23172 | 23952 | 23584 | 24484 | 21773 | 21331 | 24986 | 25605 | 25939 | 25498 | 23200
563 | 563 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 11 | 18301 | 18560 | 17289 | 17434 | 20531 | 21210 | 22174 | 21981 | 20019 | 23032 | 24027 | 23594 | 24548 | 21783 | 21038 | 24890 | 25280 | 26043 | 25041 | 23252
564 | 564 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 12 | 18340 | 18536 | 17225 | 17516 | 20396 | 21163 | 22089 | 21827 | 19848 | 22821 | 23839 | 23511 | 24445 | 21614 | 20620 | 24671 | 24791 | 25951 | 24585 | 23095
565 | 565 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 13 | 18241 | 18464 | 17147 | 17577 | 20278 | 21045 | 21986 | 21730 | 19738 | 22658 | 23612 | 23378 | 24298 | 21501 | 20456 | 24486 | 24275 | 25782 | 24180 | 22959
566 | 566 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 14 | 18371 | 18505 | 17095 | 17525 | 20231 | 21211 | 22044 | 21792 | 19714 | 22615 | 23493 | 23548 | 24320 | 21433 | 20141 | 24369 | 23825 | 25769 | 23927 | 22856
567 | 567 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 15 | 18149 | 18264 | 16964 | 17484 | 20107 | 20894 | 21744 | 21401 | 19423 | 22358 | 23112 | 23135 | 23911 | 21088 | 20237 | 23949 | 23520 | 25324 | 23661 | 22484
568 | 568 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 16 | 18185 | 18171 | 17071 | 17757 | 20281 | 20784 | 21570 | 21042 | 19285 | 22346 | 23215 | 22845 | 23540 | 20842 | 20833 | 23935 | 24092 | 24885 | 23519 | 22192
569 | 569 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 17 | 18763 | 18744 | 17734 | 18605 | 21036 | 21183 | 21917 | 21410 | 19855 | 22983 | 23793 | 23249 | 23766 | 21438 | 22020 | 24615 | 25144 | 25129 | 24254 | 22797
570 | 570 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 18 | 19825 | 19517 | 18663 | 19769 | 22068 | 22140 | 22884 | 22202 | 20665 | 23971 | 24515 | 24150 | 24950 | 22556 | 23386 | 25976 | 26485 | 26432 | 25708 | 24012
571 | 571 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 19 | 19871 | 19417 | 18614 | 19709 | 22184 | 22332 | 22875 | 22230 | 20781 | 24127 | 24983 | 24681 | 25430 | 23046 | 23862 | 26679 | 27360 | 27130 | 26274 | 24658
572 | 572 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 20 | 19733 | 19032 | 18191 | 19558 | 21940 | 22412 | 22733 | 21973 | 20595 | 24155 | 25295 | 25249 | 25816 | 23201 | 24261 | 27129 | 28235 | 27793 | 26873 | 24994
573 | 573 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 21 | 19406 | 18662 | 17897 | 19324 | 21530 | 22278 | 22529 | 21840 | 20634 | 24010 | 25648 | 25675 | 26161 | 23734 | 24714 | 27410 | 29081 | 28433 | 27556 | 25780
574 | 574 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 22 | 18612 | 18074 | 17480 | 18827 | 20808 | 21688 | 21889 | 21429 | 20457 | 23479 | 25446 | 25466 | 25884 | 23838 | 24644 | 27089 | 29156 | 28338 | 27668 | 26040
575 | 575 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 23 | 17503 | 17256 | 16953 | 18227 | 19887 | 20667 | 21048 | 20773 | 20154 | 22725 | 24812 | 24699 | 25268 | 23702 | 24360 | 26364 | 28572 | 27829 | 27286 | 25988
576 | 576 | 24 | 1 | 24 | Winter | 1 | 24 | Winter | 24 | 16320 | 16289 | 16325 | 17516 | 18969 | 19629 | 20174 | 20102 | 19793 | 22018 | 24070 | 23870 | 24583 | 23459 | 23933 | 25674 | 27878 | 27209 | 26833 | 25811
577 | 577 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 1 | 15604 | 15440 | 15637 | 16972 | 18577 | 18969 | 19678 | 19138 | 18759 | 21918 | 23697 | 23378 | 24223 | 21883 | 23596 | 25931 | 27745 | 26887 | 25618 | 23944
578 | 578 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 2 | 15146 | 14912 | 15219 | 16577 | 18198 | 18566 | 19260 | 18623 | 18411 | 21546 | 23449 | 22932 | 23719 | 21424 | 23070 | 25298 | 27198 | 26305 | 24917 | 23431
579 | 579 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 3 | 14955 | 14690 | 15052 | 16571 | 18133 | 18486 | 19150 | 18553 | 18397 | 21555 | 23441 | 22826 | 23564 | 21342 | 22989 | 25050 | 26954 | 26059 | 24673 | 23292
580 | 580 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 4 | 14843 | 14471 | 14862 | 16566 | 18035 | 18308 | 18933 | 18206 | 18086 | 21278 | 23057 | 22302 | 22964 | 20770 | 22601 | 24441 | 26254 | 25234 | 23773 | 22575
581 | 581 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 5 | 14976 | 14361 | 14722 | 16731 | 18079 | 18344 | 18810 | 17839 | 17791 | 21058 | 22717 | 21947 | 22350 | 20108 | 22296 | 23828 | 25492 | 24354 | 22733 | 21736
582 | 582 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 6 | 15486 | 14321 | 14647 | 17205 | 18539 | 18718 | 19024 | 17533 | 17494 | 21165 | 22805 | 21864 | 21988 | 19461 | 22220 | 23540 | 25144 | 23725 | 21648 | 20919
583 | 583 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 7 | 16667 | 14640 | 14995 | 18351 | 19693 | 19864 | 19985 | 17710 | 17599 | 21943 | 23806 | 22583 | 22540 | 19343 | 22953 | 24004 | 25769 | 24100 | 21225 | 20700
584 | 584 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 8 | 18168 | 15654 | 15911 | 19912 | 21079 | 21438 | 21358 | 18701 | 18422 | 23200 | 25100 | 23945 | 23692 | 20025 | 24356 | 25022 | 26877 | 25158 | 22015 | 21352
585 | 585 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 9 | 18491 | 16379 | 16633 | 20357 | 21442 | 21736 | 21803 | 19464 | 19162 | 23624 | 25196 | 24171 | 23991 | 20671 | 24688 | 25282 | 26937 | 25413 | 22656 | 21971
586 | 586 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 10 | 18333 | 16557 | 16923 | 20252 | 21307 | 21592 | 21635 | 19688 | 19505 | 23639 | 25047 | 24126 | 23830 | 20986 | 24691 | 25325 | 26752 | 25288 | 22992 | 22327
587 | 587 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 11 | 18182 | 16358 | 16930 | 19948 | 21123 | 21456 | 21436 | 19519 | 19548 | 23592 | 24852 | 24059 | 23218 | 20568 | 24473 | 24875 | 25964 | 24717 | 22925 | 21947
588 | 588 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 12 | 18322 | 16400 | 17106 | 19912 | 21076 | 21461 | 21362 | 19434 | 19615 | 23473 | 24703 | 24026 | 22823 | 20223 | 24326 | 24448 | 25359 | 24332 | 22838 | 21603
589 | 589 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 13 | 18273 | 16306 | 17167 | 19804 | 20880 | 21356 | 21261 | 19326 | 19651 | 23246 | 24391 | 23883 | 22419 | 20062 | 24142 | 23930 | 24692 | 23921 | 22699 | 21421
590 | 590 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 14 | 18356 | 16278 | 17126 | 19771 | 20827 | 21430 | 21336 | 19315 | 19652 | 23157 | 24374 | 23940 | 22218 | 19772 | 24049 | 23505 | 24262 | 23688 | 22617 | 21103
591 | 591 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 15 | 18218 | 16196 | 17148 | 19721 | 20679 | 21197 | 21015 | 19092 | 19536 | 22831 | 23984 | 23580 | 22039 | 19915 | 23677 | 23252 | 24088 | 23469 | 22289 | 21228
592 | 592 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 16 | 18297 | 16406 | 17512 | 19995 | 20966 | 21127 | 20758 | 19057 | 19691 | 22991 | 23674 | 23291 | 22037 | 20589 | 23729 | 23903 | 24391 | 23391 | 22060 | 21877
593 | 593 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 17 | 18915 | 17177 | 18475 | 20875 | 21786 | 21609 | 21251 | 19747 | 20417 | 23665 | 23612 | 23610 | 22863 | 21849 | 24492 | 25057 | 25013 | 24225 | 22767 | 23166
594 | 594 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 18 | 19931 | 18114 | 19631 | 21919 | 22543 | 22613 | 22050 | 20547 | 21521 | 24354 | 23964 | 24737 | 24197 | 23204 | 25850 | 26395 | 26080 | 25686 | 23981 | 24597
595 | 595 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 19 | 19875 | 18027 | 19515 | 21977 | 22705 | 22553 | 22015 | 20574 | 21601 | 24697 | 24339 | 25117 | 24497 | 23602 | 26481 | 27193 | 27042 | 26207 | 24591 | 25119
596 | 596 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 20 | 19528 | 17618 | 19379 | 21750 | 22717 | 22417 | 21732 | 20351 | 21636 | 24947 | 25124 | 25451 | 24844 | 23991 | 26929 | 28058 | 28229 | 26828 | 24959 | 25647
597 | 597 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 21 | 19174 | 17313 | 19124 | 21326 | 22585 | 22156 | 21521 | 20305 | 21638 | 25200 | 25745 | 25702 | 25201 | 24390 | 27167 | 28856 | 29390 | 27497 | 25731 | 26246
598 | 598 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 22 | 18425 | 16914 | 18607 | 20597 | 22024 | 21472 | 21048 | 20062 | 21308 | 24930 | 25973 | 25360 | 25103 | 24291 | 26807 | 28886 | 29930 | 27590 | 25981 | 26262
599 | 599 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 23 | 17406 | 16365 | 17982 | 19654 | 21150 | 20588 | 20350 | 19715 | 20856 | 24268 | 25586 | 24703 | 24616 | 23988 | 26070 | 28294 | 29589 | 27199 | 25937 | 26029
600 | 600 | 25 | 1 | 25 | Winter | 1 | 25 | Winter | 24 | 16324 | 15659 | 17199 | 18681 | 20119 | 19641 | 19600 | 19276 | 20349 | 23498 | 24843 | 23986 | 24059 | 23535 | 25354 | 27569 | 28911 | 26707 | 25727 | 25617
601 | 601 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 1 | 15672 | 15081 | 16702 | 18320 | 19716 | 19162 | 18699 | 18370 | 19885 | 23174 | 24545 | 23660 | 23034 | 23268 | 25633 | 27475 | 28901 | 25544 | 23948 | 25314
602 | 602 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 2 | 15243 | 14657 | 16296 | 17926 | 19389 | 18735 | 18174 | 18008 | 19576 | 22933 | 24253 | 23192 | 22429 | 22770 | 25021 | 26954 | 28471 | 24861 | 23453 | 24772
603 | 603 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 3 | 14998 | 14424 | 16247 | 17823 | 19347 | 18599 | 18088 | 17972 | 19725 | 22966 | 24208 | 23045 | 22255 | 22687 | 24769 | 26698 | 27886 | 24599 | 23292 | 24644
604 | 604 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 4 | 14905 | 14277 | 16277 | 17775 | 19295 | 18452 | 17823 | 17745 | 19668 | 22700 | 23826 | 22548 | 21617 | 22371 | 24233 | 26062 | 27102 | 23755 | 22618 | 24190
605 | 605 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 5 | 14935 | 14150 | 16450 | 17837 | 19363 | 18369 | 17511 | 17501 | 19657 | 22406 | 23481 | 22016 | 20853 | 22110 | 23663 | 25340 | 26259 | 22735 | 21781 | 23765
606 | 606 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 6 | 15370 | 14074 | 16941 | 18318 | 19866 | 18619 | 17275 | 17271 | 19886 | 22567 | 23489 | 21738 | 20037 | 22062 | 23408 | 25021 | 25850 | 21659 | 20956 | 23568
607 | 607 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 7 | 16522 | 14433 | 18120 | 19514 | 21141 | 19619 | 17524 | 17448 | 20929 | 23641 | 24312 | 22385 | 19826 | 22836 | 23926 | 25702 | 26480 | 21268 | 20757 | 24263
608 | 608 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 8 | 17805 | 15341 | 19653 | 20907 | 22645 | 20963 | 18516 | 18280 | 22482 | 24939 | 25711 | 23567 | 20692 | 24240 | 24968 | 26836 | 27727 | 22057 | 21399 | 25641
609 | 609 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 9 | 18153 | 16053 | 20111 | 21264 | 22842 | 21416 | 19297 | 19048 | 22928 | 25120 | 25883 | 23898 | 21389 | 24600 | 25250 | 26914 | 27872 | 22712 | 22031 | 25955
610 | 610 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 10 | 17967 | 16335 | 19977 | 21059 | 22492 | 21196 | 19451 | 19323 | 22817 | 24877 | 25565 | 23727 | 21674 | 24599 | 25283 | 26723 | 27721 | 23045 | 22386 | 25989
611 | 611 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 11 | 17627 | 16212 | 19490 | 20617 | 21782 | 20690 | 18925 | 18982 | 22139 | 24084 | 24870 | 23161 | 21616 | 24434 | 24882 | 25988 | 27581 | 23030 | 22063 | 25860
612 | 612 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 12 | 17605 | 16336 | 19379 | 20466 | 21403 | 20460 | 18644 | 18836 | 21758 | 23516 | 24338 | 22800 | 21567 | 24320 | 24492 | 25429 | 27586 | 22983 | 21756 | 25756
613 | 613 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 13 | 17490 | 16326 | 19206 | 20182 | 20983 | 20220 | 18380 | 18699 | 21403 | 22926 | 23755 | 22462 | 21506 | 24211 | 24041 | 24827 | 27221 | 22910 | 21646 | 25619
614 | 614 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 14 | 17433 | 16139 | 19026 | 19971 | 20690 | 20083 | 18143 | 18449 | 21127 | 22548 | 23447 | 22245 | 21436 | 24102 | 23596 | 24376 | 26878 | 22803 | 21297 | 25475
615 | 615 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 15 | 17346 | 16297 | 19127 | 20021 | 20729 | 19984 | 18158 | 18590 | 21178 | 22536 | 23269 | 22080 | 21142 | 23735 | 23352 | 24208 | 26581 | 22480 | 21429 | 25083
616 | 616 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 16 | 17471 | 16819 | 19609 | 20544 | 21092 | 20060 | 18481 | 19132 | 21635 | 22814 | 23348 | 22050 | 20921 | 23744 | 23963 | 24468 | 26172 | 22202 | 22026 | 25061
617 | 617 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 17 | 18256 | 17926 | 20646 | 21562 | 21760 | 20818 | 19454 | 20161 | 22693 | 23280 | 23726 | 22820 | 21555 | 24450 | 25070 | 25033 | 25627 | 22859 | 23268 | 25795
618 | 618 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 18 | 19159 | 19216 | 21831 | 22548 | 22770 | 21891 | 20519 | 21535 | 23977 | 23914 | 24732 | 24100 | 22661 | 25785 | 26393 | 26090 | 26435 | 24078 | 24696 | 27205
619 | 619 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 19 | 19016 | 19120 | 21886 | 22699 | 23147 | 21845 | 20521 | 21579 | 24067 | 24301 | 25262 | 24335 | 23064 | 26379 | 27151 | 27020 | 27150 | 24692 | 25221 | 27934
620 | 620 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 20 | 18628 | 18915 | 21621 | 22646 | 23361 | 21505 | 20226 | 21533 | 24055 | 24918 | 25833 | 24565 | 23159 | 26765 | 27937 | 28131 | 28214 | 25026 | 25716 | 28450
621 | 621 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 21 | 18270 | 18656 | 21185 | 22477 | 23448 | 21245 | 20113 | 21484 | 23842 | 25468 | 26271 | 24832 | 23610 | 26953 | 28685 | 29250 | 29195 | 25786 | 26322 | 28836
622 | 622 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 22 | 17685 | 18140 | 20460 | 21886 | 23073 | 20744 | 19827 | 21115 | 23275 | 25671 | 26159 | 24688 | 23670 | 26575 | 28690 | 29766 | 29577 | 26029 | 26342 | 28572
623 | 623 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 23 | 16825 | 17451 | 19441 | 20929 | 22163 | 19948 | 19378 | 20561 | 22419 | 25177 | 25516 | 24122 | 23479 | 25781 | 28040 | 29370 | 29328 | 25939 | 26075 | 27840
624 | 624 | 26 | 1 | 26 | Winter | 1 | 26 | Winter | 24 | 15854 | 16662 | 18455 | 19901 | 21142 | 19175 | 18916 | 20030 | 21695 | 24445 | 24711 | 23575 | 23230 | 25086 | 27331 | 28709 | 28663 | 25752 | 25684 | 27172
625 | 625 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 1 | 14799 | 15885 | 17797 | 19290 | 20218 | 18010 | 17801 | 19282 | 21300 | 23771 | 24193 | 22274 | 21497 | 25016 | 26922 | 28395 | 28609 | 23682 | 25076 | 27271
626 | 626 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 2 | 14322 | 15521 | 17415 | 18908 | 19892 | 17498 | 17454 | 18990 | 20955 | 23533 | 23604 | 21699 | 21074 | 24427 | 26424 | 27981 | 27825 | 23194 | 24541 | 26633
627 | 627 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 3 | 14089 | 15418 | 17273 | 18830 | 19803 | 17374 | 17384 | 19107 | 20949 | 23498 | 23506 | 21556 | 20991 | 24198 | 26184 | 27413 | 27201 | 23040 | 24418 | 26340
628 | 628 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 4 | 13934 | 15433 | 17247 | 18817 | 19725 | 17151 | 17202 | 19100 | 20781 | 23204 | 23072 | 21006 | 20522 | 23728 | 25612 | 26695 | 26376 | 22398 | 23989 | 25707
629 | 629 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 5 | 13835 | 15589 | 17323 | 18929 | 19729 | 16885 | 17007 | 19146 | 20628 | 22945 | 22684 | 20316 | 19912 | 23210 | 24938 | 25882 | 25599 | 21578 | 23575 | 24989
630 | 630 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 6 | 13800 | 16110 | 17824 | 19471 | 20104 | 16709 | 16851 | 19461 | 20805 | 23042 | 22521 | 19603 | 19319 | 23016 | 24679 | 25515 | 25046 | 20781 | 23393 | 24590
631 | 631 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 7 | 14116 | 17298 | 19047 | 20698 | 21252 | 16974 | 17062 | 20546 | 21644 | 23937 | 23285 | 19428 | 19227 | 23548 | 25363 | 26137 | 25451 | 20554 | 24050 | 24974
632 | 632 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 8 | 15124 | 18863 | 20467 | 22283 | 22898 | 17985 | 17929 | 22133 | 22930 | 25391 | 24810 | 20322 | 19925 | 24607 | 26529 | 27396 | 26823 | 21200 | 25415 | 25941
633 | 633 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 9 | 15849 | 19307 | 20824 | 22440 | 23072 | 18752 | 18697 | 22591 | 23378 | 25580 | 25167 | 21044 | 20591 | 24898 | 26615 | 27553 | 27122 | 21820 | 25734 | 26188
634 | 634 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 10 | 16231 | 19414 | 20838 | 22277 | 22916 | 19145 | 19218 | 22736 | 23575 | 25519 | 25148 | 21515 | 21097 | 25115 | 26611 | 27600 | 27048 | 22365 | 25964 | 26465
635 | 635 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 11 | 16339 | 19407 | 20910 | 22129 | 22866 | 19253 | 19545 | 22766 | 23811 | 25551 | 25066 | 21690 | 20974 | 24952 | 26121 | 27688 | 26550 | 22281 | 26070 | 26350
636 | 636 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 12 | 16460 | 19489 | 20987 | 22013 | 22752 | 19264 | 19707 | 22719 | 23757 | 25340 | 24782 | 21658 | 20694 | 24583 | 25588 | 27720 | 26267 | 22004 | 25987 | 25995
637 | 637 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 13 | 16324 | 19381 | 20775 | 21740 | 22455 | 19135 | 19720 | 22536 | 23505 | 24943 | 24393 | 21509 | 20502 | 24040 | 24895 | 27259 | 25673 | 21801 | 25767 | 25439
638 | 638 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 14 | 16284 | 19330 | 20719 | 21625 | 22430 | 19097 | 19684 | 22494 | 23403 | 24895 | 24286 | 21460 | 20194 | 23616 | 24460 | 26935 | 25164 | 21465 | 25635 | 24970
639 | 639 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 15 | 16191 | 19312 | 20643 | 21528 | 22169 | 18913 | 19603 | 22308 | 23091 | 24456 | 23895 | 21161 | 20334 | 23368 | 24280 | 26635 | 25004 | 21583 | 25230 | 24683
640 | 640 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 16 | 16285 | 19518 | 20804 | 21590 | 22018 | 18830 | 19699 | 22291 | 23151 | 24017 | 23559 | 20881 | 20889 | 23917 | 24465 | 26155 | 25066 | 22102 | 25128 | 25179
641 | 641 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 17 | 16809 | 20188 | 21452 | 22125 | 22322 | 19341 | 20230 | 22818 | 23600 | 23822 | 23882 | 21322 | 21912 | 24832 | 24847 | 25418 | 25698 | 23153 | 25671 | 26109
642 | 642 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 18 | 17612 | 21100 | 22174 | 23117 | 23122 | 20067 | 21217 | 23671 | 24177 | 24352 | 24778 | 22252 | 23125 | 26026 | 25781 | 26117 | 27070 | 24478 | 26972 | 27377
643 | 643 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 19 | 17509 | 21115 | 22303 | 23625 | 23440 | 20037 | 21221 | 23702 | 24447 | 24779 | 25068 | 22567 | 23460 | 26709 | 26646 | 26775 | 27803 | 24986 | 27681 | 28249
644 | 644 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 20 | 17043 | 20786 | 22186 | 23723 | 23551 | 19680 | 21107 | 23605 | 24573 | 25218 | 25283 | 22563 | 23750 | 27416 | 27678 | 27773 | 28502 | 25461 | 28180 | 29161
645 | 645 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 21 | 16700 | 20317 | 21944 | 23647 | 23429 | 19477 | 20957 | 23288 | 24704 | 25521 | 25431 | 22891 | 24060 | 28058 | 28698 | 28681 | 29137 | 26016 | 28524 | 30052
646 | 646 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 22 | 16326 | 19603 | 21328 | 22966 | 22763 | 19151 | 20545 | 22681 | 24391 | 25361 | 25172 | 22898 | 23934 | 28028 | 29173 | 29049 | 29107 | 26032 | 28266 | 30186
647 | 647 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 23 | 15753 | 18596 | 20382 | 21871 | 21721 | 18709 | 20007 | 21834 | 23670 | 24724 | 24515 | 22692 | 23600 | 27374 | 28782 | 28799 | 28551 | 25779 | 27555 | 29629
648 | 648 | 27 | 1 | 27 | Winter | 1 | 27 | Winter | 24 | 15032 | 17550 | 19276 | 20729 | 20553 | 18166 | 19397 | 21025 | 22863 | 23867 | 23774 | 22390 | 23129 | 26629 | 28086 | 28095 | 27860 | 25351 | 26860 | 28937
649 | 649 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 1 | 14143 | 16834 | 18580 | 19530 | 19656 | 17035 | 18565 | 20477 | 22261 | 23251 | 23095 | 20702 | 22515 | 26140 | 27691 | 27959 | 27145 | 24685 | 26892 | 28529
650 | 650 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 2 | 13714 | 16437 | 18170 | 19163 | 19043 | 16649 | 18232 | 20095 | 21965 | 22659 | 22628 | 20290 | 22031 | 25650 | 27283 | 27179 | 26509 | 24141 | 26240 | 27984
651 | 651 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 3 | 13486 | 16299 | 18087 | 19069 | 18932 | 16582 | 18354 | 20113 | 22022 | 22627 | 22508 | 20242 | 21977 | 25443 | 26746 | 26584 | 26050 | 24028 | 25967 | 27710
652 | 652 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 4 | 13340 | 16240 | 18069 | 18989 | 18778 | 16403 | 18362 | 19974 | 21822 | 22263 | 22068 | 19806 | 21703 | 24901 | 26043 | 25775 | 25319 | 23595 | 25317 | 26989
653 | 653 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 5 | 13224 | 16311 | 18205 | 19027 | 18761 | 16247 | 18458 | 19890 | 21625 | 21965 | 21524 | 19266 | 21498 | 24293 | 25292 | 25041 | 24329 | 23200 | 24616 | 26160
654 | 654 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 6 | 13188 | 16852 | 18785 | 19468 | 19078 | 16157 | 18862 | 20173 | 21896 | 21928 | 21051 | 18773 | 21535 | 24121 | 24999 | 24553 | 23424 | 23054 | 24261 | 25759
655 | 655 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 7 | 13554 | 18130 | 20058 | 20675 | 20160 | 16418 | 20022 | 21113 | 22995 | 22791 | 21089 | 18774 | 22349 | 24889 | 25699 | 25022 | 23216 | 23754 | 24681 | 26347
656 | 656 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 8 | 14444 | 19579 | 21620 | 22283 | 21761 | 17241 | 21587 | 22408 | 24368 | 24308 | 21861 | 19469 | 23751 | 26058 | 26950 | 26385 | 23888 | 25102 | 25624 | 27404
657 | 657 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 9 | 15138 | 19899 | 21768 | 22436 | 22183 | 17989 | 22038 | 22870 | 24516 | 24662 | 22507 | 20145 | 24107 | 26158 | 27105 | 26679 | 24373 | 25405 | 25865 | 27424
658 | 658 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 10 | 15484 | 19729 | 21426 | 22092 | 21909 | 18298 | 21965 | 22836 | 24258 | 24410 | 22893 | 20499 | 24155 | 26007 | 27005 | 26449 | 24896 | 25490 | 25999 | 27309
659 | 659 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 11 | 15373 | 19333 | 20787 | 21505 | 21173 | 17999 | 21331 | 22364 | 23461 | 23574 | 22557 | 20122 | 23982 | 25266 | 26844 | 25702 | 25111 | 25347 | 25632 | 26606
660 | 660 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 12 | 15535 | 19240 | 20526 | 21212 | 20732 | 17915 | 20998 | 22009 | 22886 | 22921 | 22273 | 19879 | 23931 | 24752 | 26911 | 25447 | 25489 | 25300 | 25314 | 26099
661 | 661 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 13 | 15428 | 18937 | 20121 | 20780 | 20234 | 17753 | 20630 | 21556 | 22312 | 22309 | 21988 | 19650 | 23688 | 24024 | 26415 | 24821 | 25399 | 25037 | 24720 | 25357
662 | 662 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 14 | 15320 | 18848 | 19941 | 20671 | 20028 | 17586 | 20437 | 21299 | 22022 | 22021 | 21700 | 19421 | 23661 | 23664 | 26166 | 24388 | 25130 | 24975 | 24330 | 24962
663 | 663 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 15 | 15473 | 18929 | 20008 | 20612 | 19984 | 17746 | 20520 | 21273 | 22062 | 21936 | 21566 | 19561 | 23282 | 23485 | 25862 | 24227 | 24871 | 24569 | 24035 | 24760
664 | 664 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 16 | 15987 | 19386 | 20423 | 20879 | 20321 | 18340 | 21047 | 21876 | 22472 | 22241 | 21743 | 20151 | 23244 | 23710 | 25416 | 24329 | 24494 | 24489 | 24551 | 24946
665 | 665 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 17 | 17109 | 20428 | 21390 | 21659 | 21254 | 19416 | 22140 | 22924 | 23259 | 23178 | 22659 | 21356 | 23944 | 24266 | 24860 | 25146 | 24634 | 25219 | 25664 | 25531
666 | 666 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 18 | 18230 | 21299 | 22546 | 22603 | 22234 | 20588 | 23157 | 23679 | 23904 | 24186 | 23784 | 22582 | 25197 | 25232 | 25604 | 26568 | 26139 | 26585 | 26981 | 26584
667 | 667 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 19 | 18120 | 21423 | 23057 | 22901 | 22322 | 20594 | 23167 | 23911 | 24382 | 24396 | 24362 | 22867 | 25732 | 26046 | 26219 | 27268 | 26744 | 27294 | 27855 | 27596
668 | 668 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 20 | 17897 | 21308 | 23135 | 22994 | 22064 | 20483 | 23049 | 23990 | 24859 | 24531 | 24301 | 23101 | 26054 | 27022 | 27178 | 27927 | 27104 | 27801 | 28781 | 28821
669 | 669 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 21 | 17631 | 21051 | 23064 | 22886 | 21774 | 20326 | 22720 | 24068 | 25240 | 24611 | 24575 | 23376 | 26192 | 28006 | 28065 | 28550 | 27859 | 28173 | 29694 | 30055
670 | 670 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 22 | 17143 | 20436 | 22378 | 22226 | 21232 | 19909 | 22097 | 23725 | 25133 | 24317 | 24430 | 23224 | 25811 | 28458 | 28416 | 28514 | 27933 | 27925 | 29846 | 30691
671 | 671 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 23 | 16461 | 19454 | 21250 | 21156 | 20342 | 19333 | 21218 | 22946 | 24440 | 23626 | 24080 | 22856 | 25018 | 28044 | 28140 | 27939 | 27730 | 27207 | 29276 | 30365
672 | 672 | 28 | 1 | 28 | Winter | 1 | 28 | Winter | 24 | 15621 | 18316 | 20065 | 19952 | 19337 | 18677 | 20359 | 22089 | 23583 | 22873 | 23570 | 22372 | 24283 | 27340 | 27427 | 27245 | 27336 | 26503 | 28587 | 29721
673 | 673 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 1 | 15264 | 18088 | 19361 | 19577 | 19226 | 18404 | 20331 | 22044 | 23254 | 22845 | 22322 | 22138 | 24463 | 27300 | 27666 | 26898 | 25643 | 26877 | 28541 | 29757
674 | 674 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 2 | 14843 | 17636 | 18927 | 18874 | 18706 | 17964 | 19841 | 21636 | 22882 | 22284 | 21883 | 21660 | 23875 | 26904 | 26896 | 26262 | 25142 | 26222 | 27987 | 29300
675 | 675 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 3 | 14661 | 17413 | 18700 | 18614 | 18408 | 17912 | 19689 | 21515 | 22707 | 22011 | 21754 | 21609 | 23668 | 26370 | 26301 | 25802 | 24886 | 25936 | 27700 | 28689
676 | 676 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 4 | 14647 | 17406 | 18635 | 18472 | 18240 | 17932 | 19583 | 21364 | 22459 | 21638 | 21385 | 21392 | 23234 | 25725 | 25541 | 25112 | 24293 | 25306 | 26993 | 27863
677 | 677 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 5 | 14808 | 17555 | 18700 | 18481 | 18080 | 18065 | 19560 | 21244 | 22290 | 21185 | 20926 | 21250 | 22790 | 25035 | 24858 | 24167 | 23461 | 24628 | 26181 | 26955
678 | 678 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 6 | 15347 | 18134 | 19169 | 18821 | 18102 | 18498 | 19902 | 21584 | 22492 | 20805 | 20482 | 21352 | 22680 | 24794 | 24405 | 23312 | 22626 | 24286 | 25786 | 26522
679 | 679 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 7 | 16568 | 19424 | 20411 | 19942 | 18534 | 19686 | 20921 | 22751 | 23483 | 20915 | 20375 | 22210 | 23289 | 25531 | 24912 | 23113 | 22224 | 24711 | 26371 | 27109
680 | 680 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 8 | 18125 | 21037 | 22061 | 21574 | 19430 | 21281 | 22299 | 24201 | 24973 | 21766 | 20953 | 23655 | 24379 | 26824 | 26312 | 23811 | 22755 | 25686 | 27454 | 28337
681 | 681 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 9 | 18523 | 21197 | 22185 | 21966 | 20058 | 21694 | 22743 | 24346 | 25128 | 22414 | 21562 | 24008 | 24661 | 26962 | 26603 | 24276 | 23329 | 25908 | 27459 | 28442
682 | 682 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 10 | 18600 | 20996 | 21988 | 21850 | 20549 | 21774 | 22855 | 24255 | 25016 | 22968 | 22063 | 24155 | 24829 | 26951 | 26477 | 24892 | 23875 | 26136 | 27450 | 28471
683 | 683 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 11 | 18446 | 20712 | 21806 | 21537 | 20768 | 21638 | 22898 | 24026 | 24899 | 23234 | 22186 | 24072 | 24494 | 26887 | 25808 | 25208 | 23976 | 25862 | 26839 | 28456
684 | 684 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 12 | 18512 | 20616 | 21715 | 21333 | 20900 | 21592 | 22850 | 23789 | 24674 | 23286 | 22159 | 23963 | 24110 | 26898 | 25496 | 25527 | 24064 | 25483 | 26281 | 28476
685 | 685 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 13 | 18424 | 20361 | 21449 | 21026 | 20888 | 21437 | 22618 | 23451 | 24295 | 23242 | 22121 | 23769 | 23579 | 26453 | 24918 | 25485 | 23923 | 24938 | 25584 | 27997
686 | 686 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 14 | 18389 | 20257 | 21426 | 20924 | 20791 | 21388 | 22527 | 23335 | 24249 | 23153 | 22042 | 23700 | 23188 | 26160 | 24438 | 25171 | 23613 | 24501 | 25140 | 27668
687 | 687 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 15 | 18301 | 20106 | 21131 | 20608 | 20372 | 21136 | 22138 | 22974 | 23681 | 22574 | 21757 | 23298 | 22906 | 25834 | 24251 | 24882 | 23618 | 24177 | 24908 | 27296
688 | 688 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 16 | 18610 | 20328 | 21172 | 20666 | 20251 | 21309 | 22324 | 22960 | 23410 | 22286 | 21852 | 23315 | 23517 | 25446 | 24400 | 24559 | 23739 | 24735 | 25130 | 26839
689 | 689 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 17 | 19431 | 21058 | 21704 | 21321 | 20836 | 22076 | 23016 | 23360 | 23428 | 22770 | 22561 | 23957 | 24559 | 24837 | 25163 | 24651 | 24207 | 25799 | 25660 | 26236
690 | 690 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 18 | 20428 | 22219 | 22627 | 22302 | 21788 | 23116 | 23792 | 24012 | 24118 | 23830 | 23551 | 25140 | 25762 | 25548 | 26555 | 26115 | 25714 | 27100 | 26690 | 27021
691 | 691 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 19 | 20485 | 22761 | 22960 | 22427 | 22146 | 23197 | 24079 | 24535 | 24584 | 24428 | 24128 | 25612 | 26389 | 26099 | 27204 | 26680 | 26239 | 27961 | 27688 | 27765
692 | 692 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 20 | 20175 | 22833 | 23039 | 22157 | 21832 | 23097 | 24139 | 24975 | 25009 | 24328 | 24223 | 25867 | 27046 | 26984 | 27798 | 27003 | 26483 | 28872 | 28897 | 28877
693 | 693 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 21 | 19750 | 22710 | 22906 | 21846 | 21626 | 22738 | 24152 | 25280 | 25271 | 24496 | 24379 | 25923 | 27630 | 27787 | 28357 | 27689 | 27001 | 29755 | 30112 | 29910
694 | 694 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 22 | 19007 | 21959 | 22159 | 21233 | 21097 | 22025 | 23689 | 25048 | 25006 | 24222 | 24016 | 25451 | 27530 | 28040 | 28243 | 27679 | 26810 | 29841 | 30693 | 30318
695 | 695 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 23 | 17947 | 20774 | 21021 | 20271 | 20461 | 21048 | 22798 | 24235 | 24245 | 23757 | 23480 | 24622 | 26834 | 27737 | 27640 | 27457 | 26468 | 29249 | 30357 | 30115
696 | 696 | 29 | 1 | 29 | Winter | 1 | 29 | Winter | 24 | 16896 | 19552 | 19778 | 19227 | 19682 | 20142 | 21882 | 23319 | 23343 | 23233 | 22998 | 23883 | 26093 | 27029 | 26941 | 27067 | 26122 | 28561 | 29724 | 29467
697 | 697 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 1 | 16440 | 18581 | 19097 | 18798 | 18521 | 19731 | 21436 | 22580 | 22969 | 21737 | 22261 | 23850 | 25794 | 27103 | 26442 | 25292 | 25522 | 28347 | 29600 | 29571
698 | 698 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 2 | 15995 | 18129 | 18395 | 18263 | 18076 | 19229 | 21015 | 22197 | 22254 | 21301 | 21869 | 23288 | 25318 | 26359 | 25827 | 24807 | 25150 | 27802 | 29152 | 28752
699 | 699 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 3 | 15788 | 17900 | 18134 | 17960 | 17929 | 19081 | 20916 | 22047 | 22076 | 21224 | 21821 | 23109 | 25126 | 25789 | 25392 | 24566 | 24932 | 27527 | 28550 | 28111
700 | 700 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 4 | 15726 | 17833 | 17999 | 17800 | 17770 | 19000 | 20802 | 21852 | 21771 | 20913 | 21462 | 22730 | 24640 | 25074 | 24735 | 23993 | 24336 | 26827 | 27724 | 27209
701 | 701 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 5 | 15780 | 17895 | 18006 | 17644 | 17636 | 18996 | 20723 | 21734 | 21533 | 20500 | 21288 | 22338 | 24087 | 24431 | 23824 | 23176 | 23761 | 26016 | 26809 | 26366
702 | 702 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 6 | 16291 | 18347 | 18361 | 17680 | 17545 | 19366 | 21115 | 22008 | 21541 | 20107 | 21413 | 22279 | 23952 | 24015 | 22995 | 22349 | 23546 | 25620 | 26355 | 25731
703 | 703 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 7 | 17599 | 19642 | 19527 | 18144 | 17673 | 20444 | 22354 | 23086 | 22495 | 20061 | 22362 | 22978 | 24786 | 24583 | 22851 | 21984 | 24357 | 26245 | 26962 | 26148
704 | 704 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 8 | 19092 | 21255 | 21141 | 19021 | 18329 | 21828 | 23808 | 24587 | 24060 | 20644 | 23870 | 24114 | 25999 | 26002 | 23563 | 22519 | 25826 | 27336 | 28185 | 27500
705 | 705 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 9 | 19362 | 21369 | 21532 | 19646 | 18985 | 22254 | 23963 | 24759 | 24406 | 21281 | 24173 | 24414 | 26101 | 26293 | 24039 | 23098 | 26034 | 27347 | 28285 | 27776
706 | 706 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 10 | 19369 | 21238 | 21468 | 20181 | 19469 | 22366 | 23886 | 24662 | 24349 | 21790 | 24207 | 24650 | 26134 | 26244 | 24732 | 23724 | 26061 | 27419 | 28397 | 27759
707 | 707 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 11 | 19188 | 20993 | 21040 | 20238 | 19349 | 22141 | 23364 | 24224 | 23747 | 21536 | 23860 | 24424 | 25602 | 25690 | 25165 | 23946 | 25716 | 26926 | 28501 | 27257
708 | 708 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 12 | 19012 | 20734 | 20651 | 20156 | 19148 | 21822 | 22829 | 23683 | 23095 | 21139 | 23395 | 23973 | 24966 | 25312 | 25418 | 23970 | 25406 | 26302 | 28458 | 26894
709 | 709 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 13 | 18704 | 20343 | 20191 | 19966 | 18937 | 21369 | 22246 | 23043 | 22441 | 20803 | 22972 | 23419 | 24260 | 24713 | 25351 | 23807 | 24959 | 25580 | 27956 | 26259
710 | 710 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 14 | 18652 | 20303 | 20038 | 19794 | 18762 | 21175 | 22007 | 22855 | 22187 | 20562 | 22774 | 23108 | 23930 | 24314 | 25113 | 23572 | 24600 | 25214 | 27698 | 25825
711 | 711 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 15 | 18695 | 20164 | 19921 | 19597 | 18835 | 21063 | 21918 | 22589 | 21959 | 20575 | 22581 | 22878 | 23754 | 24171 | 24865 | 23615 | 24482 | 25014 | 27368 | 25643
712 | 712 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 16 | 19090 | 20323 | 20167 | 19698 | 19313 | 21540 | 22228 | 22688 | 22168 | 21065 | 22775 | 23411 | 23956 | 24262 | 24481 | 23670 | 24617 | 25159 | 26838 | 25669
713 | 713 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 17 | 19940 | 20912 | 20885 | 20381 | 20129 | 22401 | 22818 | 22916 | 22907 | 21999 | 23446 | 24302 | 24314 | 24876 | 24422 | 23987 | 25478 | 25542 | 26090 | 26295
714 | 714 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 18 | 20939 | 21958 | 21993 | 21512 | 21340 | 23454 | 23748 | 23847 | 24200 | 23251 | 24555 | 25471 | 25222 | 26239 | 25864 | 25480 | 26621 | 26567 | 26869 | 27743
715 | 715 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 19 | 21084 | 22247 | 22083 | 21822 | 21640 | 23701 | 24225 | 24236 | 24438 | 23738 | 24994 | 26012 | 25962 | 26820 | 26371 | 25963 | 27013 | 27549 | 27593 | 28516
716 | 716 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 20 | 20952 | 22307 | 21767 | 21477 | 21432 | 23702 | 24598 | 24578 | 24529 | 23756 | 25195 | 26576 | 26855 | 27341 | 26633 | 26169 | 27412 | 28736 | 28688 | 29267
717 | 717 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 21 | 20687 | 22172 | 21444 | 21253 | 21228 | 23674 | 24840 | 24771 | 24552 | 23844 | 25297 | 27089 | 27759 | 27841 | 27271 | 26663 | 27853 | 29944 | 29736 | 30027
718 | 718 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 22 | 19990 | 21412 | 20808 | 20705 | 20623 | 23152 | 24545 | 24451 | 24139 | 23440 | 24817 | 26926 | 28109 | 27682 | 27226 | 26447 | 27534 | 30502 | 30138 | 30020
719 | 719 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 23 | 18946 | 20259 | 19817 | 20041 | 19867 | 22212 | 23669 | 23624 | 23297 | 22846 | 23940 | 26197 | 27655 | 27059 | 26982 | 26096 | 26882 | 30153 | 29935 | 29464
720 | 720 | 30 | 1 | 30 | Winter | 1 | 30 | Winter | 24 | 17810 | 18986 | 18738 | 19231 | 19166 | 21250 | 22711 | 22671 | 22501 | 22362 | 23148 | 25439 | 26955 | 26353 | 26583 | 25742 | 26118 | 29513 | 29289 | 28816
721 | 721 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 1 | 17191 | 18141 | 18188 | 17940 | 18277 | 20620 | 21792 | 22139 | 21969 | 21515 | 23315 | 24958 | 26595 | 25731 | 24709 | 24995 | 26941 | 29223 | 29246 | 28127
722 | 722 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 2 | 16755 | 17493 | 17661 | 17485 | 17911 | 20197 | 21411 | 21436 | 21405 | 21146 | 22835 | 24505 | 26224 | 25133 | 24237 | 24636 | 26468 | 28779 | 28435 | 27469
723 | 723 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 3 | 16544 | 17187 | 17338 | 17309 | 17824 | 20082 | 21255 | 21250 | 21167 | 21121 | 22718 | 24338 | 25716 | 24715 | 24009 | 24428 | 26163 | 28181 | 27792 | 26980
724 | 724 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 4 | 16548 | 17057 | 17200 | 17165 | 17683 | 20008 | 21111 | 21011 | 20865 | 20830 | 22377 | 23925 | 25133 | 24119 | 23481 | 23869 | 25541 | 27379 | 26908 | 26203
725 | 725 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 5 | 16711 | 17099 | 17079 | 17071 | 17776 | 19996 | 21073 | 20864 | 20484 | 20740 | 22043 | 23468 | 24513 | 23287 | 22725 | 23344 | 24834 | 26503 | 26090 | 25143
726 | 726 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 6 | 17305 | 17495 | 17174 | 17058 | 18236 | 20478 | 21459 | 21006 | 20190 | 20971 | 22055 | 23449 | 24351 | 22541 | 21986 | 23192 | 24507 | 26095 | 25499 | 24173
727 | 727 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 7 | 18594 | 18664 | 17667 | 17185 | 19477 | 21759 | 22589 | 22024 | 20366 | 21959 | 22759 | 24331 | 25149 | 22433 | 21628 | 24003 | 24875 | 26701 | 25902 | 23921
728 | 728 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 8 | 20164 | 20238 | 18546 | 17818 | 21076 | 23212 | 24091 | 23607 | 21204 | 23471 | 23967 | 25558 | 26437 | 23149 | 22153 | 25451 | 25882 | 27907 | 27231 | 24579
729 | 729 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 9 | 20358 | 20642 | 19214 | 18483 | 21425 | 23397 | 24297 | 23983 | 21907 | 23823 | 24313 | 25710 | 26601 | 23669 | 22753 | 25691 | 26115 | 28032 | 27516 | 25057
730 | 730 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 10 | 20048 | 20417 | 19602 | 18804 | 21258 | 23142 | 24027 | 23750 | 22308 | 23686 | 24416 | 25568 | 26503 | 24191 | 23203 | 25549 | 26240 | 27973 | 27327 | 25628
731 | 731 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 11 | 19600 | 19965 | 19615 | 18652 | 20954 | 22557 | 23523 | 23097 | 22121 | 23247 | 24205 | 24938 | 26469 | 24519 | 23344 | 25113 | 25902 | 27980 | 26743 | 25995
732 | 732 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 12 | 19328 | 19640 | 19587 | 18504 | 20700 | 22066 | 23013 | 22479 | 21830 | 22784 | 23786 | 24299 | 26414 | 24772 | 23369 | 24806 | 25648 | 27935 | 26381 | 26255
733 | 733 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 13 | 18974 | 19265 | 19462 | 18362 | 20459 | 21547 | 22435 | 21892 | 21541 | 22401 | 23370 | 23633 | 25984 | 24745 | 23246 | 24401 | 25287 | 27476 | 25786 | 26209
734 | 734 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 14 | 18850 | 19109 | 19296 | 18192 | 20355 | 21314 | 22255 | 21643 | 21287 | 22204 | 23041 | 23305 | 25763 | 24506 | 23009 | 24040 | 24881 | 27212 | 25347 | 25934
735 | 735 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 15 | 18860 | 19023 | 19128 | 18295 | 20274 | 21258 | 22028 | 21453 | 21032 | 22037 | 22746 | 23157 | 25501 | 24283 | 23074 | 23947 | 24621 | 26906 | 25189 | 25689
736 | 736 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 16 | 19292 | 19343 | 19298 | 18854 | 20594 | 21656 | 22227 | 21759 | 21216 | 22337 | 23202 | 23465 | 25146 | 23993 | 23228 | 24176 | 24959 | 26474 | 25311 | 25356
737 | 737 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 17 | 20124 | 20137 | 20060 | 19765 | 21410 | 22352 | 22553 | 22588 | 22024 | 23099 | 23977 | 23921 | 24490 | 24027 | 23647 | 25135 | 25691 | 25825 | 26037 | 25410
738 | 738 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 18 | 21394 | 21220 | 21122 | 20924 | 22340 | 23281 | 23439 | 23825 | 23356 | 24140 | 24959 | 24789 | 25153 | 25439 | 25097 | 26250 | 26869 | 26594 | 27478 | 26898
739 | 739 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 19 | 21930 | 21296 | 21402 | 21196 | 22456 | 23735 | 23787 | 23997 | 23874 | 24507 | 25496 | 25457 | 25633 | 25890 | 25542 | 26612 | 27608 | 27312 | 28243 | 27540
740 | 740 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 20 | 21963 | 20921 | 21005 | 20956 | 22347 | 24036 | 24051 | 23984 | 23672 | 24615 | 25950 | 26249 | 26423 | 26073 | 25698 | 26972 | 28372 | 28379 | 28967 | 27913
741 | 741 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 21 | 21819 | 20598 | 20747 | 20709 | 22072 | 24201 | 24165 | 23904 | 23765 | 24624 | 26308 | 27049 | 27154 | 26645 | 26128 | 27376 | 29179 | 29408 | 29710 | 28746
742 | 742 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 22 | 21068 | 19942 | 20200 | 20100 | 21369 | 23857 | 23804 | 23432 | 23449 | 24116 | 26034 | 27348 | 27363 | 26572 | 25888 | 27043 | 29140 | 29809 | 29701 | 28834
743 | 743 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 23 | 19866 | 18940 | 19517 | 19340 | 20362 | 22950 | 22938 | 22560 | 22915 | 23215 | 25279 | 26855 | 27037 | 26303 | 25522 | 26381 | 28600 | 29593 | 29155 | 28652
744 | 744 | 31 | 1 | 31 | Winter | 1 | 31 | Winter | 24 | 18642 | 17829 | 18652 | 18601 | 19354 | 21939 | 21932 | 21707 | 22345 | 22415 | 24493 | 26135 | 26316 | 25881 | 25159 | 25612 | 27880 | 28932 | 28505 | 28288
745 | 745 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 1 | 17646 | 17420 | 17515 | 17891 | 19141 | 21299 | 21620 | 21437 | 21080 | 22818 | 24793 | 25723 | 26208 | 24041 | 24416 | 26362 | 28095 | 28858 | 27789 | 26163
746 | 746 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 2 | 17219 | 16898 | 17086 | 17549 | 18726 | 20898 | 20966 | 20928 | 20705 | 22417 | 24369 | 25381 | 25494 | 23591 | 24071 | 25906 | 27680 | 28061 | 27143 | 25665
747 | 747 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 3 | 16910 | 16463 | 16773 | 17306 | 18436 | 20570 | 20584 | 20480 | 20403 | 22090 | 23959 | 24923 | 24962 | 23395 | 23893 | 25629 | 27429 | 27437 | 26671 | 25416
748 | 748 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 4 | 16829 | 16295 | 16602 | 17135 | 18310 | 20412 | 20338 | 20178 | 20094 | 21757 | 23508 | 24400 | 24313 | 22903 | 23364 | 25034 | 26734 | 26563 | 25897 | 24777
749 | 749 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 5 | 16890 | 16159 | 16488 | 17208 | 18293 | 20388 | 20200 | 19817 | 19707 | 21444 | 23119 | 23851 | 23746 | 22188 | 22868 | 24356 | 25919 | 25748 | 24840 | 23884
750 | 750 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 6 | 17373 | 16255 | 16506 | 17699 | 18703 | 20809 | 20417 | 19614 | 19424 | 21528 | 23235 | 23785 | 23442 | 21501 | 22758 | 24072 | 25586 | 25178 | 23883 | 23021
751 | 751 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 7 | 18677 | 16765 | 16672 | 18965 | 19776 | 21929 | 21515 | 19884 | 19425 | 22317 | 24143 | 24658 | 24052 | 21176 | 23597 | 24470 | 26277 | 25598 | 23634 | 22588
752 | 752 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 8 | 20286 | 17693 | 17376 | 20613 | 21289 | 23556 | 23190 | 20826 | 20079 | 23646 | 25287 | 26012 | 25512 | 21748 | 25092 | 25534 | 27234 | 26969 | 24326 | 23125
753 | 753 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 9 | 20407 | 18383 | 18048 | 20949 | 21723 | 23718 | 23571 | 21549 | 20745 | 24018 | 25368 | 26194 | 25826 | 22357 | 25343 | 25776 | 27219 | 27253 | 24803 | 23702
754 | 754 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 10 | 20201 | 18870 | 18473 | 20884 | 21799 | 23508 | 23446 | 22063 | 21203 | 24231 | 25372 | 26144 | 25657 | 22860 | 25257 | 25953 | 27159 | 27123 | 25428 | 24244
755 | 755 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 11 | 20281 | 19327 | 18814 | 21109 | 22135 | 23567 | 23407 | 22532 | 21554 | 24693 | 25581 | 26299 | 25217 | 23193 | 25018 | 25805 | 26560 | 26729 | 25994 | 24608
756 | 756 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 12 | 20289 | 19586 | 19013 | 21253 | 22304 | 23535 | 23293 | 22789 | 21732 | 24846 | 25591 | 26259 | 24855 | 23239 | 24728 | 25571 | 25976 | 26381 | 26270 | 24648
757 | 757 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 13 | 20134 | 19672 | 19110 | 21285 | 22292 | 23323 | 23036 | 22846 | 21797 | 24792 | 25421 | 25903 | 24367 | 23185 | 24392 | 25279 | 25432 | 25860 | 26295 | 24578
758 | 758 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 14 | 19897 | 19328 | 18747 | 21002 | 21930 | 22996 | 22618 | 22426 | 21385 | 24308 | 25126 | 25459 | 23725 | 22716 | 23799 | 24644 | 25003 | 25182 | 25786 | 24078
759 | 759 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 15 | 19868 | 19270 | 18960 | 21048 | 21895 | 22934 | 22575 | 22320 | 21569 | 24168 | 25112 | 25265 | 23671 | 22845 | 23770 | 24452 | 24933 | 25087 | 25599 | 24191
760 | 760 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 16 | 19956 | 19257 | 19306 | 21134 | 22036 | 22898 | 22565 | 22157 | 21773 | 24232 | 24904 | 24935 | 23872 | 23008 | 24007 | 24801 | 25084 | 25215 | 25266 | 24328
761 | 761 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 17 | 20212 | 19543 | 19682 | 21356 | 22127 | 22791 | 22617 | 22120 | 21910 | 24066 | 24363 | 24165 | 24468 | 23310 | 24850 | 25415 | 25483 | 25828 | 25205 | 24655
762 | 762 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 18 | 21071 | 20428 | 20610 | 22070 | 22835 | 23721 | 23591 | 23161 | 22857 | 24739 | 24730 | 24685 | 25710 | 24652 | 25864 | 26490 | 25982 | 27183 | 26605 | 26063
763 | 763 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 19 | 21294 | 20597 | 20784 | 22072 | 23031 | 24111 | 23600 | 23487 | 23153 | 25045 | 25047 | 25091 | 26223 | 25052 | 26184 | 27186 | 26390 | 27938 | 27238 | 26618
764 | 764 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 20 | 21292 | 20169 | 20476 | 21894 | 22905 | 24243 | 23459 | 23142 | 23024 | 25331 | 25500 | 25787 | 26632 | 25148 | 26495 | 27893 | 27259 | 28636 | 27598 | 26857
765 | 765 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 21 | 21088 | 19836 | 20150 | 21535 | 22688 | 24145 | 23232 | 23070 | 22942 | 25508 | 25869 | 26379 | 27002 | 25478 | 26812 | 28612 | 28259 | 29321 | 28384 | 27395
766 | 766 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 22 | 20334 | 19272 | 19524 | 20814 | 22042 | 23462 | 22688 | 22668 | 22463 | 25145 | 25822 | 26550 | 26814 | 25231 | 26473 | 28568 | 28803 | 29323 | 28490 | 27270
767 | 767 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 23 | 19226 | 18632 | 18800 | 19865 | 21140 | 22433 | 21867 | 22189 | 21943 | 24459 | 25280 | 26192 | 26190 | 24857 | 25806 | 28017 | 28580 | 28783 | 28318 | 26971
768 | 768 | 32 | 2 | 1 | Winter | 2 | 1 | Winter | 24 | 17960 | 17778 | 18036 | 18856 | 20139 | 21352 | 21001 | 21606 | 21469 | 23713 | 24539 | 25448 | 25465 | 24480 | 25027 | 27286 | 27888 | 28119 | 27949 | 26642
769 | 769 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 1 | 17494 | 16912 | 17529 | 18783 | 20320 | 21050 | 20932 | 20614 | 21130 | 24128 | 24176 | 25654 | 25160 | 24057 | 26042 | 27810 | 27871 | 27734 | 26174 | 26173
770 | 770 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 2 | 16930 | 16492 | 17207 | 18383 | 19898 | 20431 | 20460 | 20272 | 20865 | 23753 | 23699 | 24965 | 24596 | 23734 | 25608 | 27407 | 27261 | 27092 | 25678 | 25801
771 | 771 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 3 | 16514 | 16140 | 16936 | 18062 | 19659 | 20024 | 19985 | 19946 | 20584 | 23442 | 23323 | 24436 | 24197 | 23552 | 25327 | 27146 | 26935 | 26599 | 25408 | 25572
772 | 772 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 4 | 16358 | 15966 | 16774 | 17952 | 19528 | 19809 | 19728 | 19680 | 20281 | 23074 | 22871 | 23865 | 23664 | 23069 | 24779 | 26497 | 26219 | 25848 | 24780 | 24943
773 | 773 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 5 | 16382 | 15866 | 16872 | 17971 | 19549 | 19724 | 19437 | 19360 | 20204 | 22759 | 22511 | 23385 | 22897 | 22629 | 24155 | 25731 | 25439 | 24822 | 23900 | 24330
774 | 774 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 6 | 16753 | 15852 | 17380 | 18389 | 20052 | 19963 | 19285 | 19116 | 20478 | 22877 | 22493 | 23153 | 22206 | 22553 | 23896 | 25418 | 24943 | 23865 | 23007 | 24095
775 | 775 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 7 | 17951 | 16084 | 18690 | 19531 | 21368 | 21119 | 19645 | 19220 | 21553 | 23888 | 23343 | 23858 | 22173 | 23432 | 24352 | 26162 | 25438 | 23645 | 22604 | 24883
776 | 776 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 8 | 19509 | 16750 | 20296 | 21044 | 22708 | 22768 | 20597 | 19880 | 23126 | 25079 | 24612 | 25305 | 22908 | 24886 | 25390 | 27100 | 26612 | 24306 | 23095 | 26305
777 | 777 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 9 | 19869 | 17401 | 20599 | 21439 | 22832 | 23122 | 21295 | 20550 | 23454 | 25232 | 24726 | 25606 | 23412 | 25111 | 25624 | 27071 | 26692 | 24749 | 23655 | 26486
778 | 778 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 10 | 19537 | 17649 | 20333 | 21272 | 22443 | 22753 | 21546 | 20755 | 23171 | 24927 | 24296 | 25283 | 23830 | 24870 | 25641 | 26858 | 26298 | 25215 | 24051 | 26276
779 | 779 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 11 | 19228 | 17720 | 20262 | 21228 | 22003 | 22272 | 21551 | 20597 | 22896 | 24399 | 23862 | 24747 | 24270 | 24551 | 25398 | 26173 | 25729 | 25693 | 24324 | 25980
780 | 780 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 12 | 18948 | 17708 | 20161 | 21131 | 21508 | 21846 | 21468 | 20422 | 22636 | 23815 | 23397 | 24261 | 24415 | 24138 | 25046 | 25460 | 25284 | 25850 | 24238 | 25565
781 | 781 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 13 | 18698 | 17720 | 20110 | 21018 | 21173 | 21454 | 21372 | 20326 | 22439 | 23352 | 22950 | 23774 | 24455 | 23802 | 24755 | 24910 | 24895 | 25871 | 24170 | 25207
782 | 782 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 14 | 18254 | 17303 | 19741 | 20577 | 20827 | 20913 | 20813 | 19763 | 21914 | 22887 | 22502 | 23123 | 23963 | 23198 | 24109 | 24472 | 24496 | 25344 | 23651 | 24565
783 | 783 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 15 | 18360 | 17583 | 19891 | 20673 | 20978 | 20994 | 20833 | 20071 | 22026 | 22996 | 22409 | 23147 | 23875 | 23243 | 23991 | 24472 | 24315 | 25227 | 23831 | 24584
784 | 784 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 16 | 18885 | 18302 | 20400 | 21253 | 21603 | 21502 | 21215 | 20838 | 22527 | 23554 | 22602 | 23575 | 23804 | 23703 | 24550 | 24837 | 24313 | 25103 | 24167 | 25005
785 | 785 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 17 | 19661 | 19154 | 21166 | 21965 | 22578 | 22292 | 21956 | 21797 | 23222 | 24243 | 23193 | 24289 | 23847 | 24675 | 25289 | 25357 | 24852 | 25166 | 24611 | 26001
786 | 786 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 18 | 20627 | 20121 | 21879 | 22728 | 23178 | 23324 | 23028 | 22764 | 24022 | 24632 | 24241 | 25531 | 25203 | 25708 | 26391 | 25894 | 26321 | 26634 | 26078 | 27101
787 | 787 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 19 | 20626 | 20280 | 21875 | 22895 | 23462 | 23314 | 23316 | 23017 | 24198 | 24925 | 25095 | 25960 | 25573 | 25976 | 27032 | 26250 | 27390 | 27239 | 26622 | 27520
788 | 788 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 20 | 20227 | 19960 | 21719 | 22758 | 23436 | 23173 | 22956 | 22862 | 24217 | 25220 | 25584 | 26316 | 25710 | 26281 | 27723 | 27110 | 28156 | 27627 | 26896 | 27956
789 | 789 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 21 | 19850 | 19629 | 21324 | 22487 | 23210 | 22884 | 22801 | 22712 | 24058 | 25486 | 25974 | 26579 | 26150 | 26523 | 28376 | 28050 | 29051 | 28385 | 27427 | 28399
790 | 790 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 22 | 19166 | 18999 | 20574 | 21791 | 22512 | 22283 | 22318 | 22176 | 23446 | 25356 | 25554 | 26312 | 26022 | 26132 | 28278 | 28540 | 28930 | 28448 | 27289 | 28122
791 | 791 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 23 | 18192 | 18240 | 19589 | 20852 | 21481 | 21407 | 21788 | 21593 | 22609 | 24737 | 24825 | 25636 | 25725 | 25434 | 27687 | 28282 | 28334 | 28256 | 26966 | 27486
792 | 792 | 33 | 2 | 2 | Winter | 2 | 2 | Winter | 24 | 17094 | 17406 | 18527 | 19791 | 20359 | 20464 | 21116 | 21022 | 21790 | 23919 | 24011 | 24906 | 25302 | 24671 | 26960 | 27595 | 27613 | 27892 | 26644 | 26756
793 | 793 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 1 | 16696 | 16557 | 18071 | 19584 | 19221 | 20011 | 19779 | 20247 | 21886 | 23124 | 23492 | 24407 | 23674 | 25424 | 27254 | 27369 | 27449 | 25924 | 25955 | 27758
794 | 794 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 2 | 16181 | 16211 | 17649 | 19127 | 18760 | 19505 | 19405 | 19947 | 21504 | 22640 | 22964 | 23859 | 23230 | 24993 | 26858 | 26762 | 26783 | 25421 | 25578 | 27272
795 | 795 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 3 | 15822 | 16038 | 17441 | 19017 | 18644 | 19196 | 19262 | 19869 | 21369 | 22519 | 22775 | 23495 | 23043 | 24748 | 26629 | 26460 | 26448 | 25169 | 25358 | 26959
796 | 796 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 4 | 15703 | 15976 | 17393 | 18963 | 18587 | 19044 | 19112 | 19699 | 21190 | 22247 | 22393 | 23022 | 22598 | 24244 | 26013 | 25785 | 25706 | 24549 | 24732 | 26288
797 | 797 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 5 | 15580 | 16076 | 17429 | 19015 | 18684 | 18800 | 18842 | 19680 | 20956 | 21973 | 22060 | 22339 | 21943 | 23674 | 25302 | 25043 | 24904 | 23679 | 24124 | 25513
798 | 798 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 6 | 15655 | 16585 | 17862 | 19560 | 19143 | 18705 | 18672 | 20039 | 21094 | 22049 | 22051 | 21740 | 21276 | 23468 | 25030 | 24576 | 24451 | 22800 | 23889 | 25099
799 | 799 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 7 | 16175 | 17877 | 19025 | 20883 | 20268 | 19077 | 18809 | 21154 | 21960 | 22967 | 23001 | 21761 | 21004 | 23949 | 25803 | 25083 | 25141 | 22384 | 24654 | 25420
800 | 800 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 8 | 17086 | 19478 | 20567 | 22246 | 21652 | 20032 | 19489 | 22755 | 23304 | 24265 | 24404 | 22554 | 21573 | 25035 | 26787 | 26292 | 26405 | 22897 | 26093 | 26404
801 | 801 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 9 | 17725 | 19778 | 20942 | 22352 | 21809 | 20691 | 20139 | 23075 | 23642 | 24378 | 24640 | 23050 | 22159 | 25258 | 26754 | 26365 | 26568 | 23432 | 26258 | 26577
802 | 802 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 10 | 18022 | 19538 | 20775 | 21983 | 21398 | 20973 | 20386 | 22845 | 23637 | 24008 | 24334 | 23405 | 22459 | 25212 | 26484 | 25925 | 26328 | 23773 | 25990 | 26587
803 | 803 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 11 | 18373 | 19648 | 20943 | 21802 | 21306 | 21303 | 20585 | 22965 | 23953 | 23972 | 24274 | 23794 | 22648 | 24913 | 25750 | 25295 | 26334 | 23999 | 25651 | 26343
804 | 804 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 12 | 18507 | 19715 | 21014 | 21490 | 21105 | 21440 | 20646 | 22958 | 23994 | 23779 | 23995 | 23944 | 22576 | 24567 | 25044 | 24862 | 26071 | 23924 | 25243 | 25994
805 | 805 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 13 | 18600 | 19761 | 21036 | 21295 | 20894 | 21514 | 20727 | 22959 | 23955 | 23535 | 23725 | 23997 | 22539 | 24291 | 24508 | 24486 | 25782 | 23865 | 24905 | 25697
806 | 806 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 14 | 18308 | 19540 | 20769 | 21117 | 20742 | 21149 | 20367 | 22652 | 23528 | 23312 | 23420 | 23574 | 22112 | 23717 | 24128 | 24151 | 25421 | 23407 | 24324 | 25071
807 | 807 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 15 | 18351 | 19691 | 20877 | 21262 | 20701 | 21155 | 20654 | 22742 | 23497 | 23194 | 23334 | 23527 | 22344 | 23643 | 24165 | 24009 | 25281 | 23620 | 24377 | 24957
808 | 808 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 16 | 18509 | 19986 | 21167 | 21621 | 20682 | 21218 | 21069 | 22869 | 23744 | 22982 | 23273 | 23436 | 22674 | 24180 | 24502 | 23968 | 25104 | 23915 | 24760 | 25446
809 | 809 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 17 | 18927 | 20443 | 21517 | 22177 | 20714 | 21428 | 21432 | 22923 | 23745 | 22831 | 23296 | 23480 | 23098 | 24920 | 25026 | 24508 | 25226 | 24364 | 25752 | 26202
810 | 810 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 18 | 19868 | 21155 | 22328 | 22825 | 21715 | 22548 | 22411 | 23712 | 24475 | 23855 | 24277 | 24809 | 24501 | 26026 | 25570 | 25996 | 26355 | 25862 | 26882 | 27397
811 | 811 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 19 | 19905 | 21041 | 22369 | 22947 | 22151 | 22645 | 22439 | 23626 | 24483 | 24376 | 24769 | 25113 | 24846 | 26618 | 25890 | 27038 | 27243 | 26412 | 27307 | 28193
812 | 812 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 20 | 19468 | 20819 | 22139 | 22814 | 22182 | 22172 | 22168 | 23503 | 24632 | 24666 | 25116 | 25152 | 24905 | 27232 | 26677 | 27745 | 28029 | 26670 | 27729 | 29014
813 | 813 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 21 | 19139 | 20449 | 21855 | 22562 | 22123 | 21987 | 21985 | 23299 | 24729 | 24979 | 25452 | 25516 | 25198 | 27835 | 27574 | 28623 | 28881 | 27211 | 28190 | 29876
814 | 814 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 22 | 18521 | 19660 | 21110 | 21810 | 21399 | 21444 | 21389 | 22632 | 24265 | 24485 | 25046 | 25303 | 24876 | 27667 | 27997 | 28455 | 28775 | 27042 | 27889 | 29876
815 | 815 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 23 | 17872 | 18662 | 20147 | 20763 | 20410 | 20876 | 20773 | 21755 | 23519 | 23728 | 24417 | 24971 | 24461 | 27053 | 27719 | 27840 | 28330 | 26714 | 27255 | 29362
816 | 816 | 34 | 2 | 3 | Winter | 2 | 3 | Winter | 24 | 17054 | 17582 | 19085 | 19647 | 19404 | 20215 | 20213 | 20948 | 22766 | 22966 | 23670 | 24540 | 24093 | 26328 | 27033 | 27119 | 27648 | 26397 | 26542 | 28692
817 | 817 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 1 | 16080 | 17248 | 19042 | 18691 | 18978 | 19187 | 19708 | 21208 | 23122 | 22745 | 22997 | 23097 | 23544 | 26773 | 26863 | 27006 | 26806 | 25786 | 27582 | 29123
818 | 818 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 2 | 15654 | 16832 | 18596 | 18235 | 18519 | 18813 | 19415 | 20842 | 22681 | 22261 | 22478 | 22681 | 23231 | 26338 | 26280 | 26360 | 26162 | 25414 | 27109 | 28692
819 | 819 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 3 | 15383 | 16609 | 18472 | 18105 | 18370 | 18650 | 19331 | 20710 | 22617 | 22112 | 22321 | 22500 | 23069 | 26136 | 25987 | 26032 | 25866 | 25192 | 26789 | 28406
820 | 820 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 4 | 15245 | 16546 | 18422 | 18059 | 18275 | 18512 | 19182 | 20571 | 22409 | 21803 | 21964 | 22112 | 22627 | 25577 | 25358 | 25331 | 25193 | 24577 | 26127 | 27661
821 | 821 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 5 | 15131 | 16589 | 18481 | 18177 | 18295 | 18265 | 19198 | 20395 | 22172 | 21539 | 21476 | 21506 | 22221 | 24920 | 24657 | 24560 | 24356 | 23968 | 25343 | 26768
822 | 822 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 6 | 15131 | 17040 | 19046 | 18694 | 18720 | 18146 | 19621 | 20632 | 22382 | 21641 | 21084 | 20927 | 22191 | 24715 | 24255 | 24154 | 23604 | 23744 | 24959 | 26345
823 | 823 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 7 | 15361 | 18231 | 20384 | 19850 | 20052 | 18311 | 20801 | 21574 | 23393 | 22679 | 21154 | 20714 | 23099 | 25482 | 24799 | 24875 | 23324 | 24530 | 25281 | 26974
824 | 824 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 8 | 16062 | 19834 | 21765 | 21243 | 21628 | 19011 | 22431 | 22989 | 24684 | 24123 | 21759 | 21323 | 24616 | 26559 | 26036 | 26160 | 23734 | 25981 | 26276 | 27889
825 | 825 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 9 | 16688 | 20205 | 21890 | 21399 | 21922 | 19655 | 22772 | 23349 | 24801 | 24386 | 22204 | 21928 | 24854 | 26516 | 26128 | 26340 | 24077 | 26160 | 26444 | 27803
826 | 826 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 10 | 16899 | 19981 | 21483 | 20947 | 21497 | 19843 | 22493 | 23279 | 24460 | 24025 | 22378 | 22171 | 24514 | 26153 | 25642 | 26056 | 24309 | 25850 | 26402 | 27519
827 | 827 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 11 | 17236 | 20234 | 21382 | 20936 | 21426 | 20118 | 22666 | 23651 | 24390 | 24016 | 22415 | 22472 | 24247 | 25501 | 25116 | 26164 | 24438 | 25608 | 26274 | 26927
828 | 828 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 12 | 17347 | 20299 | 21056 | 20710 | 21082 | 20129 | 22599 | 23612 | 24006 | 23643 | 22171 | 22448 | 23887 | 24852 | 24723 | 25944 | 24332 | 25254 | 25975 | 26267
829 | 829 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 13 | 17386 | 20274 | 20791 | 20431 | 20740 | 20119 | 22503 | 23470 | 23681 | 23256 | 21890 | 22393 | 23546 | 24351 | 24330 | 25640 | 24119 | 24893 | 25663 | 25702
830 | 830 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 14 | 17196 | 20131 | 20703 | 20377 | 20582 | 19847 | 22287 | 23140 | 23536 | 23038 | 21472 | 22068 | 23101 | 24091 | 24101 | 25377 | 23658 | 24409 | 25135 | 25391
831 | 831 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 15 | 17431 | 20215 | 20810 | 20309 | 20529 | 20098 | 22341 | 23077 | 23594 | 22913 | 21320 | 22276 | 23152 | 24127 | 23935 | 25206 | 23475 | 24432 | 24993 | 25384
832 | 832 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 16 | 17919 | 20475 | 21167 | 20298 | 20657 | 20519 | 22473 | 23302 | 23785 | 22860 | 21288 | 22582 | 23535 | 24480 | 23873 | 25000 | 23325 | 24768 | 25447 | 25652
833 | 833 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 17 | 18456 | 20876 | 21796 | 20414 | 21046 | 20986 | 22624 | 23425 | 24123 | 22958 | 21499 | 22931 | 24436 | 25211 | 24344 | 25060 | 23353 | 25695 | 26147 | 26128
834 | 834 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 18 | 19443 | 21689 | 22487 | 21429 | 21926 | 22031 | 23462 | 24208 | 24856 | 23959 | 22777 | 24266 | 25455 | 25958 | 25766 | 26146 | 24755 | 26803 | 27298 | 26709
835 | 835 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 19 | 19494 | 21741 | 22642 | 21879 | 22147 | 22079 | 23386 | 24200 | 25040 | 24378 | 23383 | 24542 | 25679 | 26385 | 26759 | 26989 | 25829 | 27215 | 28074 | 27168
836 | 836 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 20 | 19113 | 21478 | 22480 | 21895 | 22121 | 21797 | 23237 | 24297 | 25121 | 24629 | 23425 | 24526 | 25904 | 27063 | 27408 | 27723 | 26243 | 27635 | 28890 | 28113
837 | 837 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 21 | 18796 | 21159 | 22189 | 21800 | 21963 | 21570 | 22986 | 24293 | 25232 | 24853 | 23721 | 24734 | 26115 | 27792 | 28219 | 28518 | 27026 | 28086 | 29728 | 29213
838 | 838 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 22 | 18153 | 20410 | 21424 | 21077 | 21267 | 20950 | 22295 | 23777 | 24765 | 24391 | 23466 | 24369 | 25689 | 27915 | 28027 | 28396 | 27048 | 27799 | 29727 | 29794
839 | 839 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 23 | 17387 | 19412 | 20340 | 20059 | 20405 | 20305 | 21377 | 22983 | 23895 | 23726 | 23117 | 23925 | 24967 | 27401 | 27387 | 27929 | 26841 | 27151 | 29208 | 29583
840 | 840 | 35 | 2 | 4 | Winter | 2 | 4 | Winter | 24 | 16542 | 18295 | 19162 | 18996 | 19352 | 19678 | 20499 | 22151 | 23028 | 22945 | 22645 | 23526 | 24177 | 26626 | 26637 | 27219 | 26440 | 26400 | 28525 | 28926
841 | 841 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 1 | 15802 | 18179 | 18103 | 18481 | 18616 | 19066 | 20554 | 22377 | 22265 | 22227 | 21818 | 22936 | 24861 | 26235 | 26495 | 26338 | 25127 | 27360 | 28923 | 28768
842 | 842 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 2 | 15484 | 17772 | 17673 | 18040 | 18126 | 18794 | 20216 | 21973 | 21849 | 21774 | 21403 | 22642 | 24457 | 25673 | 25867 | 25718 | 24589 | 26887 | 28504 | 28137
843 | 843 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 3 | 15295 | 17617 | 17520 | 17861 | 17945 | 18677 | 20060 | 21889 | 21727 | 21625 | 21271 | 22498 | 24217 | 25401 | 25556 | 25434 | 24380 | 26570 | 28220 | 27787
844 | 844 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 4 | 15254 | 17569 | 17483 | 17777 | 17827 | 18540 | 19951 | 21727 | 21509 | 21331 | 20998 | 22112 | 23767 | 24830 | 24901 | 24795 | 23852 | 25917 | 27482 | 27020
845 | 845 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 5 | 15349 | 17649 | 17640 | 17839 | 17737 | 18604 | 19846 | 21576 | 21309 | 20933 | 20526 | 21779 | 23260 | 24200 | 24187 | 24007 | 23072 | 25164 | 26605 | 26160
846 | 846 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 6 | 15846 | 18213 | 18190 | 18288 | 17793 | 19057 | 20143 | 21854 | 21475 | 20631 | 20016 | 21819 | 23134 | 23851 | 23819 | 23304 | 22236 | 24797 | 26185 | 25587
847 | 847 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 7 | 17151 | 19572 | 19380 | 19655 | 18160 | 20267 | 21166 | 22930 | 22473 | 20771 | 20006 | 22780 | 23663 | 24443 | 24590 | 23042 | 22029 | 25135 | 26823 | 26044
848 | 848 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 8 | 18744 | 20986 | 20790 | 21240 | 18893 | 21908 | 22647 | 24285 | 23830 | 21434 | 20568 | 24316 | 24793 | 25697 | 25896 | 23461 | 22473 | 26141 | 27742 | 27232
849 | 849 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 9 | 19061 | 21133 | 20948 | 21527 | 19452 | 22235 | 23012 | 24424 | 23964 | 21900 | 21169 | 24572 | 25030 | 25797 | 26092 | 23800 | 22937 | 26308 | 27661 | 27285
850 | 850 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 10 | 18854 | 20779 | 20547 | 21140 | 19594 | 21965 | 22929 | 24074 | 23539 | 22054 | 21491 | 24330 | 25029 | 25408 | 25911 | 24121 | 23424 | 26363 | 27482 | 26920
851 | 851 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 11 | 18866 | 20503 | 20325 | 20800 | 19323 | 21803 | 22912 | 23602 | 23129 | 21637 | 21436 | 24067 | 24845 | 24878 | 26010 | 24270 | 23871 | 26237 | 26895 | 26443
852 | 852 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 12 | 18877 | 20116 | 20025 | 20356 | 18994 | 21595 | 22706 | 23027 | 22635 | 21169 | 21240 | 23747 | 24575 | 24524 | 25824 | 24195 | 23930 | 25973 | 26270 | 26100
853 | 853 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 13 | 18773 | 19788 | 19652 | 19901 | 18640 | 21361 | 22408 | 22529 | 22083 | 20682 | 20962 | 23397 | 24269 | 24119 | 25504 | 23971 | 23805 | 25647 | 25698 | 25680
854 | 854 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 14 | 18461 | 19517 | 19409 | 19538 | 18071 | 20922 | 21848 | 22133 | 21678 | 19995 | 20499 | 22838 | 23676 | 23769 | 25123 | 23393 | 23439 | 25001 | 25263 | 25289
855 | 855 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 15 | 18584 | 19617 | 19364 | 19515 | 18013 | 21017 | 21835 | 22236 | 21566 | 19895 | 20511 | 22883 | 23563 | 23596 | 24942 | 23199 | 23351 | 24846 | 25236 | 25077
856 | 856 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 16 | 18984 | 20136 | 19546 | 19863 | 18371 | 21435 | 22343 | 22769 | 21705 | 20242 | 20920 | 23259 | 24052 | 23525 | 24720 | 23035 | 23307 | 25279 | 25479 | 24936
857 | 857 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 17 | 19748 | 21143 | 20089 | 20750 | 19284 | 22206 | 23132 | 23820 | 22392 | 21209 | 21796 | 24168 | 24745 | 24011 | 24793 | 23086 | 23472 | 25991 | 25969 | 25439
858 | 858 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 18 | 20440 | 21806 | 21034 | 21596 | 20355 | 23026 | 23900 | 24524 | 23436 | 22377 | 22858 | 25111 | 25772 | 25388 | 25836 | 24431 | 24751 | 27119 | 26520 | 26929
859 | 859 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 19 | 20317 | 21947 | 21490 | 21797 | 20801 | 22951 | 23862 | 24663 | 23909 | 22887 | 23388 | 25256 | 26278 | 26312 | 26616 | 25449 | 25531 | 27874 | 26949 | 28021
860 | 860 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 20 | 20110 | 21748 | 21495 | 21757 | 20451 | 22804 | 23917 | 24685 | 24144 | 22859 | 23269 | 25439 | 26834 | 26913 | 27311 | 25845 | 25778 | 28687 | 27901 | 28824
861 | 861 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 21 | 19742 | 21417 | 21367 | 21564 | 20258 | 22506 | 23827 | 24692 | 24348 | 23028 | 23404 | 25565 | 27329 | 27642 | 28038 | 26565 | 26306 | 29499 | 28982 | 29820
862 | 862 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 22 | 18966 | 20614 | 20624 | 20865 | 19699 | 21784 | 23250 | 24159 | 23807 | 22702 | 23011 | 25085 | 27122 | 27404 | 27883 | 26549 | 26133 | 29479 | 29553 | 29740
863 | 863 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 23 | 17964 | 19526 | 19596 | 19989 | 19142 | 20850 | 22425 | 23267 | 23018 | 22340 | 22600 | 24357 | 26500 | 26759 | 27420 | 26341 | 25843 | 28967 | 29352 | 29186
864 | 864 | 36 | 2 | 5 | Winter | 2 | 5 | Winter | 24 | 16828 | 18310 | 18464 | 18864 | 18391 | 19887 | 21498 | 22295 | 22147 | 21816 | 22149 | 23555 | 25751 | 25994 | 26697 | 25946 | 25507 | 28280 | 28698 | 28487
865 | 865 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 1 | 16396 | 17214 | 17923 | 18103 | 17933 | 19858 | 21661 | 21486 | 21852 | 21154 | 21720 | 24161 | 26116 | 25832 | 25814 | 24710 | 24963 | 28637 | 28521 | 28344
866 | 866 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 2 | 16005 | 16775 | 17483 | 17593 | 17510 | 19508 | 21250 | 21071 | 21426 | 20753 | 21437 | 23776 | 25708 | 25232 | 25201 | 24183 | 24572 | 28218 | 27894 | 27662
867 | 867 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 3 | 15772 | 16615 | 17288 | 17385 | 17346 | 19334 | 21160 | 20949 | 21265 | 20646 | 21413 | 23555 | 25516 | 24939 | 24915 | 23979 | 24447 | 27936 | 27543 | 27290
868 | 868 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 4 | 15713 | 16589 | 17220 | 17276 | 17265 | 19253 | 21043 | 20792 | 21020 | 20436 | 21235 | 23174 | 25023 | 24350 | 24331 | 23485 | 24013 | 27220 | 26799 | 26512
869 | 869 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 5 | 15768 | 16741 | 17304 | 17208 | 17096 | 19188 | 20953 | 20668 | 20845 | 20025 | 21028 | 22733 | 24442 | 23695 | 23587 | 22725 | 23501 | 26361 | 25944 | 25624
870 | 870 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 6 | 16196 | 17322 | 17795 | 17305 | 16999 | 19531 | 21320 | 20939 | 21019 | 19590 | 21186 | 22676 | 24316 | 23392 | 22936 | 21922 | 23306 | 25982 | 25386 | 25091
871 | 871 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 7 | 17423 | 18559 | 19198 | 17697 | 17313 | 20618 | 22462 | 22020 | 22140 | 19641 | 22191 | 23289 | 25143 | 24204 | 22714 | 21738 | 24048 | 26631 | 25840 | 25772
872 | 872 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 8 | 19068 | 19966 | 20781 | 18428 | 17920 | 22131 | 23852 | 23419 | 23641 | 20244 | 23538 | 24478 | 26238 | 25525 | 23153 | 22197 | 25351 | 27557 | 27021 | 27021
873 | 873 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 9 | 19468 | 20144 | 21102 | 19019 | 18535 | 22526 | 24025 | 23599 | 23950 | 20897 | 23855 | 24782 | 26248 | 25772 | 23542 | 22704 | 25630 | 27515 | 27118 | 27214
874 | 874 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 10 | 19430 | 19921 | 20865 | 19310 | 18975 | 22561 | 23796 | 23307 | 23708 | 21344 | 23794 | 24916 | 26116 | 25727 | 24002 | 23326 | 25608 | 27476 | 26903 | 27211
875 | 875 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 11 | 19377 | 19635 | 20452 | 18957 | 18914 | 22387 | 23177 | 22739 | 23046 | 21075 | 23356 | 24678 | 25446 | 25789 | 24116 | 23743 | 25208 | 26859 | 26397 | 27328
876 | 876 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 12 | 19447 | 19425 | 20111 | 18733 | 18927 | 22281 | 22682 | 22335 | 22539 | 20943 | 23034 | 24471 | 24900 | 25668 | 24108 | 23864 | 24898 | 26304 | 26118 | 27226
877 | 877 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 13 | 19352 | 19098 | 19695 | 18431 | 18805 | 22045 | 22244 | 21852 | 22006 | 20722 | 22678 | 24141 | 24357 | 25320 | 23865 | 23720 | 24518 | 25700 | 25672 | 26873
878 | 878 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 14 | 19178 | 18995 | 19490 | 18034 | 18628 | 21685 | 22040 | 21650 | 21713 | 20460 | 22351 | 23647 | 24063 | 25030 | 23377 | 23444 | 24138 | 25352 | 25369 | 26551
879 | 879 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 15 | 19268 | 18950 | 19450 | 17958 | 18657 | 21665 | 22122 | 21520 | 21611 | 20449 | 22323 | 23534 | 24075 | 24844 | 23175 | 23346 | 24072 | 25313 | 25144 | 26324
880 | 880 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 16 | 19519 | 19007 | 19654 | 18158 | 18921 | 22003 | 22492 | 21499 | 21744 | 20687 | 22576 | 23907 | 24317 | 24535 | 22919 | 23203 | 24255 | 25457 | 24905 | 25947
881 | 881 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 17 | 20111 | 19392 | 20378 | 18905 | 19584 | 22621 | 23379 | 22000 | 22414 | 21376 | 23171 | 24486 | 24966 | 24503 | 22858 | 23271 | 24887 | 25854 | 25291 | 25928
882 | 882 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 18 | 20919 | 20317 | 21189 | 19973 | 20467 | 23451 | 24124 | 23046 | 23430 | 22462 | 24056 | 25459 | 25624 | 25500 | 24156 | 24494 | 26067 | 26360 | 26741 | 26999
883 | 883 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 19 | 20984 | 20826 | 21451 | 20458 | 20897 | 23481 | 24328 | 23561 | 23873 | 22998 | 24611 | 25885 | 25961 | 26213 | 25108 | 25227 | 26946 | 26777 | 27831 | 27910
884 | 884 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 20 | 20682 | 20755 | 21363 | 20075 | 20600 | 23466 | 24276 | 23708 | 24037 | 22785 | 24711 | 26342 | 26566 | 26820 | 25447 | 25448 | 27275 | 27694 | 28614 | 28733
885 | 885 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 21 | 20344 | 20596 | 21140 | 19858 | 20375 | 23322 | 24196 | 23823 | 24163 | 22828 | 24714 | 26752 | 27189 | 27474 | 26101 | 25935 | 27641 | 28746 | 29604 | 29665
886 | 886 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 22 | 19584 | 19854 | 20418 | 19290 | 19760 | 22701 | 23591 | 23226 | 23652 | 22393 | 24161 | 26490 | 27241 | 27275 | 26051 | 25743 | 27300 | 29290 | 29522 | 29628
887 | 887 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 23 | 18565 | 18790 | 19501 | 18690 | 19119 | 21806 | 22614 | 22349 | 22915 | 21918 | 23437 | 25816 | 26715 | 26768 | 25815 | 25439 | 26698 | 29076 | 28958 | 29213
888 | 888 | 37 | 2 | 6 | Winter | 2 | 6 | Winter | 24 | 17426 | 17639 | 18340 | 17915 | 18423 | 20834 | 21608 | 21434 | 22042 | 21468 | 22682 | 25055 | 25941 | 26041 | 25422 | 25097 | 26009 | 28419 | 28263 | 28549
889 | 889 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 1 | 17296 | 17100 | 17607 | 17476 | 17935 | 20944 | 20791 | 21125 | 21391 | 21108 | 22212 | 25383 | 25545 | 25206 | 24233 | 24570 | 25780 | 28257 | 28130 | 27614
890 | 890 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 2 | 16907 | 16674 | 17093 | 17036 | 17635 | 20526 | 20377 | 20698 | 20946 | 20848 | 21767 | 24995 | 25005 | 24617 | 23726 | 24190 | 25227 | 27636 | 27455 | 26966
891 | 891 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 3 | 16754 | 16457 | 16872 | 16852 | 17583 | 20427 | 20258 | 20544 | 20806 | 20845 | 21611 | 24832 | 24758 | 24361 | 23539 | 24074 | 24940 | 27295 | 27091 | 26653
892 | 892 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 4 | 16719 | 16392 | 16766 | 16771 | 17590 | 20337 | 20144 | 20356 | 20574 | 20724 | 21260 | 24406 | 24254 | 23825 | 23078 | 23665 | 24276 | 26561 | 26316 | 25941
893 | 893 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 5 | 16811 | 16505 | 16727 | 16632 | 17735 | 20307 | 20095 | 20269 | 20255 | 20589 | 20973 | 23912 | 23706 | 23147 | 22374 | 23193 | 23570 | 25741 | 25447 | 25046
894 | 894 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 6 | 17392 | 17047 | 16853 | 16582 | 18259 | 20737 | 20455 | 20549 | 20032 | 20821 | 21069 | 23873 | 23438 | 22547 | 21628 | 23028 | 23280 | 25201 | 24921 | 24224
895 | 895 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 7 | 18744 | 18445 | 17277 | 16890 | 19449 | 21918 | 21584 | 21736 | 20239 | 21869 | 21751 | 24740 | 24075 | 22362 | 21451 | 23775 | 23699 | 25648 | 25587 | 23890
896 | 896 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 8 | 20148 | 20011 | 18020 | 17479 | 20841 | 23323 | 23008 | 23267 | 20931 | 23230 | 22620 | 25881 | 25341 | 22814 | 21908 | 25077 | 24337 | 26837 | 26839 | 24278
897 | 897 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 9 | 20283 | 20248 | 18586 | 18032 | 21136 | 23457 | 23158 | 23549 | 21422 | 23527 | 22701 | 25869 | 25444 | 23182 | 22363 | 25319 | 24323 | 26888 | 26988 | 24607
898 | 898 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 10 | 19858 | 19855 | 18691 | 18270 | 20850 | 23012 | 22654 | 23095 | 21498 | 23251 | 22604 | 25523 | 24992 | 23429 | 22771 | 25085 | 24311 | 26463 | 26773 | 24889
899 | 899 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 11 | 19495 | 19476 | 18399 | 18283 | 20603 | 22437 | 22117 | 22474 | 20891 | 22808 | 22273 | 24844 | 24431 | 23529 | 23193 | 24682 | 24066 | 25949 | 26892 | 25031
900 | 900 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 12 | 19075 | 19056 | 18103 | 18220 | 20300 | 21862 | 21620 | 21876 | 20386 | 22378 | 21774 | 24174 | 24018 | 23400 | 23199 | 24257 | 23577 | 25554 | 26661 | 24905
901 | 901 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 13 | 18794 | 18694 | 17853 | 18156 | 20079 | 21473 | 21185 | 21390 | 19996 | 22055 | 21409 | 23664 | 23618 | 23185 | 23091 | 23909 | 23193 | 25139 | 26336 | 24667
902 | 902 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 14 | 18708 | 18562 | 17520 | 18047 | 19889 | 21334 | 21052 | 21164 | 19564 | 21788 | 21032 | 23432 | 23411 | 22762 | 22874 | 23587 | 22749 | 24891 | 26070 | 24203
903 | 903 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 15 | 18832 | 18576 | 17502 | 18139 | 19961 | 21474 | 20987 | 21125 | 19496 | 21820 | 20896 | 23505 | 23288 | 22620 | 22835 | 23578 | 22553 | 24725 | 25901 | 24026
904 | 904 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 16 | 19360 | 18902 | 17825 | 18539 | 20387 | 21983 | 21113 | 21405 | 19798 | 22218 | 21344 | 23900 | 23267 | 22500 | 22839 | 23894 | 22949 | 24614 | 25661 | 23869
905 | 905 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 17 | 20317 | 19680 | 18625 | 19277 | 20946 | 22944 | 21692 | 22149 | 20650 | 22882 | 21786 | 24618 | 23724 | 22515 | 22973 | 24600 | 23486 | 25085 | 25714 | 23901
906 | 906 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 18 | 21011 | 20489 | 19670 | 20153 | 21742 | 23725 | 22720 | 23137 | 21895 | 23723 | 22556 | 25274 | 25065 | 23822 | 24204 | 25791 | 24333 | 26567 | 26826 | 25300
907 | 907 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 19 | 21195 | 20773 | 20142 | 20574 | 22151 | 23913 | 23220 | 23534 | 22436 | 24216 | 23287 | 25546 | 25923 | 24729 | 24906 | 26645 | 25447 | 27656 | 27732 | 26425
908 | 908 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 20 | 20938 | 20645 | 19727 | 20270 | 21994 | 23803 | 23308 | 23606 | 22302 | 24231 | 23894 | 26053 | 26428 | 24993 | 25082 | 26949 | 26485 | 28425 | 28545 | 26856
909 | 909 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 21 | 20592 | 20412 | 19504 | 20020 | 21673 | 23664 | 23357 | 23647 | 22402 | 24167 | 24203 | 26582 | 27083 | 25600 | 25526 | 27290 | 27258 | 29406 | 29479 | 27723
910 | 910 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 22 | 19764 | 19730 | 18935 | 19399 | 20907 | 23015 | 22711 | 23085 | 22034 | 23572 | 23903 | 26579 | 26801 | 25521 | 25304 | 26927 | 27249 | 29316 | 29444 | 27803
911 | 911 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 23 | 18638 | 18762 | 18293 | 18737 | 19955 | 21995 | 21780 | 22285 | 21568 | 22802 | 23137 | 25990 | 26095 | 25240 | 24973 | 26302 | 26666 | 28723 | 29010 | 27611
912 | 912 | 38 | 2 | 7 | Winter | 2 | 7 | Winter | 24 | 17430 | 17563 | 17476 | 18012 | 18979 | 20934 | 20805 | 21351 | 21010 | 22043 | 22470 | 25211 | 25343 | 24823 | 24630 | 25605 | 26060 | 28014 | 28341 | 27249
913 | 913 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 1 | 16294 | 16765 | 16974 | 17452 | 18059 | 20000 | 20408 | 20650 | 20386 | 21484 | 22398 | 24721 | 25126 | 23638 | 24066 | 25289 | 26106 | 27815 | 27352 | 25773
914 | 914 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 2 | 15848 | 16233 | 16500 | 17109 | 17608 | 19554 | 19953 | 20174 | 19965 | 21036 | 21952 | 24188 | 24524 | 23120 | 23678 | 24726 | 25555 | 27126 | 26684 | 25209
915 | 915 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 3 | 15704 | 15972 | 16291 | 17031 | 17470 | 19423 | 19793 | 20024 | 19851 | 20900 | 21771 | 23976 | 24266 | 22956 | 23586 | 24459 | 25232 | 26773 | 26379 | 24995
916 | 916 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 4 | 15693 | 15867 | 16220 | 17050 | 17394 | 19350 | 19661 | 19854 | 19699 | 20632 | 21421 | 23540 | 23735 | 22548 | 23219 | 23833 | 24541 | 26014 | 25676 | 24439
917 | 917 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 5 | 15875 | 15863 | 16112 | 17230 | 17460 | 19369 | 19657 | 19626 | 19375 | 20439 | 21048 | 23087 | 23182 | 21901 | 22799 | 23180 | 23817 | 25182 | 24809 | 23613
918 | 918 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 6 | 16493 | 15987 | 16105 | 17798 | 17933 | 19808 | 20034 | 19511 | 19036 | 20627 | 21090 | 22946 | 22971 | 21219 | 22683 | 22940 | 23505 | 24699 | 24012 | 22758
919 | 919 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 7 | 17726 | 16417 | 16442 | 19004 | 19090 | 20963 | 21287 | 19801 | 19123 | 21384 | 21874 | 23654 | 23828 | 21075 | 23456 | 23388 | 23920 | 25370 | 23681 | 22499
920 | 920 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 8 | 19102 | 17165 | 17039 | 20383 | 20251 | 22383 | 22845 | 20526 | 19740 | 22304 | 22984 | 24955 | 25170 | 21544 | 24766 | 24066 | 24773 | 26630 | 24082 | 22938
921 | 921 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 9 | 19230 | 17764 | 17620 | 20687 | 20399 | 22545 | 23161 | 21061 | 20381 | 22433 | 22958 | 25093 | 25406 | 22036 | 25042 | 24074 | 24601 | 26807 | 24420 | 23399
922 | 922 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 10 | 18887 | 17982 | 17954 | 20491 | 20274 | 22119 | 22781 | 21212 | 20692 | 22402 | 22690 | 24700 | 25222 | 22513 | 24889 | 24134 | 24347 | 26670 | 24780 | 23911
923 | 923 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 11 | 18668 | 17789 | 18081 | 20353 | 20086 | 21684 | 22251 | 20717 | 20531 | 22127 | 22193 | 24159 | 25294 | 22956 | 24502 | 23900 | 23778 | 26794 | 24941 | 24376
924 | 924 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 12 | 18434 | 17608 | 18147 | 20190 | 19816 | 21350 | 21799 | 20387 | 20457 | 21777 | 21867 | 23764 | 25067 | 22984 | 24092 | 23431 | 23333 | 26586 | 24838 | 24398
925 | 925 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 13 | 18136 | 17353 | 18099 | 19991 | 19548 | 20952 | 21349 | 20043 | 20309 | 21453 | 21539 | 23306 | 24695 | 22819 | 23684 | 22986 | 22943 | 26198 | 24544 | 24210
926 | 926 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 14 | 18057 | 17006 | 17974 | 19788 | 19263 | 20810 | 21111 | 19601 | 20090 | 21071 | 21249 | 23073 | 24425 | 22571 | 23328 | 22510 | 22603 | 25895 | 24044 | 23923
927 | 927 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 15 | 18018 | 16931 | 18009 | 19808 | 19156 | 20705 | 21029 | 19488 | 20089 | 20894 | 21230 | 22895 | 24235 | 22470 | 23256 | 22253 | 22539 | 25663 | 23807 | 23799
928 | 928 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 16 | 18225 | 17256 | 18393 | 20220 | 19549 | 20833 | 21303 | 19777 | 20450 | 21322 | 21449 | 22907 | 24083 | 22489 | 23590 | 22665 | 22710 | 25433 | 23649 | 23786
929 | 929 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 17 | 18602 | 17970 | 19030 | 20672 | 19961 | 21297 | 21908 | 20478 | 21061 | 21594 | 21914 | 23351 | 24114 | 22607 | 24278 | 23193 | 23333 | 25473 | 23659 | 23929
930 | 930 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 18 | 19497 | 18927 | 19804 | 21382 | 20637 | 22242 | 22785 | 21586 | 22044 | 22228 | 22785 | 24633 | 25106 | 23829 | 25455 | 24033 | 24587 | 26591 | 25064 | 25219
931 | 931 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 19 | 20004 | 19360 | 20196 | 21759 | 21061 | 22714 | 23131 | 22048 | 22508 | 22841 | 23433 | 25408 | 25746 | 24462 | 26262 | 25089 | 25729 | 27473 | 26162 | 26039
932 | 932 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 20 | 19904 | 18947 | 19875 | 21578 | 21234 | 22758 | 23139 | 21835 | 22222 | 23328 | 23963 | 25832 | 26282 | 24602 | 26527 | 26088 | 26597 | 28284 | 26602 | 26296
933 | 933 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 21 | 19707 | 18678 | 19578 | 21216 | 21059 | 22716 | 23075 | 21813 | 22167 | 23526 | 24360 | 26349 | 26830 | 24962 | 26797 | 26789 | 27518 | 29172 | 27435 | 26858
934 | 934 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 22 | 18936 | 18115 | 18935 | 20440 | 20411 | 22021 | 22441 | 21375 | 21673 | 23156 | 24066 | 25990 | 26573 | 24696 | 26397 | 26739 | 27547 | 29111 | 27499 | 26716
935 | 935 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 23 | 17861 | 17447 | 18264 | 19483 | 19435 | 21061 | 21616 | 20878 | 21158 | 22368 | 23301 | 25264 | 26034 | 24358 | 25768 | 26159 | 26926 | 28678 | 27318 | 26442
936 | 936 | 39 | 2 | 8 | Winter | 2 | 8 | Winter | 24 | 16718 | 16605 | 17487 | 18470 | 18497 | 20043 | 20624 | 20259 | 20674 | 21676 | 22557 | 24476 | 25288 | 24003 | 25060 | 25540 | 26273 | 27993 | 26950 | 26135
937 | 937 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 1 | 16158 | 16121 | 16896 | 17534 | 18092 | 19639 | 19940 | 19736 | 20296 | 21628 | 22327 | 24258 | 24421 | 23430 | 24700 | 25564 | 26120 | 27007 | 25506 | 25520
938 | 938 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 2 | 15732 | 15656 | 16546 | 17070 | 17640 | 19173 | 19445 | 19299 | 20003 | 21190 | 21835 | 23706 | 23854 | 23078 | 24173 | 25043 | 25525 | 26356 | 24963 | 25124
939 | 939 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 3 | 15524 | 15426 | 16456 | 16929 | 17494 | 19020 | 19305 | 19196 | 20013 | 21058 | 21640 | 23476 | 23631 | 23001 | 23922 | 24730 | 25191 | 26056 | 24749 | 24992
940 | 940 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 4 | 15467 | 15315 | 16464 | 16855 | 17408 | 18908 | 19163 | 19074 | 19944 | 20775 | 21240 | 23016 | 23134 | 22659 | 23323 | 24063 | 24446 | 25359 | 24176 | 24517
941 | 941 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 5 | 15609 | 15207 | 16663 | 16956 | 17444 | 18957 | 19001 | 18812 | 19889 | 20489 | 20769 | 22545 | 22544 | 22290 | 22721 | 23384 | 23551 | 24519 | 23367 | 23985
942 | 942 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 6 | 16188 | 15221 | 17282 | 17478 | 17935 | 19400 | 18979 | 18555 | 20226 | 20635 | 20674 | 22438 | 22032 | 22234 | 22534 | 23119 | 23002 | 23743 | 22507 | 23772
943 | 943 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 7 | 17584 | 15571 | 18504 | 18677 | 19050 | 20684 | 19329 | 18710 | 21311 | 21488 | 21220 | 23376 | 21904 | 23024 | 23031 | 23574 | 23238 | 23429 | 22263 | 24475
944 | 944 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 8 | 19120 | 16172 | 19863 | 19850 | 20334 | 22222 | 20055 | 19335 | 22672 | 22614 | 22251 | 24753 | 22381 | 24348 | 23727 | 24457 | 24110 | 23825 | 22694 | 25758
945 | 945 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 9 | 19347 | 16765 | 20161 | 19987 | 20472 | 22536 | 20599 | 20004 | 22994 | 22618 | 22373 | 24987 | 22784 | 24615 | 23738 | 24289 | 24080 | 24155 | 23153 | 25980
946 | 946 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 10 | 19162 | 17249 | 20096 | 19976 | 20321 | 22306 | 20915 | 20493 | 22972 | 22522 | 22365 | 24854 | 23160 | 24508 | 23845 | 24079 | 24162 | 24572 | 23732 | 25906
947 | 947 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 11 | 19076 | 17675 | 20331 | 20177 | 20394 | 22270 | 20966 | 20921 | 23235 | 22647 | 22361 | 24899 | 23256 | 24109 | 23585 | 23487 | 24204 | 24710 | 24177 | 25541
948 | 948 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 12 | 18836 | 17859 | 20303 | 20064 | 20290 | 22001 | 20837 | 21069 | 23190 | 22556 | 22245 | 24658 | 23135 | 23678 | 23096 | 23021 | 24113 | 24582 | 24183 | 25112
949 | 949 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 13 | 18561 | 17921 | 20232 | 19931 | 20145 | 21700 | 20651 | 21085 | 23077 | 22398 | 22089 | 24340 | 22925 | 23339 | 22712 | 22697 | 23930 | 24345 | 24047 | 24749
950 | 950 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 14 | 18361 | 17768 | 19999 | 19633 | 19893 | 21445 | 20197 | 20855 | 22779 | 22101 | 21853 | 24017 | 22402 | 22928 | 22179 | 22298 | 23640 | 23790 | 23699 | 24304
951 | 951 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 15 | 18342 | 17823 | 20040 | 19557 | 19919 | 21381 | 20096 | 20859 | 22766 | 22085 | 21811 | 23878 | 22240 | 22902 | 21969 | 22277 | 23548 | 23597 | 23615 | 24256
952 | 952 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 16 | 18590 | 18115 | 20349 | 19804 | 20049 | 21490 | 20189 | 20998 | 22908 | 22061 | 21850 | 23794 | 22188 | 23297 | 22437 | 22501 | 23473 | 23490 | 23641 | 24620
953 | 953 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 17 | 19003 | 18451 | 20461 | 19830 | 20090 | 21604 | 20336 | 21004 | 22764 | 21837 | 21976 | 23803 | 22166 | 23976 | 22946 | 23100 | 23630 | 23492 | 23768 | 25317
954 | 954 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 18 | 19691 | 19125 | 21038 | 20431 | 20799 | 22377 | 21312 | 21838 | 23368 | 22529 | 22759 | 24713 | 23412 | 25079 | 23747 | 24307 | 24632 | 24847 | 25023 | 26518
955 | 955 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 19 | 19910 | 19457 | 21368 | 20783 | 21247 | 22635 | 21655 | 22170 | 23677 | 22979 | 23319 | 25265 | 24232 | 25830 | 24744 | 25401 | 25508 | 25929 | 25824 | 27428
956 | 956 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 20 | 19729 | 19097 | 21149 | 20886 | 21246 | 22588 | 21368 | 21804 | 23594 | 23385 | 23690 | 25690 | 24412 | 26030 | 25656 | 26203 | 26424 | 26342 | 26057 | 27764
957 | 957 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 21 | 19457 | 18802 | 20762 | 20669 | 21120 | 22458 | 21270 | 21685 | 23413 | 23674 | 23995 | 26132 | 24905 | 26239 | 26297 | 27065 | 27231 | 27153 | 26620 | 28142
958 | 958 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 22 | 18752 | 18160 | 19944 | 19972 | 20449 | 21768 | 20761 | 21132 | 22742 | 23299 | 23772 | 25787 | 24744 | 25778 | 26197 | 27038 | 27338 | 27179 | 26461 | 27799
959 | 959 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 23 | 17796 | 17465 | 18987 | 18995 | 19477 | 20932 | 20256 | 20608 | 21988 | 22532 | 23157 | 25216 | 24453 | 25132 | 25603 | 26409 | 26883 | 26993 | 26191 | 27228
960 | 960 | 40 | 2 | 9 | Winter | 2 | 9 | Winter | 24 | 16607 | 16672 | 17952 | 18045 | 18493 | 19922 | 19625 | 20110 | 21233 | 21823 | 22556 | 24440 | 24010 | 24413 | 24954 | 25746 | 26371 | 26607 | 25865 | 26556
961 | 961 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 1 | 15820 | 16013 | 16962 | 17534 | 17877 | 19165 | 19082 | 19616 | 20576 | 21520 | 21923 | 23614 | 22945 | 24049 | 24972 | 25605 | 25752 | 25202 | 25254 | 26339
962 | 962 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 2 | 15318 | 15665 | 16507 | 17079 | 17444 | 18669 | 18640 | 19320 | 20129 | 21060 | 21402 | 23070 | 22470 | 23542 | 24474 | 25026 | 25120 | 24669 | 24868 | 25774
963 | 963 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 3 | 15051 | 15542 | 16346 | 16909 | 17282 | 18506 | 18519 | 19318 | 20016 | 20890 | 21169 | 22868 | 22314 | 23310 | 24172 | 24695 | 24724 | 24450 | 24731 | 25469
964 | 964 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 4 | 14940 | 15539 | 16284 | 16840 | 17176 | 18389 | 18428 | 19289 | 19804 | 20573 | 20725 | 22446 | 21942 | 22763 | 23558 | 23990 | 23912 | 23907 | 24265 | 24746
965 | 965 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 5 | 14942 | 15756 | 16400 | 16901 | 17129 | 18268 | 18210 | 19287 | 19684 | 20184 | 20293 | 21930 | 21345 | 22211 | 22924 | 23131 | 23053 | 23101 | 23727 | 23980
966 | 966 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 6 | 15067 | 16407 | 16933 | 17428 | 17560 | 18294 | 18016 | 19699 | 19962 | 20168 | 20255 | 21508 | 20704 | 22078 | 22708 | 22610 | 22514 | 22248 | 23514 | 23635
967 | 967 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 7 | 15539 | 17684 | 18216 | 18614 | 18639 | 18716 | 18261 | 20883 | 20836 | 20842 | 21025 | 21488 | 20645 | 22655 | 23241 | 22923 | 22918 | 22049 | 24250 | 24039
968 | 968 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 8 | 16276 | 19037 | 19418 | 19914 | 19830 | 19443 | 18901 | 22274 | 21773 | 21915 | 22130 | 21995 | 21138 | 23371 | 24145 | 23807 | 23945 | 22477 | 25532 | 24658
969 | 969 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 9 | 16907 | 19371 | 19595 | 20094 | 20059 | 20011 | 19607 | 22643 | 21954 | 22096 | 22415 | 22450 | 21683 | 23428 | 24028 | 23827 | 24204 | 22975 | 25795 | 24670
970 | 970 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 10 | 17412 | 19485 | 19725 | 20099 | 20121 | 20476 | 20244 | 22774 | 22249 | 22239 | 22598 | 22975 | 22372 | 23681 | 23977 | 24064 | 24352 | 23700 | 25870 | 24978
971 | 971 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 11 | 17534 | 19764 | 19957 | 20218 | 20085 | 20568 | 20712 | 23078 | 22635 | 22268 | 22651 | 23109 | 22825 | 23468 | 23426 | 24138 | 23999 | 24181 | 25545 | 24817
972 | 972 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 12 | 17556 | 19853 | 19957 | 20224 | 20052 | 20549 | 20967 | 23131 | 22619 | 22264 | 22569 | 23095 | 22943 | 23070 | 23056 | 24154 | 23663 | 24303 | 25228 | 24424
973 | 973 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 13 | 17419 | 19800 | 19837 | 20091 | 19904 | 20378 | 20997 | 23030 | 22472 | 22103 | 22372 | 22894 | 22839 | 22697 | 22742 | 23979 | 23259 | 24178 | 24875 | 24037
974 | 974 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 14 | 17046 | 19605 | 19561 | 19853 | 19736 | 19942 | 20784 | 22748 | 22086 | 21883 | 22089 | 22389 | 22541 | 22181 | 22355 | 23700 | 22766 | 23841 | 24440 | 23484
975 | 975 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 15 | 16976 | 19605 | 19475 | 19862 | 19732 | 19827 | 20774 | 22720 | 21896 | 21826 | 21879 | 22214 | 22462 | 21957 | 22315 | 23590 | 22555 | 23736 | 24369 | 23225
976 | 976 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 16 | 17001 | 19681 | 19465 | 19796 | 19735 | 19729 | 20715 | 22666 | 21857 | 21655 | 21631 | 21958 | 22306 | 22218 | 22325 | 23297 | 22575 | 23538 | 24508 | 23435
977 | 977 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 17 | 17313 | 19728 | 19451 | 19797 | 19995 | 19831 | 20662 | 22466 | 21376 | 21656 | 21502 | 21824 | 22305 | 22618 | 22818 | 23333 | 23217 | 23554 | 25104 | 23849
978 | 978 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 18 | 18146 | 20261 | 20054 | 20490 | 20542 | 20793 | 21456 | 23005 | 21849 | 22372 | 22197 | 22988 | 23443 | 23372 | 23971 | 24312 | 24235 | 24785 | 26270 | 24657
979 | 979 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 19 | 18543 | 20623 | 20467 | 20983 | 20949 | 21178 | 21818 | 23336 | 22352 | 22880 | 22696 | 23769 | 24061 | 24358 | 25056 | 25191 | 25135 | 25620 | 27211 | 25836
980 | 980 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 20 | 18101 | 20374 | 20535 | 20939 | 20955 | 20860 | 21420 | 23201 | 22725 | 23138 | 22892 | 23867 | 24114 | 25206 | 25804 | 26051 | 25700 | 25856 | 27545 | 26931
981 | 981 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 21 | 17815 | 19993 | 20283 | 20760 | 20751 | 20703 | 21244 | 22944 | 22813 | 23334 | 23219 | 24256 | 24409 | 25766 | 26593 | 26813 | 26535 | 26396 | 27918 | 27725
982 | 982 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 22 | 17231 | 19156 | 19553 | 20052 | 20176 | 20150 | 20647 | 22218 | 22362 | 23051 | 23005 | 24022 | 24085 | 25621 | 26519 | 26887 | 26635 | 26221 | 27567 | 27734
983 | 983 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 23 | 16562 | 18168 | 18544 | 19052 | 19282 | 19607 | 20081 | 21424 | 21560 | 22385 | 22380 | 23695 | 23714 | 24985 | 25865 | 26411 | 26160 | 25936 | 26990 | 27202
984 | 984 | 41 | 2 | 10 | Winter | 2 | 10 | Winter | 24 | 15737 | 17101 | 17541 | 18024 | 18363 | 18922 | 19527 | 20611 | 20870 | 21774 | 21746 | 23236 | 23339 | 24328 | 25190 | 25888 | 25582 | 25600 | 26317 | 26601
985 | 985 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 1 | 15418 | 16257 | 17149 | 17515 | 17653 | 18567 | 19175 | 20004 | 20850 | 21274 | 21064 | 22443 | 22964 | 24499 | 25211 | 25425 | 24754 | 25174 | 26250 | 26859
986 | 986 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 2 | 14963 | 15818 | 16691 | 17070 | 17180 | 18113 | 18871 | 19560 | 20432 | 20784 | 20530 | 21978 | 22626 | 24010 | 24637 | 24799 | 24090 | 24781 | 25681 | 26312
987 | 987 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 3 | 14715 | 15625 | 16503 | 16894 | 16993 | 17977 | 18862 | 19452 | 20311 | 20597 | 20240 | 21833 | 22545 | 23720 | 24316 | 24402 | 23637 | 24636 | 25372 | 25953
988 | 988 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 4 | 14599 | 15568 | 16443 | 16804 | 16853 | 17898 | 18857 | 19288 | 20091 | 20231 | 19761 | 21513 | 22257 | 23160 | 23661 | 23634 | 22825 | 24186 | 24668 | 25215
989 | 989 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 5 | 14493 | 15712 | 16535 | 16804 | 16906 | 17726 | 18912 | 19250 | 19889 | 19901 | 19210 | 20989 | 21941 | 22596 | 22866 | 22829 | 21828 | 23671 | 23925 | 24423
990 | 990 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 6 | 14533 | 16313 | 17093 | 17307 | 17382 | 17590 | 19397 | 19637 | 20130 | 19983 | 18677 | 20444 | 21941 | 22460 | 22419 | 22352 | 20856 | 23478 | 23619 | 24053
991 | 991 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 7 | 14902 | 17614 | 18267 | 18415 | 18426 | 17836 | 20616 | 20563 | 21067 | 20804 | 18719 | 20419 | 22786 | 23019 | 22749 | 22758 | 20639 | 24202 | 24005 | 24412
992 | 992 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 8 | 15518 | 18866 | 19578 | 19626 | 19667 | 18481 | 22025 | 21556 | 22246 | 21949 | 19567 | 20942 | 24135 | 23950 | 23656 | 23800 | 21347 | 25490 | 24612 | 25226
993 | 993 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 9 | 16155 | 19031 | 19786 | 19878 | 20032 | 19192 | 22423 | 21766 | 22322 | 22265 | 20239 | 21518 | 24468 | 23871 | 23702 | 24081 | 21945 | 25779 | 24629 | 25070
994 | 994 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 10 | 16842 | 19150 | 19823 | 19953 | 20159 | 19844 | 22572 | 22064 | 22409 | 22458 | 20785 | 22224 | 24540 | 23839 | 23953 | 24245 | 22553 | 25881 | 24953 | 25077
995 | 995 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 11 | 17294 | 19338 | 19911 | 19880 | 20096 | 20260 | 22809 | 22388 | 22516 | 22446 | 21007 | 22662 | 24164 | 23272 | 24015 | 23877 | 22892 | 25534 | 24789 | 24545
996 | 996 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 12 | 17428 | 19186 | 19746 | 19662 | 19811 | 20311 | 22645 | 22142 | 22282 | 22120 | 20931 | 22678 | 23735 | 22799 | 23918 | 23427 | 22970 | 25109 | 24286 | 24072
997 | 997 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 13 | 17347 | 18912 | 19450 | 19343 | 19454 | 20157 | 22349 | 21792 | 21918 | 21708 | 20683 | 22465 | 23286 | 22372 | 23630 | 22910 | 22810 | 24643 | 23792 | 23635
998 | 998 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 14 | 17268 | 18719 | 19275 | 19238 | 19290 | 20008 | 22127 | 21471 | 21683 | 21483 | 20381 | 22244 | 22953 | 22057 | 23422 | 22488 | 22476 | 24275 | 23302 | 23288
999 | 999 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 15 | 17295 | 18650 | 19282 | 19233 | 19151 | 19998 | 22094 | 21279 | 21636 | 21268 | 20218 | 22176 | 22910 | 22025 | 23319 | 22285 | 22281 | 24207 | 23048 | 23234
1000 | 1000 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 16 | 17442 | 18728 | 19317 | 19345 | 19194 | 20052 | 22149 | 21322 | 21504 | 21132 | 20150 | 22100 | 23148 | 22111 | 23095 | 22380 | 22083 | 24398 | 23327 | 23269
1001 | 1001 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 17 | 17748 | 18868 | 19472 | 19767 | 19349 | 20186 | 22126 | 21047 | 21360 | 21157 | 20189 | 22100 | 23716 | 22606 | 23149 | 23028 | 22078 | 24991 | 23752 | 23799
1002 | 1002 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 18 | 18394 | 19496 | 20216 | 20340 | 19989 | 21049 | 22718 | 21588 | 22080 | 21868 | 21083 | 23162 | 24759 | 23710 | 24090 | 24013 | 23016 | 26155 | 24540 | 25028
1003 | 1003 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 19 | 18740 | 19905 | 20723 | 20743 | 20287 | 21419 | 23037 | 22064 | 22529 | 22286 | 21523 | 23701 | 25482 | 24716 | 24898 | 24861 | 23816 | 27075 | 25697 | 26230
1004 | 1004 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 20 | 18383 | 19932 | 20651 | 20706 | 20091 | 21020 | 22876 | 22380 | 22862 | 22391 | 21712 | 23694 | 25622 | 25401 | 25702 | 25373 | 24391 | 27406 | 26781 | 27133
1005 | 1005 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 21 | 18108 | 19683 | 20465 | 20489 | 19930 | 20835 | 22619 | 22404 | 23074 | 22634 | 22057 | 23941 | 25800 | 26139 | 26433 | 26191 | 25228 | 27804 | 27591 | 28161
1006 | 1006 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 22 | 17466 | 18922 | 19736 | 19892 | 19397 | 20218 | 21868 | 21887 | 22636 | 22357 | 21954 | 23573 | 25308 | 26021 | 26470 | 26263 | 25415 | 27461 | 27589 | 28229
1007 | 1007 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 23 | 16762 | 17932 | 18730 | 18988 | 18545 | 19638 | 21046 | 21058 | 21838 | 21720 | 21659 | 23187 | 24655 | 25355 | 25983 | 25790 | 25306 | 26883 | 27068 | 27652
1008 | 1008 | 42 | 2 | 11 | Winter | 2 | 11 | Winter | 24 | 15940 | 16853 | 17645 | 18019 | 17631 | 19021 | 20169 | 20312 | 21068 | 21060 | 21208 | 22778 | 23910 | 24656 | 25434 | 25192 | 24929 | 26182 | 26460 | 27012
1009 | 1009 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 1 | 15398 | 16373 | 17026 | 17205 | 16893 | 18558 | 19384 | 20149 | 20781 | 20321 | 20663 | 22375 | 23590 | 24621 | 24937 | 24334 | 23927 | 26039 | 26681 | 27045
1010 | 1010 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 2 | 15061 | 15934 | 16600 | 16745 | 16428 | 18272 | 18969 | 19766 | 20378 | 19854 | 20261 | 22059 | 23095 | 24070 | 24325 | 23677 | 23419 | 25477 | 26144 | 26425
1011 | 1011 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 3 | 14940 | 15745 | 16423 | 16555 | 16179 | 18254 | 18866 | 19651 | 20232 | 19601 | 20097 | 22020 | 22895 | 23795 | 23970 | 23270 | 23114 | 25193 | 25810 | 26070
1012 | 1012 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 4 | 14925 | 15671 | 16334 | 16421 | 15969 | 18250 | 18726 | 19469 | 19965 | 19183 | 19755 | 21778 | 22410 | 23191 | 23246 | 22487 | 22508 | 24498 | 25080 | 25273
1013 | 1013 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 5 | 15152 | 15785 | 16357 | 16504 | 15775 | 18335 | 18745 | 19338 | 19667 | 18712 | 19259 | 21520 | 21931 | 22456 | 22495 | 21529 | 21728 | 23770 | 24295 | 24306
1014 | 1014 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 6 | 15806 | 16333 | 16886 | 17003 | 15650 | 18843 | 19189 | 19642 | 19747 | 18266 | 18736 | 21582 | 21883 | 22064 | 22049 | 20604 | 20912 | 23476 | 23926 | 23676
1015 | 1015 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 7 | 17061 | 17543 | 18037 | 18073 | 16071 | 20078 | 20183 | 20635 | 20470 | 18365 | 18721 | 22467 | 22468 | 22430 | 22489 | 20391 | 20611 | 23858 | 24290 | 23876
1016 | 1016 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 8 | 18416 | 18876 | 19268 | 19323 | 17120 | 21490 | 21241 | 21869 | 21605 | 19274 | 19335 | 23834 | 23226 | 23365 | 23550 | 21106 | 21063 | 24484 | 25105 | 24716
1017 | 1017 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 9 | 18735 | 19071 | 19499 | 19654 | 17784 | 21836 | 21420 | 21935 | 21783 | 19923 | 19952 | 24164 | 23273 | 23382 | 23815 | 21662 | 21604 | 24475 | 24912 | 24685
1018 | 1018 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 10 | 18817 | 19045 | 19483 | 19685 | 18146 | 21859 | 21569 | 21879 | 21794 | 20308 | 20475 | 24210 | 23515 | 23602 | 23955 | 22240 | 22157 | 24773 | 24899 | 24967
1019 | 1019 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 11 | 18816 | 18910 | 19122 | 19265 | 17922 | 21638 | 21370 | 21435 | 21164 | 19905 | 20388 | 23851 | 23299 | 23680 | 23594 | 22604 | 22224 | 24616 | 24389 | 25078
1020 | 1020 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 12 | 18687 | 18666 | 18830 | 18891 | 17734 | 21341 | 20958 | 21019 | 20704 | 19601 | 20274 | 23459 | 22839 | 23626 | 23182 | 22715 | 22110 | 24157 | 23953 | 25029
1021 | 1021 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 13 | 18569 | 18459 | 18600 | 18617 | 17590 | 21111 | 20662 | 20699 | 20366 | 19377 | 20136 | 23144 | 22484 | 23469 | 22802 | 22688 | 21925 | 23789 | 23649 | 24865
1022 | 1022 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 14 | 18435 | 18298 | 18492 | 18443 | 17325 | 20874 | 20325 | 20439 | 20168 | 19045 | 19843 | 22828 | 22049 | 23275 | 22392 | 22366 | 21489 | 23316 | 23311 | 24638
1023 | 1023 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 15 | 18378 | 18249 | 18450 | 18276 | 17192 | 20819 | 20118 | 20374 | 20082 | 18869 | 19819 | 22728 | 21771 | 23115 | 22130 | 22112 | 21457 | 23000 | 23193 | 24438
1024 | 1024 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 16 | 18568 | 18353 | 18660 | 18443 | 17423 | 21048 | 20328 | 20464 | 20245 | 19054 | 20100 | 22906 | 22030 | 22839 | 22158 | 21853 | 21766 | 23206 | 23163 | 24104
1025 | 1025 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 17 | 18950 | 18818 | 19448 | 19019 | 18169 | 21557 | 20629 | 20941 | 21065 | 19744 | 20754 | 23464 | 22436 | 22880 | 22796 | 21844 | 22506 | 23628 | 23672 | 24160
1026 | 1026 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 18 | 19575 | 19650 | 20060 | 19730 | 18977 | 22264 | 21297 | 21780 | 21965 | 20704 | 21902 | 24487 | 23176 | 23831 | 23800 | 22799 | 23835 | 24458 | 24934 | 25207
1027 | 1027 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 19 | 19942 | 20181 | 20501 | 20058 | 19196 | 22646 | 21818 | 22266 | 22501 | 21134 | 22480 | 25126 | 24064 | 24561 | 24570 | 23533 | 24727 | 25580 | 26096 | 26137
1028 | 1028 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 20 | 19686 | 20061 | 20435 | 19833 | 19021 | 22473 | 22086 | 22523 | 22671 | 21236 | 22641 | 25208 | 24837 | 25293 | 25034 | 24092 | 25084 | 26645 | 26997 | 27119
1029 | 1029 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 21 | 19349 | 19837 | 20177 | 19635 | 18866 | 22169 | 22033 | 22634 | 22800 | 21462 | 22863 | 25307 | 25343 | 25943 | 25794 | 24866 | 25713 | 27438 | 28009 | 28019
1030 | 1030 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 22 | 18529 | 19091 | 19547 | 19089 | 18446 | 21397 | 21460 | 22134 | 22457 | 21293 | 22556 | 24772 | 25134 | 25933 | 25834 | 25018 | 25631 | 27421 | 28072 | 28185
1031 | 1031 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 23 | 17520 | 18053 | 18603 | 18198 | 17917 | 20517 | 20560 | 21265 | 21734 | 20933 | 22134 | 24081 | 24501 | 25417 | 25330 | 24888 | 25345 | 26885 | 27489 | 27773
1032 | 1032 | 43 | 2 | 12 | Winter | 2 | 12 | Winter | 24 | 16424 | 16923 | 17573 | 17225 | 17174 | 19566 | 19726 | 20403 | 21028 | 20436 | 21694 | 23338 | 23844 | 24872 | 24736 | 24518 | 24976 | 26285 | 26863 | 27295
1033 | 1033 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 1 | 15513 | 16250 | 16706 | 16445 | 16918 | 18737 | 19491 | 20069 | 20432 | 20033 | 21392 | 22911 | 23890 | 24308 | 23822 | 23524 | 24516 | 26421 | 26837 | 26759
1034 | 1034 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 2 | 15115 | 15832 | 16255 | 15978 | 16513 | 18324 | 19113 | 19669 | 20008 | 19663 | 21070 | 22455 | 23430 | 23731 | 23197 | 23037 | 24113 | 25889 | 26230 | 26107
1035 | 1035 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 3 | 14939 | 15635 | 16058 | 15721 | 16348 | 18215 | 19000 | 19533 | 19839 | 19529 | 20990 | 22285 | 23192 | 23407 | 22808 | 22748 | 23915 | 25571 | 25889 | 25699
1036 | 1036 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 4 | 14881 | 15549 | 15938 | 15526 | 16225 | 18103 | 18860 | 19322 | 19529 | 19250 | 20792 | 21864 | 22686 | 22738 | 22071 | 22167 | 23460 | 24854 | 25102 | 24830
1037 | 1037 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 5 | 15023 | 15596 | 16045 | 15359 | 16060 | 18165 | 18791 | 19101 | 19274 | 18818 | 20493 | 21454 | 22184 | 22042 | 21160 | 21417 | 22895 | 24088 | 24137 | 23898
1038 | 1038 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 6 | 15594 | 16117 | 16570 | 15259 | 15906 | 18637 | 19167 | 19270 | 19405 | 18353 | 20540 | 21457 | 22105 | 21645 | 20271 | 20617 | 22681 | 23740 | 23500 | 23268
1039 | 1039 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 7 | 16917 | 17336 | 17674 | 15708 | 16130 | 19696 | 20216 | 20083 | 20306 | 18398 | 21525 | 22117 | 22698 | 22128 | 20096 | 20336 | 23457 | 24117 | 23704 | 23610
1040 | 1040 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 8 | 18198 | 18578 | 18913 | 16743 | 16817 | 20765 | 21469 | 21248 | 21488 | 19032 | 22868 | 22918 | 23649 | 23192 | 20816 | 20784 | 24653 | 24921 | 24525 | 24602
1041 | 1041 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 9 | 18306 | 18799 | 19235 | 17391 | 17517 | 20931 | 21527 | 21438 | 21777 | 19665 | 23209 | 22988 | 23540 | 23461 | 21367 | 21318 | 24860 | 24721 | 24485 | 24821
1042 | 1042 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 10 | 18259 | 18722 | 19203 | 17689 | 17946 | 20992 | 21387 | 21370 | 21744 | 20108 | 23198 | 23145 | 23404 | 23516 | 21863 | 21793 | 24863 | 24625 | 24687 | 24936
1043 | 1043 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 11 | 18159 | 18403 | 18833 | 17511 | 18033 | 20803 | 20975 | 20772 | 21109 | 20002 | 22774 | 22899 | 22848 | 23132 | 22206 | 21843 | 24354 | 24107 | 24784 | 24610
1044 | 1044 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 12 | 17909 | 18098 | 18459 | 17307 | 17996 | 20375 | 20532 | 20292 | 20534 | 19836 | 22345 | 22381 | 22358 | 22672 | 22265 | 21680 | 23804 | 23619 | 24685 | 24139
1045 | 1045 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 13 | 17695 | 17867 | 18178 | 17155 | 17920 | 20069 | 20201 | 19935 | 20127 | 19670 | 22017 | 21999 | 22028 | 22259 | 22211 | 21467 | 23403 | 23288 | 24491 | 23714
1046 | 1046 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 14 | 17401 | 17656 | 17909 | 16793 | 17598 | 19646 | 19847 | 19644 | 19769 | 19278 | 21723 | 21471 | 21626 | 21756 | 21788 | 20930 | 23063 | 22847 | 24159 | 23181
1047 | 1047 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 15 | 17306 | 17616 | 17752 | 16669 | 17615 | 19458 | 19792 | 19570 | 19547 | 19263 | 21623 | 21208 | 21537 | 21508 | 21543 | 20905 | 22916 | 22734 | 23972 | 22892
1048 | 1048 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 16 | 17534 | 17920 | 18031 | 17007 | 18029 | 19773 | 20001 | 19852 | 19757 | 19664 | 21773 | 21563 | 21673 | 21661 | 21405 | 21327 | 23023 | 22818 | 23744 | 22978
1049 | 1049 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 17 | 18060 | 18789 | 18703 | 17848 | 18748 | 20180 | 20585 | 20759 | 20531 | 20410 | 22444 | 22065 | 22267 | 22399 | 21496 | 22168 | 23840 | 23432 | 23904 | 23730
1050 | 1050 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 18 | 18852 | 19455 | 19417 | 18688 | 19787 | 20937 | 21476 | 21667 | 21408 | 21568 | 23363 | 22851 | 23429 | 23439 | 22496 | 23550 | 25130 | 24742 | 25012 | 24886
1051 | 1051 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 19 | 19285 | 19895 | 19753 | 18905 | 20279 | 21453 | 21942 | 22168 | 21854 | 22078 | 23989 | 23663 | 24364 | 24159 | 23193 | 24418 | 26109 | 25908 | 25942 | 25805
1052 | 1052 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 20 | 19290 | 19778 | 19501 | 18713 | 20090 | 21679 | 22156 | 22273 | 21882 | 22167 | 24190 | 24366 | 24992 | 24566 | 23710 | 24761 | 26601 | 26811 | 26924 | 26419
1053 | 1053 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 21 | 19020 | 19492 | 19251 | 18509 | 19928 | 21565 | 22172 | 22290 | 22012 | 22297 | 24334 | 24778 | 25618 | 25235 | 24397 | 25332 | 27128 | 27778 | 27808 | 27371
1054 | 1054 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 22 | 18262 | 18856 | 18701 | 18090 | 19404 | 20967 | 21621 | 21903 | 21695 | 21955 | 23869 | 24539 | 25456 | 25247 | 24533 | 25238 | 26885 | 27830 | 27985 | 27552
1055 | 1055 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 23 | 17243 | 17894 | 17797 | 17544 | 18793 | 20026 | 20711 | 21130 | 20990 | 21502 | 23188 | 23859 | 24764 | 24721 | 24392 | 24941 | 26304 | 27243 | 27570 | 27097
1056 | 1056 | 44 | 2 | 13 | Winter | 2 | 13 | Winter | 24 | 16132 | 16822 | 16785 | 16768 | 18131 | 19146 | 19805 | 20376 | 20250 | 21070 | 22455 | 23180 | 24076 | 24117 | 24014 | 24578 | 25633 | 26617 | 27093 | 26544
1057 | 1057 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 1 | 15451 | 15796 | 15872 | 16349 | 17596 | 18693 | 19292 | 19596 | 19408 | 20671 | 22425 | 23039 | 23836 | 23115 | 22928 | 23998 | 26014 | 26449 | 26415 | 25431
1058 | 1058 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 2 | 15033 | 15342 | 15400 | 15926 | 17282 | 18301 | 18884 | 19163 | 18957 | 20361 | 22024 | 22601 | 23317 | 22501 | 22454 | 23605 | 25433 | 25850 | 25775 | 24762
1059 | 1059 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 3 | 14828 | 15102 | 15109 | 15720 | 17171 | 18149 | 18717 | 18967 | 18688 | 20271 | 21852 | 22380 | 23063 | 22124 | 22172 | 23408 | 25158 | 25500 | 25352 | 24309
1060 | 1060 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 4 | 14769 | 14999 | 14937 | 15617 | 17187 | 18050 | 18564 | 18729 | 18349 | 20145 | 21491 | 21950 | 22524 | 21449 | 21635 | 22981 | 24488 | 24735 | 24495 | 23445
1061 | 1061 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 5 | 14899 | 15129 | 14798 | 15485 | 17208 | 18037 | 18417 | 18561 | 17957 | 19917 | 21168 | 21532 | 21862 | 20601 | 20932 | 22452 | 23794 | 23796 | 23579 | 22375
1062 | 1062 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 6 | 15442 | 15682 | 14725 | 15379 | 17660 | 18473 | 18674 | 18796 | 17570 | 20035 | 21296 | 21536 | 21537 | 19761 | 20187 | 22267 | 23524 | 23182 | 22969 | 21300
1063 | 1063 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 7 | 16695 | 16836 | 15244 | 15641 | 18978 | 19605 | 19591 | 19806 | 17772 | 21101 | 22003 | 22221 | 21989 | 19663 | 19952 | 23090 | 23846 | 23423 | 23331 | 21054
1064 | 1064 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 8 | 18018 | 18064 | 16298 | 16318 | 20334 | 20875 | 20796 | 21022 | 18700 | 22477 | 22887 | 23214 | 22945 | 20404 | 20411 | 24296 | 24558 | 24263 | 24327 | 21738
1065 | 1065 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 9 | 18103 | 18277 | 16864 | 16904 | 20533 | 20839 | 20909 | 21231 | 19264 | 22737 | 23031 | 23033 | 22875 | 20873 | 20844 | 24407 | 24655 | 24125 | 24446 | 22196
1066 | 1066 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 10 | 17743 | 17981 | 16910 | 17064 | 20219 | 20418 | 20551 | 20909 | 19288 | 22429 | 22938 | 22636 | 22750 | 21112 | 21055 | 24148 | 24818 | 24067 | 24303 | 22482
1067 | 1067 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 11 | 17421 | 17478 | 16582 | 17010 | 19762 | 19827 | 19756 | 20089 | 18647 | 21757 | 22595 | 21902 | 22639 | 21267 | 20939 | 23466 | 25346 | 23991 | 23799 | 22687
1068 | 1068 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 12 | 17171 | 17167 | 16454 | 17047 | 19501 | 19458 | 19329 | 19575 | 18349 | 21371 | 22179 | 21453 | 22561 | 21364 | 20813 | 22955 | 25326 | 23940 | 23376 | 22797
1069 | 1069 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 13 | 17007 | 16976 | 16385 | 17066 | 19337 | 19226 | 19072 | 19273 | 18196 | 21132 | 21886 | 21166 | 22417 | 21351 | 20644 | 22597 | 25168 | 23787 | 22999 | 22773
1070 | 1070 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 14 | 16878 | 16850 | 16161 | 16886 | 19252 | 19016 | 18926 | 19062 | 17901 | 20981 | 21561 | 20888 | 22243 | 21052 | 20232 | 22379 | 24820 | 23576 | 22578 | 22444
1071 | 1071 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 15 | 16907 | 16785 | 16116 | 16985 | 19277 | 19046 | 18940 | 18932 | 17819 | 20969 | 21427 | 20879 | 22166 | 20887 | 20283 | 22307 | 24591 | 23465 | 22364 | 22247
1072 | 1072 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 16 | 17333 | 17266 | 16651 | 17609 | 19685 | 19472 | 19446 | 19367 | 18333 | 21347 | 22002 | 21237 | 22222 | 20961 | 20919 | 22630 | 24774 | 23443 | 22656 | 22264
1073 | 1073 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 17 | 17949 | 17966 | 17520 | 18374 | 20398 | 20117 | 20419 | 20200 | 19186 | 22089 | 22635 | 21842 | 22379 | 21067 | 21783 | 23474 | 24569 | 23616 | 23422 | 22378
1074 | 1074 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 18 | 18882 | 18677 | 18345 | 19425 | 21147 | 21073 | 21355 | 21093 | 20263 | 23041 | 23210 | 22983 | 23365 | 22051 | 23139 | 24753 | 25111 | 24717 | 24584 | 23434
1075 | 1075 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 19 | 19430 | 19024 | 18572 | 19927 | 21653 | 21557 | 21852 | 21512 | 20673 | 23614 | 24100 | 23855 | 24045 | 22698 | 23983 | 25702 | 26244 | 25644 | 25497 | 24267
1076 | 1076 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 20 | 19223 | 18699 | 18273 | 19639 | 21560 | 21612 | 21780 | 21335 | 20563 | 23595 | 24500 | 24376 | 24698 | 23137 | 24278 | 26154 | 27092 | 26599 | 26103 | 24907
1077 | 1077 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 21 | 18948 | 18426 | 18038 | 19435 | 21340 | 21547 | 21710 | 21361 | 20675 | 23646 | 24849 | 24897 | 25242 | 23765 | 24790 | 26635 | 27934 | 27461 | 27025 | 25789
1078 | 1078 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 22 | 18201 | 17860 | 17613 | 18902 | 20655 | 20950 | 21264 | 20990 | 20479 | 23153 | 24594 | 24677 | 25199 | 23866 | 24658 | 26378 | 27965 | 27628 | 27206 | 26056
1079 | 1079 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 23 | 17146 | 16943 | 17022 | 18263 | 19777 | 19987 | 20428 | 20219 | 20058 | 22430 | 23903 | 23927 | 24637 | 23669 | 24336 | 25767 | 27471 | 27182 | 26744 | 25950
1080 | 1080 | 45 | 2 | 14 | Winter | 2 | 14 | Winter | 24 | 16038 | 15917 | 16223 | 17603 | 18831 | 19061 | 19645 | 19455 | 19555 | 21724 | 23217 | 23228 | 24107 | 23295 | 23986 | 25117 | 26906 | 26706 | 26218 | 25639
1081 | 1081 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 1 | 15282 | 15047 | 15838 | 16666 | 18355 | 18541 | 18889 | 18682 | 19144 | 21711 | 22857 | 22997 | 23436 | 22304 | 23137 | 25494 | 26590 | 26063 | 25154 | 24392
1082 | 1082 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 2 | 14870 | 14569 | 15406 | 16338 | 17949 | 18110 | 18435 | 18209 | 18752 | 21300 | 22402 | 22512 | 22897 | 21864 | 22736 | 24946 | 26019 | 25436 | 24495 | 23905
1083 | 1083 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 3 | 14660 | 14280 | 15194 | 16236 | 17822 | 17956 | 18261 | 17966 | 18615 | 21188 | 22200 | 22288 | 22582 | 21594 | 22575 | 24682 | 25693 | 25028 | 24038 | 23577
1084 | 1084 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 4 | 14592 | 14111 | 15096 | 16155 | 17719 | 17833 | 18071 | 17682 | 18403 | 20900 | 21844 | 21815 | 21977 | 21096 | 22103 | 24041 | 25010 | 24188 | 23180 | 22927
1085 | 1085 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 5 | 14659 | 13974 | 14984 | 16216 | 17821 | 17742 | 17971 | 17366 | 18043 | 20655 | 21552 | 21241 | 21359 | 20443 | 21603 | 23386 | 24290 | 23296 | 22114 | 22086
1086 | 1086 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 6 | 15212 | 13944 | 14929 | 16435 | 18391 | 18092 | 18311 | 17096 | 17680 | 20889 | 21705 | 21031 | 21049 | 19756 | 21150 | 23157 | 24038 | 22705 | 21059 | 21218
1087 | 1087 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 7 | 16464 | 14447 | 15193 | 16906 | 19421 | 19025 | 19355 | 17347 | 17765 | 21629 | 22475 | 21534 | 21589 | 19527 | 21160 | 23485 | 24532 | 23056 | 20789 | 20879
1088 | 1088 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 8 | 17691 | 15475 | 15864 | 17216 | 20510 | 20224 | 20575 | 18281 | 18386 | 22528 | 23476 | 22513 | 22675 | 19986 | 21359 | 24199 | 25340 | 24044 | 21458 | 21299
1089 | 1089 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 9 | 17918 | 16159 | 16573 | 17633 | 20796 | 20459 | 20916 | 18982 | 19044 | 22812 | 23518 | 22572 | 22968 | 20545 | 21669 | 24418 | 25235 | 24286 | 22028 | 21820
1090 | 1090 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 10 | 17917 | 16580 | 17117 | 18060 | 20986 | 20502 | 21012 | 19440 | 19636 | 23154 | 23552 | 22717 | 23043 | 21034 | 22173 | 24862 | 25325 | 24420 | 22596 | 22350
1091 | 1091 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 11 | 17791 | 16701 | 17573 | 18286 | 21311 | 20384 | 20906 | 19582 | 20119 | 23622 | 23552 | 22663 | 22537 | 20967 | 22444 | 25430 | 25377 | 23963 | 22853 | 22319
1092 | 1092 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 12 | 17704 | 16765 | 17847 | 18386 | 21277 | 20276 | 20741 | 19659 | 20387 | 23603 | 23400 | 22580 | 22121 | 20847 | 22527 | 25427 | 25227 | 23548 | 22969 | 22199
1093 | 1093 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 13 | 17499 | 16675 | 17850 | 18291 | 21045 | 20040 | 20471 | 19546 | 20365 | 23352 | 23222 | 22337 | 21642 | 20573 | 22374 | 25158 | 25037 | 23057 | 22837 | 21916
1094 | 1094 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 14 | 17275 | 16315 | 17540 | 17899 | 20706 | 19779 | 20148 | 19141 | 20000 | 22923 | 22923 | 22012 | 21097 | 20005 | 21877 | 24656 | 24694 | 22476 | 22348 | 21316
1095 | 1095 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 15 | 17208 | 16172 | 17530 | 17754 | 20538 | 19682 | 19906 | 18942 | 19947 | 22672 | 22898 | 21854 | 20839 | 19970 | 21649 | 24342 | 24634 | 22175 | 22061 | 21261
1096 | 1096 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 16 | 17410 | 16368 | 17798 | 17904 | 20660 | 19772 | 19898 | 18985 | 20067 | 22730 | 22886 | 21762 | 21037 | 20440 | 21570 | 24359 | 24533 | 22297 | 21904 | 21704
1097 | 1097 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 17 | 17999 | 16877 | 18151 | 18455 | 20652 | 20144 | 20054 | 19100 | 20091 | 22523 | 22824 | 21951 | 21827 | 21335 | 21854 | 24179 | 24580 | 23102 | 22053 | 22611
1098 | 1098 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 18 | 18594 | 17572 | 19014 | 19296 | 21072 | 20862 | 20687 | 19885 | 21048 | 22797 | 23383 | 22883 | 22843 | 22688 | 23066 | 24723 | 25277 | 24264 | 23126 | 24027
1099 | 1099 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 19 | 18993 | 17757 | 19449 | 19881 | 21655 | 21252 | 20970 | 20134 | 21409 | 23468 | 24020 | 23494 | 23517 | 23485 | 23947 | 25827 | 26292 | 25180 | 23954 | 24981
1100 | 1100 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 20 | 18813 | 17496 | 19196 | 19922 | 21747 | 21210 | 20820 | 20044 | 21396 | 23868 | 24625 | 24047 | 23823 | 23723 | 24522 | 26621 | 27350 | 25767 | 24583 | 25358
1101 | 1101 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 21 | 18479 | 17215 | 18948 | 19636 | 21588 | 21046 | 20746 | 20045 | 21411 | 24095 | 24982 | 24461 | 24382 | 24150 | 24921 | 27394 | 28222 | 26655 | 25437 | 25998
1102 | 1102 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 22 | 17845 | 16812 | 18435 | 19148 | 21016 | 20583 | 20353 | 19822 | 21058 | 23808 | 24721 | 24375 | 24371 | 24025 | 24834 | 27428 | 28279 | 26855 | 25732 | 26006
1103 | 1103 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 23 | 16905 | 16233 | 17810 | 18419 | 20102 | 19759 | 19587 | 19403 | 20608 | 23130 | 24026 | 23805 | 23839 | 23713 | 24404 | 26937 | 27767 | 26407 | 25651 | 25750
1104 | 1104 | 46 | 2 | 15 | Winter | 2 | 15 | Winter | 24 | 15837 | 15424 | 17104 | 17610 | 19173 | 18932 | 18779 | 18857 | 20198 | 22447 | 23286 | 23229 | 23203 | 23333 | 23934 | 26347 | 27080 | 25838 | 25318 | 25415
1105 | 1105 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 1 | 15126 | 15256 | 16347 | 18057 | 18654 | 18341 | 18190 | 18688 | 19622 | 22244 | 23041 | 22847 | 22554 | 22769 | 25163 | 26297 | 26916 | 25072 | 24391 | 24808
1106 | 1106 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 2 | 14686 | 14819 | 16023 | 17652 | 18233 | 17900 | 17736 | 18315 | 19333 | 21844 | 22629 | 22323 | 21973 | 22370 | 24617 | 25725 | 26375 | 24403 | 23886 | 24367
1107 | 1107 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 3 | 14450 | 14581 | 15899 | 17503 | 18036 | 17710 | 17480 | 18161 | 19273 | 21657 | 22503 | 22042 | 21622 | 22231 | 24373 | 25410 | 26099 | 23957 | 23564 | 24168
1108 | 1108 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 4 | 14372 | 14492 | 15833 | 17426 | 17953 | 17564 | 17251 | 18002 | 19117 | 21385 | 22153 | 21536 | 21023 | 21819 | 23802 | 24781 | 25392 | 23134 | 22942 | 23620
1109 | 1109 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 5 | 14526 | 14409 | 15921 | 17570 | 18020 | 17528 | 17012 | 17715 | 18993 | 21186 | 21778 | 21015 | 20256 | 21384 | 23204 | 24115 | 24651 | 22108 | 22118 | 23004
1110 | 1110 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 6 | 15097 | 14354 | 16169 | 18167 | 18535 | 17913 | 16813 | 17411 | 18929 | 21409 | 21732 | 20800 | 19498 | 20985 | 23023 | 23900 | 24251 | 21072 | 21239 | 22435
1111 | 1111 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 7 | 16241 | 14653 | 16676 | 19256 | 19743 | 19005 | 17152 | 17593 | 19194 | 22273 | 22513 | 21432 | 19443 | 21030 | 23408 | 24443 | 24650 | 20827 | 20922 | 22381
1112 | 1112 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 8 | 17471 | 15376 | 17032 | 20416 | 21039 | 20283 | 18162 | 18300 | 19586 | 23372 | 23854 | 22583 | 20230 | 21276 | 24170 | 25303 | 25806 | 21532 | 21368 | 22596
1113 | 1113 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 9 | 17641 | 15945 | 17306 | 20544 | 21044 | 20482 | 18724 | 18844 | 19908 | 23310 | 24032 | 22750 | 20681 | 21434 | 24254 | 25077 | 25939 | 21950 | 21760 | 22727
1114 | 1114 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 10 | 17283 | 16090 | 17312 | 20268 | 20563 | 20117 | 18708 | 18966 | 19889 | 22856 | 23716 | 22444 | 20828 | 21561 | 24322 | 24796 | 25682 | 22146 | 21926 | 22889
1115 | 1115 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 11 | 16852 | 16217 | 17202 | 20168 | 20066 | 19528 | 18335 | 18899 | 19566 | 22256 | 23333 | 21803 | 20902 | 21711 | 24760 | 24717 | 25377 | 22270 | 21758 | 23072
1116 | 1116 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 12 | 16566 | 16337 | 17128 | 19941 | 19678 | 19120 | 18144 | 18887 | 19343 | 21782 | 22990 | 21328 | 20953 | 21735 | 24696 | 24517 | 25120 | 22334 | 21591 | 23092
1117 | 1117 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 13 | 16384 | 16381 | 17064 | 19723 | 19512 | 18839 | 17998 | 18818 | 19152 | 21543 | 22612 | 20985 | 20950 | 21708 | 24548 | 24446 | 24801 | 22321 | 21426 | 23035
1118 | 1118 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 14 | 16211 | 16172 | 16754 | 19466 | 19308 | 18563 | 17625 | 18475 | 18714 | 21247 | 22363 | 20602 | 20647 | 21370 | 24204 | 24258 | 24606 | 21985 | 20978 | 22664
1119 | 1119 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 15 | 16228 | 16343 | 16798 | 19508 | 19520 | 18534 | 17639 | 18636 | 18740 | 21443 | 22354 | 20510 | 20553 | 21303 | 24052 | 24356 | 24528 | 21857 | 21078 | 22574
1120 | 1120 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 16 | 16510 | 16722 | 17110 | 19809 | 19875 | 18791 | 17970 | 19061 | 19066 | 21776 | 22554 | 20677 | 20414 | 21186 | 24026 | 24210 | 24532 | 21651 | 21461 | 22420
1121 | 1121 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 17 | 17435 | 17678 | 18328 | 20541 | 20884 | 19797 | 18977 | 20022 | 20292 | 22688 | 23278 | 21701 | 20791 | 21717 | 24090 | 24498 | 25066 | 22040 | 22606 | 22970
1122 | 1122 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 18 | 18101 | 18593 | 19192 | 21054 | 21492 | 20506 | 19810 | 21019 | 21326 | 23267 | 24276 | 22732 | 21834 | 22970 | 24691 | 25247 | 26267 | 23191 | 24106 | 24298
1123 | 1123 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 19 | 18399 | 19035 | 19792 | 21634 | 21883 | 20789 | 20046 | 21358 | 21930 | 23827 | 24954 | 23324 | 22420 | 23805 | 25746 | 26222 | 27408 | 24015 | 25054 | 25280
1124 | 1124 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 20 | 18102 | 18771 | 19834 | 21700 | 22081 | 20616 | 19917 | 21301 | 22046 | 24355 | 25317 | 23555 | 22791 | 24355 | 26495 | 27240 | 28210 | 24645 | 25437 | 25978
1125 | 1125 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 21 | 17804 | 18528 | 19535 | 21505 | 21931 | 20491 | 19861 | 21270 | 21993 | 24618 | 25541 | 24026 | 23333 | 24707 | 27226 | 28076 | 28931 | 25504 | 26090 | 26532
1126 | 1126 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 22 | 17202 | 17974 | 18974 | 20848 | 21251 | 20003 | 19529 | 20828 | 21600 | 24233 | 25110 | 23903 | 23369 | 24527 | 27169 | 28045 | 28775 | 25729 | 26056 | 26472
1127 | 1127 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 23 | 16323 | 17301 | 18216 | 19903 | 20323 | 19194 | 19058 | 20323 | 21008 | 23499 | 24452 | 23318 | 23156 | 24077 | 26645 | 27506 | 28263 | 25623 | 25786 | 26086
1128 | 1128 | 47 | 2 | 16 | Winter | 2 | 16 | Winter | 24 | 15271 | 16555 | 17339 | 18902 | 19277 | 18290 | 18412 | 19802 | 20405 | 22698 | 23793 | 22662 | 22746 | 23598 | 26047 | 26825 | 27675 | 25281 | 25448 | 25658
1129 | 1129 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 1 | 14166 | 15260 | 17264 | 17843 | 18285 | 17222 | 17815 | 18726 | 20775 | 22016 | 23030 | 21513 | 21605 | 24269 | 25445 | 26130 | 26955 | 23830 | 24299 | 26502
1130 | 1130 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 2 | 13685 | 14915 | 16836 | 17383 | 17858 | 16733 | 17403 | 18397 | 20361 | 21589 | 22547 | 20950 | 21167 | 23732 | 24887 | 25601 | 26361 | 23327 | 23853 | 25917
1131 | 1131 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 3 | 13422 | 14784 | 16695 | 17192 | 17788 | 16496 | 17271 | 18363 | 20271 | 21519 | 22345 | 20638 | 20932 | 23519 | 24608 | 25352 | 26025 | 23020 | 23672 | 25636
1132 | 1132 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 4 | 13264 | 14721 | 16616 | 17108 | 17709 | 16284 | 17134 | 18236 | 20043 | 21233 | 21936 | 20092 | 20487 | 22973 | 24006 | 24661 | 25267 | 22395 | 23109 | 24917
1133 | 1133 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 5 | 13161 | 14823 | 16797 | 17220 | 17759 | 16112 | 16917 | 18189 | 19901 | 20962 | 21482 | 19423 | 19917 | 22449 | 23404 | 23978 | 24399 | 21605 | 22523 | 24181
1134 | 1134 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 6 | 13140 | 15076 | 17413 | 17778 | 18160 | 15975 | 16691 | 18213 | 20210 | 21009 | 21367 | 18761 | 19273 | 22324 | 23240 | 23602 | 23849 | 20744 | 21959 | 23849
1135 | 1135 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 7 | 13683 | 15620 | 18565 | 19037 | 19263 | 16361 | 16939 | 18552 | 21058 | 21887 | 22120 | 18797 | 19123 | 22764 | 23841 | 24061 | 24321 | 20450 | 21918 | 24133
1136 | 1136 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 8 | 14708 | 15937 | 19698 | 20292 | 20664 | 17323 | 17610 | 18915 | 22000 | 23204 | 23225 | 19582 | 19602 | 23533 | 24694 | 25191 | 25283 | 20868 | 22101 | 24794
1137 | 1137 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 9 | 15415 | 16378 | 20002 | 20475 | 21104 | 18046 | 18330 | 19426 | 22328 | 23570 | 23548 | 20222 | 20213 | 23804 | 24656 | 25508 | 25475 | 21431 | 22390 | 25018
1138 | 1138 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 10 | 15931 | 16919 | 20225 | 20521 | 21298 | 18563 | 18993 | 19962 | 22737 | 23815 | 23669 | 20811 | 20785 | 24306 | 24817 | 25711 | 25674 | 22045 | 23004 | 25579
1139 | 1139 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 11 | 16208 | 17316 | 20651 | 20606 | 21561 | 18831 | 19602 | 20357 | 23335 | 24153 | 23692 | 21147 | 20852 | 24998 | 25008 | 25656 | 25755 | 22146 | 23455 | 26333
1140 | 1140 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 12 | 16366 | 17541 | 20726 | 20542 | 21604 | 18997 | 19964 | 20529 | 23406 | 24221 | 23525 | 21341 | 20828 | 25086 | 24952 | 25551 | 25600 | 22125 | 23630 | 26422
1141 | 1141 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 13 | 16351 | 17541 | 20579 | 20462 | 21416 | 18964 | 20021 | 20479 | 23235 | 23994 | 23246 | 21299 | 20631 | 24898 | 24848 | 25194 | 25286 | 21914 | 23534 | 26220
1142 | 1142 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 14 | 16059 | 17223 | 20343 | 20281 | 21305 | 18639 | 19737 | 20111 | 22885 | 23824 | 22921 | 20920 | 20135 | 24480 | 24586 | 24919 | 24893 | 21384 | 23085 | 25758
1143 | 1143 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 15 | 15919 | 17090 | 20205 | 20298 | 21157 | 18454 | 19694 | 19927 | 22643 | 23606 | 22704 | 20676 | 20101 | 24178 | 24528 | 24688 | 24613 | 21327 | 22838 | 25428
1144 | 1144 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 16 | 15925 | 17084 | 20116 | 20291 | 21035 | 18371 | 19671 | 19781 | 22527 | 23302 | 22335 | 20423 | 20384 | 24033 | 24257 | 24555 | 24126 | 21573 | 22553 | 25234
1145 | 1145 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 17 | 16239 | 17551 | 20052 | 20441 | 20841 | 18407 | 19595 | 19922 | 22163 | 22846 | 22243 | 20364 | 21077 | 23663 | 24110 | 24659 | 24060 | 22287 | 22667 | 24875
1146 | 1146 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 18 | 16798 | 18205 | 20410 | 20872 | 21503 | 19067 | 20393 | 20734 | 22311 | 23602 | 22956 | 21163 | 22303 | 24051 | 24636 | 25649 | 25023 | 23604 | 23797 | 25345
1147 | 1147 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 19 | 16944 | 18772 | 20975 | 21237 | 22020 | 19274 | 20690 | 21281 | 22908 | 24151 | 23604 | 21655 | 23022 | 25022 | 25535 | 26723 | 25994 | 24520 | 24749 | 26508
1148 | 1148 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 20 | 16689 | 18766 | 21004 | 21391 | 21923 | 19108 | 20592 | 21346 | 23230 | 24410 | 23796 | 21938 | 23212 | 25709 | 26493 | 27478 | 26720 | 24904 | 25445 | 27413
1149 | 1149 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 21 | 16387 | 18449 | 20751 | 21173 | 21653 | 18975 | 20482 | 21200 | 23361 | 24509 | 24014 | 22359 | 23576 | 26336 | 27243 | 28136 | 27454 | 25525 | 25969 | 28304
1150 | 1150 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 22 | 15934 | 17893 | 20080 | 20473 | 20976 | 18614 | 20012 | 20765 | 22977 | 24038 | 23671 | 22339 | 23386 | 26246 | 27183 | 27973 | 27395 | 25483 | 25913 | 28383
1151 | 1151 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 23 | 15359 | 17138 | 19129 | 19542 | 20080 | 18130 | 19495 | 20155 | 22265 | 23364 | 23148 | 22109 | 23045 | 25718 | 26644 | 27463 | 27032 | 25227 | 25553 | 27956
1152 | 1152 | 48 | 2 | 17 | Winter | 2 | 17 | Winter | 24 | 14571 | 16290 | 18118 | 18502 | 19184 | 17482 | 18980 | 19558 | 21552 | 22748 | 22542 | 21687 | 22664 | 25125 | 25955 | 26875 | 26513 | 24888 | 25126 | 27413
1153 | 1153 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 1 | 14293 | 16554 | 17387 | 17821 | 18488 | 17250 | 18235 | 20142 | 21181 | 22294 | 21515 | 21066 | 22001 | 24929 | 25677 | 26554 | 25370 | 24177 | 26372 | 27303
1154 | 1154 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 2 | 13844 | 16131 | 16927 | 17391 | 18072 | 16844 | 17915 | 19749 | 20768 | 21863 | 21017 | 20627 | 21595 | 24372 | 25142 | 25954 | 24695 | 23711 | 25770 | 26684
1155 | 1155 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 3 | 13596 | 15940 | 16689 | 17275 | 17854 | 16661 | 17834 | 19623 | 20579 | 21646 | 20738 | 20399 | 21471 | 24090 | 24896 | 25617 | 24315 | 23523 | 25479 | 26335
1156 | 1156 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 4 | 13504 | 15879 | 16618 | 17216 | 17737 | 16548 | 17738 | 19448 | 20361 | 21325 | 20264 | 20022 | 21101 | 23550 | 24268 | 24908 | 23517 | 22983 | 24783 | 25624
1157 | 1157 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 5 | 13454 | 16073 | 16757 | 17305 | 17702 | 16380 | 17745 | 19385 | 20265 | 20968 | 19634 | 19524 | 20736 | 23008 | 23649 | 24093 | 22488 | 22412 | 24065 | 24860
1158 | 1158 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 6 | 13428 | 16713 | 17339 | 17762 | 18118 | 16210 | 17834 | 19795 | 20592 | 20966 | 19078 | 18980 | 20400 | 22925 | 23339 | 23606 | 21474 | 21872 | 23775 | 24557
1159 | 1159 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 7 | 13727 | 17875 | 18585 | 18875 | 19248 | 16468 | 18215 | 20700 | 21513 | 21780 | 19191 | 18866 | 20482 | 23552 | 23813 | 24083 | 21217 | 21822 | 24031 | 24985
1160 | 1160 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 8 | 14419 | 19044 | 19851 | 20273 | 20444 | 17145 | 18604 | 21702 | 22609 | 22921 | 20064 | 19359 | 20706 | 24418 | 24949 | 25042 | 21960 | 21996 | 24684 | 25742
1161 | 1161 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 9 | 15086 | 19268 | 19976 | 20626 | 20713 | 17788 | 19065 | 21975 | 22672 | 23198 | 20748 | 19916 | 20996 | 24338 | 25201 | 25175 | 22588 | 22225 | 24823 | 25567
1162 | 1162 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 10 | 15537 | 19265 | 19804 | 20588 | 20513 | 18185 | 19330 | 22082 | 22490 | 23009 | 21080 | 20336 | 21431 | 24349 | 25246 | 25228 | 23125 | 22695 | 25231 | 25620
1163 | 1163 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 11 | 15813 | 19326 | 19517 | 20426 | 19992 | 18268 | 19147 | 22069 | 21977 | 22353 | 20862 | 20311 | 21759 | 24449 | 25094 | 25221 | 23548 | 23050 | 25906 | 25756
1164 | 1164 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 12 | 15971 | 19180 | 19211 | 20185 | 19497 | 18281 | 18942 | 21729 | 21478 | 21740 | 20586 | 20229 | 21880 | 24334 | 24942 | 25013 | 23672 | 23170 | 25941 | 25645
1165 | 1165 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 13 | 15932 | 18928 | 18983 | 19845 | 19082 | 18141 | 18676 | 21326 | 21126 | 21201 | 20239 | 20010 | 21779 | 24206 | 24562 | 24671 | 23544 | 23049 | 25715 | 25501
1166 | 1166 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 14 | 15737 | 18734 | 18819 | 19744 | 18819 | 17843 | 18280 | 20945 | 20850 | 20816 | 19819 | 19614 | 21452 | 24035 | 24383 | 24375 | 23221 | 22688 | 25354 | 25301
1167 | 1167 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 15 | 15797 | 18695 | 18915 | 19689 | 18775 | 17895 | 18196 | 20810 | 20934 | 20712 | 19710 | 19637 | 21279 | 24032 | 24209 | 24151 | 23011 | 22490 | 25070 | 25279
1168 | 1168 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 16 | 16203 | 18943 | 19294 | 19995 | 19055 | 18361 | 18565 | 21212 | 21329 | 20939 | 19823 | 20087 | 21182 | 23925 | 24242 | 23829 | 22608 | 22353 | 25034 | 25133
1169 | 1169 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 17 | 16898 | 19420 | 20075 | 20500 | 19942 | 19138 | 19611 | 21825 | 22087 | 21878 | 20481 | 20869 | 21360 | 23859 | 24432 | 23855 | 22355 | 22549 | 24772 | 25101
1170 | 1170 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 18 | 17692 | 19884 | 20634 | 21264 | 20544 | 20101 | 20571 | 22145 | 22660 | 22727 | 21286 | 22060 | 22429 | 24387 | 25424 | 24805 | 23263 | 23720 | 25248 | 25746
1171 | 1171 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 19 | 18146 | 20508 | 21077 | 21840 | 21035 | 20480 | 21184 | 22784 | 23212 | 23356 | 22024 | 22753 | 23222 | 25264 | 26486 | 25772 | 24378 | 24706 | 26437 | 26810
1172 | 1172 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 20 | 17823 | 20462 | 21146 | 21657 | 20846 | 20283 | 21122 | 22945 | 23542 | 23342 | 22033 | 22875 | 23713 | 26158 | 27186 | 26455 | 24793 | 25393 | 27340 | 27936
1173 | 1173 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 21 | 17552 | 20164 | 20895 | 21361 | 20585 | 20136 | 20933 | 22983 | 23687 | 23463 | 22373 | 23167 | 23987 | 26834 | 27786 | 27142 | 25623 | 25916 | 28217 | 28892
1174 | 1174 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 22 | 17029 | 19469 | 20193 | 20702 | 19972 | 19654 | 20491 | 22545 | 23275 | 23058 | 22202 | 22946 | 23806 | 26742 | 27606 | 27072 | 25733 | 25879 | 28299 | 28988
1175 | 1175 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 23 | 16368 | 18510 | 19237 | 19788 | 19198 | 19111 | 19849 | 21799 | 22527 | 22520 | 21846 | 22582 | 23358 | 26182 | 27075 | 26697 | 25540 | 25506 | 27875 | 28522
1176 | 1176 | 49 | 2 | 18 | Winter | 2 | 18 | Winter | 24 | 15607 | 17434 | 18115 | 18814 | 18241 | 18506 | 19152 | 20993 | 21697 | 21842 | 21283 | 22165 | 22854 | 25485 | 26454 | 26155 | 25112 | 25053 | 27318 | 27856
1177 | 1177 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 1 | 14899 | 16885 | 17591 | 18294 | 17449 | 17952 | 19862 | 20799 | 21535 | 21087 | 20256 | 21678 | 24010 | 25352 | 26310 | 25174 | 23348 | 26435 | 27384 | 27789
1178 | 1178 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 2 | 14536 | 16406 | 17137 | 17836 | 16927 | 17589 | 19427 | 20345 | 21102 | 20571 | 19819 | 21291 | 23487 | 24838 | 25726 | 24513 | 22865 | 25827 | 26766 | 27207
1179 | 1179 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 3 | 14414 | 16206 | 17054 | 17649 | 16716 | 17549 | 19350 | 20216 | 21063 | 20383 | 19614 | 21220 | 23313 | 24645 | 25437 | 24178 | 22532 | 25570 | 26454 | 26935
1180 | 1180 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 4 | 14347 | 16107 | 16988 | 17527 | 16489 | 17452 | 19197 | 20028 | 20831 | 19968 | 19258 | 20882 | 22826 | 24036 | 24753 | 23393 | 21889 | 24868 | 25722 | 26150
1181 | 1181 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 5 | 14439 | 16233 | 17090 | 17510 | 16292 | 17483 | 19184 | 19992 | 20637 | 19411 | 18838 | 20567 | 22363 | 23461 | 23971 | 22396 | 21104 | 24154 | 24959 | 25346
1182 | 1182 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 6 | 14666 | 16789 | 17562 | 17937 | 16198 | 17590 | 19647 | 20380 | 20767 | 18941 | 18390 | 20278 | 22307 | 23182 | 23497 | 21409 | 20300 | 23850 | 24630 | 24865
1183 | 1183 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 7 | 15206 | 18083 | 18708 | 19096 | 16598 | 17995 | 20623 | 21371 | 21692 | 19116 | 18395 | 20422 | 22777 | 23700 | 24024 | 21175 | 20128 | 24127 | 25076 | 25231
1184 | 1184 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 8 | 15528 | 19357 | 20111 | 20293 | 17606 | 18380 | 21670 | 22497 | 23053 | 20023 | 18983 | 20686 | 23566 | 24870 | 25026 | 21945 | 20635 | 24813 | 25856 | 26341
1185 | 1185 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 9 | 15867 | 19459 | 20422 | 20523 | 18307 | 18792 | 21907 | 22537 | 23313 | 20688 | 19561 | 20956 | 23734 | 25088 | 25136 | 22533 | 21134 | 24917 | 25656 | 26545
1186 | 1186 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 10 | 16294 | 19376 | 20478 | 20426 | 18729 | 19176 | 22125 | 22494 | 23415 | 21164 | 20134 | 21389 | 24086 | 25133 | 25195 | 23066 | 21594 | 25324 | 25708 | 26620
1187 | 1187 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 11 | 16544 | 19326 | 20599 | 20230 | 19003 | 19408 | 22546 | 22476 | 23592 | 21478 | 20374 | 21651 | 24630 | 24918 | 25114 | 23434 | 21053 | 25931 | 25782 | 26463
1188 | 1188 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 12 | 16659 | 19167 | 20525 | 19947 | 19049 | 19459 | 22477 | 22285 | 23522 | 21524 | 20473 | 21698 | 24584 | 24688 | 24831 | 23493 | 20628 | 25889 | 25605 | 26247
1189 | 1189 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 13 | 16570 | 18981 | 20262 | 19634 | 18904 | 19325 | 22218 | 22092 | 23215 | 21351 | 20389 | 21541 | 24308 | 24247 | 24426 | 23295 | 20267 | 25597 | 25394 | 25779
1190 | 1190 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 14 | 16295 | 18850 | 20208 | 19435 | 18658 | 19012 | 21936 | 21919 | 23094 | 21044 | 20136 | 21172 | 23938 | 24030 | 24084 | 22927 | 19906 | 25183 | 25147 | 25523
1191 | 1191 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 15 | 16203 | 18885 | 20116 | 19356 | 18549 | 18880 | 21754 | 21946 | 22924 | 20878 | 20129 | 20994 | 23682 | 23846 | 23854 | 22710 | 19886 | 24895 | 25107 | 25298
1192 | 1192 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 16 | 16427 | 19162 | 20286 | 19464 | 18500 | 19016 | 21862 | 22051 | 22884 | 20671 | 20271 | 20995 | 23780 | 23977 | 23621 | 22401 | 20338 | 24942 | 25046 | 25362
1193 | 1193 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 17 | 17082 | 19640 | 20406 | 19879 | 18473 | 19451 | 21801 | 22068 | 22643 | 20474 | 20466 | 21262 | 23591 | 24267 | 23736 | 22247 | 21663 | 24775 | 25101 | 25663
1194 | 1194 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 18 | 17861 | 20226 | 21131 | 20458 | 19143 | 20390 | 22088 | 22578 | 23506 | 21138 | 21392 | 22389 | 24078 | 25341 | 24779 | 23253 | 23072 | 25367 | 25850 | 26854
1195 | 1195 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 19 | 18431 | 20631 | 21665 | 20882 | 19607 | 20951 | 22650 | 23033 | 24012 | 21727 | 22067 | 23093 | 24996 | 26317 | 25674 | 24294 | 24238 | 26520 | 26879 | 28031
1196 | 1196 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 20 | 18387 | 20678 | 21504 | 20719 | 19387 | 20944 | 22832 | 23377 | 24168 | 21740 | 22445 | 23505 | 25609 | 26941 | 26284 | 24668 | 24867 | 27400 | 27987 | 28867
1197 | 1197 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 21 | 18088 | 20410 | 21191 | 20433 | 19248 | 20715 | 22795 | 23429 | 24173 | 21963 | 22698 | 23703 | 26154 | 27468 | 26919 | 25438 | 25509 | 28260 | 28932 | 29655
1198 | 1198 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 22 | 17554 | 19682 | 20516 | 19819 | 18779 | 20238 | 22308 | 22955 | 23671 | 21726 | 22425 | 23477 | 26032 | 27248 | 26823 | 25514 | 25467 | 28326 | 29022 | 29570
1199 | 1199 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 23 | 16770 | 18674 | 19548 | 19002 | 18154 | 19542 | 21488 | 22134 | 22933 | 21314 | 22000 | 22976 | 25459 | 26667 | 26398 | 25284 | 25169 | 27866 | 28529 | 29092
1200 | 1200 | 50 | 2 | 19 | Winter | 2 | 19 | Winter | 24 | 15910 | 17557 | 18558 | 18033 | 17383 | 18835 | 20665 | 21289 | 22271 | 20793 | 21515 | 22468 | 24842 | 26045 | 25844 | 24864 | 24695 | 27307 | 27872 | 28536
1201 | 1201 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 1 | 16110 | 16743 | 17735 | 16937 | 16584 | 19210 | 20115 | 20787 | 21754 | 19630 | 20992 | 23333 | 24543 | 25647 | 24626 | 22933 | 24153 | 27100 | 27559 | 28158
1202 | 1202 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 2 | 15713 | 16328 | 17313 | 16435 | 16194 | 18810 | 19693 | 20393 | 21325 | 19249 | 20660 | 22872 | 24039 | 25117 | 24020 | 22490 | 23724 | 26521 | 27015 | 27559
1203 | 1203 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 3 | 15545 | 16192 | 17089 | 16184 | 15967 | 18703 | 19541 | 20337 | 21160 | 19050 | 20591 | 22704 | 23791 | 24831 | 23682 | 22148 | 23546 | 26190 | 26727 | 27200
1204 | 1204 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 4 | 15493 | 16145 | 16989 | 15981 | 15829 | 18591 | 19412 | 20169 | 20906 | 18770 | 20325 | 22284 | 23309 | 24224 | 22957 | 21556 | 23011 | 25494 | 25965 | 26393
1205 | 1205 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 5 | 15640 | 16233 | 16960 | 15776 | 15651 | 18587 | 19406 | 20018 | 20582 | 18381 | 20038 | 21856 | 22789 | 23468 | 21980 | 20764 | 22422 | 24715 | 25137 | 25407
1206 | 1206 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 6 | 16261 | 16739 | 17443 | 15741 | 15541 | 19105 | 19893 | 20264 | 20661 | 18024 | 19837 | 21875 | 22777 | 23067 | 21062 | 20011 | 21898 | 24435 | 24685 | 24788
1207 | 1207 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 7 | 17438 | 17935 | 18629 | 16155 | 15857 | 20138 | 20922 | 21259 | 21536 | 18076 | 20017 | 22417 | 23434 | 23634 | 20855 | 19847 | 21861 | 24886 | 25036 | 25215
1208 | 1208 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 8 | 18659 | 19348 | 19834 | 17176 | 16605 | 21213 | 22088 | 22669 | 22725 | 18710 | 20316 | 23278 | 24374 | 24671 | 21662 | 20375 | 22069 | 25700 | 26161 | 26180
1209 | 1209 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 9 | 18763 | 19577 | 19991 | 17799 | 17141 | 21375 | 22065 | 22872 | 22907 | 19238 | 20529 | 23409 | 24187 | 24713 | 22180 | 20802 | 22199 | 25413 | 26282 | 26173
1210 | 1210 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 10 | 18697 | 19517 | 19778 | 18108 | 17539 | 21450 | 21888 | 22843 | 22749 | 19690 | 20840 | 23626 | 24082 | 24634 | 22591 | 21141 | 22557 | 25339 | 26241 | 26154
1211 | 1211 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 11 | 18745 | 19449 | 19425 | 18223 | 17575 | 21668 | 21705 | 22850 | 22451 | 19761 | 20933 | 23988 | 23966 | 24378 | 22789 | 20433 | 22684 | 25255 | 25916 | 25951
1212 | 1212 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 12 | 18711 | 19391 | 19165 | 18287 | 17682 | 21620 | 21523 | 22793 | 22164 | 19870 | 20992 | 23947 | 23790 | 24098 | 22860 | 20020 | 22738 | 25087 | 25710 | 25684
1213 | 1213 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 13 | 18570 | 19219 | 18934 | 18213 | 17685 | 21430 | 21399 | 22557 | 21867 | 19854 | 20913 | 23738 | 23654 | 23774 | 22731 | 19736 | 22623 | 24950 | 25306 | 25316
1214 | 1214 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 14 | 18411 | 19143 | 18752 | 17987 | 17484 | 21171 | 21241 | 22454 | 21605 | 19615 | 20561 | 23389 | 23445 | 23455 | 22378 | 19388 | 22221 | 24711 | 25068 | 24963
1215 | 1215 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 15 | 18484 | 19197 | 18811 | 18014 | 17644 | 21134 | 21403 | 22423 | 21574 | 19739 | 20518 | 23270 | 23561 | 23361 | 22293 | 19498 | 22140 | 24805 | 24973 | 24827
1216 | 1216 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 16 | 18720 | 19478 | 19047 | 18089 | 18016 | 21357 | 21635 | 22512 | 21578 | 19986 | 20625 | 23450 | 23646 | 23240 | 22089 | 20049 | 22178 | 24837 | 25134 | 24638
1217 | 1217 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 17 | 18902 | 19653 | 19519 | 18122 | 18524 | 21362 | 21709 | 22325 | 21699 | 20172 | 20885 | 23262 | 23684 | 23354 | 21933 | 21373 | 22474 | 24902 | 25435 | 24761
1218 | 1218 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 18 | 19444 | 20379 | 20060 | 18783 | 19339 | 21692 | 22223 | 23141 | 22468 | 21048 | 21972 | 23736 | 24285 | 24375 | 22917 | 22788 | 23765 | 25636 | 26626 | 25901
1219 | 1219 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 19 | 20034 | 20940 | 20517 | 19258 | 19826 | 22276 | 22689 | 23636 | 22997 | 21666 | 22624 | 24599 | 25094 | 25229 | 23928 | 23928 | 24740 | 26684 | 27815 | 26962
1220 | 1220 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 20 | 19981 | 20752 | 20315 | 19017 | 19912 | 22400 | 22967 | 23704 | 22971 | 21955 | 22964 | 25113 | 25900 | 25767 | 24254 | 24518 | 25393 | 27776 | 28640 | 27718
1221 | 1221 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 21 | 19712 | 20454 | 20047 | 18892 | 19830 | 22355 | 22976 | 23670 | 23049 | 22165 | 23124 | 25619 | 26527 | 26378 | 25008 | 25175 | 25947 | 28736 | 29466 | 28597
1222 | 1222 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 22 | 18964 | 19755 | 19382 | 18374 | 19279 | 21788 | 22402 | 23077 | 22568 | 21813 | 22821 | 25405 | 26341 | 26201 | 25008 | 25080 | 25860 | 28759 | 29344 | 28562
1223 | 1223 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 23 | 17965 | 18786 | 18537 | 17734 | 18676 | 20928 | 21539 | 22294 | 21948 | 21365 | 22291 | 24791 | 25740 | 25755 | 24764 | 24766 | 25447 | 28264 | 28867 | 28214
1224 | 1224 | 51 | 2 | 20 | Winter | 2 | 20 | Winter | 24 | 16901 | 17757 | 17528 | 16926 | 17948 | 20041 | 20646 | 21572 | 21270 | 20877 | 21775 | 24155 | 25018 | 25183 | 24327 | 24287 | 24987 | 27598 | 28302 | 27705
1225 | 1225 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 1 | 15913 | 16753 | 16283 | 16007 | 17142 | 19264 | 19951 | 20853 | 20097 | 20224 | 23170 | 23663 | 24495 | 23861 | 22328 | 23605 | 26558 | 27142 | 27782 | 26270
1226 | 1226 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 2 | 15457 | 16294 | 15754 | 15585 | 16781 | 18813 | 19534 | 20405 | 19603 | 19890 | 22747 | 23158 | 24015 | 23248 | 21881 | 23164 | 26141 | 26579 | 27165 | 25594
1227 | 1227 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 3 | 15251 | 16065 | 15496 | 15351 | 16714 | 18659 | 19489 | 20252 | 19415 | 19855 | 22664 | 22953 | 23841 | 22940 | 21566 | 22996 | 25910 | 26308 | 26819 | 25219
1228 | 1228 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 4 | 15152 | 15946 | 15282 | 15201 | 16619 | 18538 | 19351 | 20035 | 19059 | 19629 | 22374 | 22515 | 23307 | 22250 | 20986 | 22478 | 25286 | 25545 | 26004 | 24353
1229 | 1229 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 5 | 15253 | 15939 | 15109 | 15059 | 16645 | 18591 | 19275 | 19801 | 18552 | 19417 | 22059 | 22082 | 22783 | 21343 | 20244 | 21930 | 24596 | 24755 | 25047 | 23218
1230 | 1230 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 6 | 15838 | 16445 | 15106 | 14999 | 16794 | 19140 | 19607 | 19988 | 18180 | 19291 | 22102 | 22157 | 22599 | 20478 | 19549 | 21441 | 24266 | 24322 | 24440 | 22126
1231 | 1231 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 7 | 17133 | 17649 | 15570 | 15331 | 17200 | 20242 | 20678 | 20953 | 18429 | 19540 | 22860 | 22903 | 23176 | 20330 | 19412 | 21428 | 24814 | 24686 | 24865 | 21828
1232 | 1232 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 8 | 18427 | 18865 | 16616 | 16072 | 17574 | 21435 | 22112 | 22183 | 19386 | 19876 | 23934 | 23874 | 24381 | 21158 | 19951 | 21643 | 25655 | 25816 | 25827 | 22594
1233 | 1233 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 9 | 18447 | 19002 | 17257 | 16591 | 17882 | 21410 | 22322 | 22375 | 20005 | 20112 | 24110 | 23716 | 24534 | 21704 | 20375 | 21781 | 25714 | 25935 | 25819 | 23096
1234 | 1234 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 10 | 18156 | 18703 | 17483 | 16893 | 18054 | 21128 | 22191 | 22112 | 20270 | 20326 | 24070 | 23505 | 24363 | 22020 | 20610 | 22038 | 25635 | 25801 | 25703 | 23453
1235 | 1235 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 11 | 17929 | 18343 | 17573 | 16917 | 18098 | 20909 | 22164 | 21782 | 20381 | 20391 | 23988 | 23350 | 23951 | 22178 | 19883 | 22138 | 24834 | 25443 | 25479 | 23648
1236 | 1236 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 12 | 17752 | 18082 | 17607 | 16991 | 18135 | 20684 | 22060 | 21457 | 20404 | 20414 | 23694 | 23136 | 23690 | 22208 | 19433 | 22165 | 24006 | 25196 | 25176 | 23678
1237 | 1237 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 13 | 17683 | 17902 | 17583 | 17044 | 18121 | 20613 | 21866 | 21210 | 20344 | 20375 | 23422 | 23053 | 23365 | 22133 | 19194 | 22099 | 23399 | 24849 | 24864 | 23578
1238 | 1238 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 14 | 17576 | 17735 | 17376 | 16862 | 17840 | 20475 | 21786 | 20975 | 20067 | 20043 | 23038 | 22866 | 23171 | 21801 | 18865 | 21715 | 22865 | 24620 | 24517 | 23217
1239 | 1239 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 15 | 17610 | 17664 | 17290 | 16908 | 17725 | 20524 | 21649 | 20838 | 19918 | 19886 | 22784 | 22871 | 23009 | 21604 | 18860 | 21519 | 22530 | 24417 | 24266 | 22991
1240 | 1240 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 16 | 17967 | 17900 | 17357 | 17278 | 17951 | 20758 | 21744 | 20852 | 19797 | 19977 | 23158 | 22946 | 23222 | 21380 | 19393 | 21534 | 23179 | 24556 | 24051 | 22721
1241 | 1241 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 17 | 18631 | 18580 | 17598 | 18007 | 18606 | 21054 | 21772 | 21182 | 19785 | 20388 | 23478 | 23137 | 23661 | 21372 | 20876 | 21990 | 24257 | 25005 | 24333 | 22730
1242 | 1242 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 18 | 19304 | 19174 | 18299 | 18884 | 19665 | 21671 | 22641 | 21983 | 20524 | 21505 | 24079 | 23781 | 24786 | 22425 | 22342 | 23339 | 25114 | 26273 | 25542 | 23860
1243 | 1243 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 19 | 19730 | 19622 | 18778 | 19377 | 20278 | 22136 | 23112 | 22477 | 21074 | 22083 | 24974 | 24523 | 25720 | 23378 | 23458 | 24285 | 26296 | 27456 | 26598 | 25027
1244 | 1244 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 20 | 19747 | 19408 | 18519 | 19454 | 20270 | 22371 | 23140 | 22384 | 21007 | 22343 | 25569 | 25244 | 26270 | 23648 | 24016 | 24922 | 27365 | 28277 | 27356 | 25465
1245 | 1245 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 21 | 19445 | 19074 | 18324 | 19285 | 20024 | 22261 | 22978 | 22309 | 21138 | 22372 | 26012 | 25717 | 26712 | 24289 | 24558 | 25386 | 28381 | 29035 | 28177 | 26366
1246 | 1246 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 22 | 18683 | 18454 | 17829 | 18751 | 19519 | 21657 | 22365 | 21802 | 20846 | 22050 | 25723 | 25492 | 26438 | 24287 | 24451 | 25301 | 28660 | 28936 | 28172 | 26525
1247 | 1247 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 23 | 17675 | 17596 | 17177 | 18146 | 18814 | 20773 | 21555 | 21148 | 20404 | 21507 | 25027 | 24867 | 25845 | 24023 | 24135 | 24894 | 28316 | 28457 | 27833 | 26351
1248 | 1248 | 52 | 2 | 21 | Winter | 2 | 21 | Winter | 24 | 16566 | 16562 | 16318 | 17390 | 18064 | 19825 | 20772 | 20411 | 19832 | 20992 | 24252 | 24132 | 25213 | 23571 | 23653 | 24428 | 27635 | 27884 | 27326 | 25960
1249 | 1249 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 1 | 15838 | 15534 | 15649 | 17246 | 19096 | 19272 | 20223 | 19439 | 18807 | 22549 | 24022 | 23825 | 24916 | 21905 | 23579 | 26231 | 27786 | 27610 | 26151 | 23936
1250 | 1250 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 2 | 15430 | 15024 | 15246 | 16889 | 18736 | 18891 | 19809 | 18982 | 18454 | 22188 | 23620 | 23374 | 24386 | 21476 | 23190 | 25824 | 27253 | 26999 | 25479 | 23457
1251 | 1251 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 3 | 15305 | 14752 | 14999 | 16796 | 18668 | 18839 | 19651 | 18791 | 18269 | 22131 | 23433 | 23242 | 24147 | 21192 | 23035 | 25623 | 26918 | 26671 | 25123 | 23112
1252 | 1252 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 4 | 15248 | 14534 | 14852 | 16806 | 18619 | 18726 | 19473 | 18481 | 18015 | 21904 | 23072 | 22782 | 23585 | 20658 | 22630 | 25039 | 26224 | 25877 | 24274 | 22431
1253 | 1253 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 5 | 15377 | 14389 | 14747 | 16854 | 18693 | 18720 | 19324 | 18069 | 17720 | 21684 | 22643 | 22362 | 22937 | 19975 | 22150 | 24403 | 25397 | 24959 | 23162 | 21576
1254 | 1254 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 6 | 15891 | 14396 | 14708 | 17302 | 19167 | 19100 | 19578 | 17780 | 17434 | 21776 | 22720 | 22276 | 22612 | 19320 | 22008 | 24095 | 25027 | 24357 | 22071 | 20748
1255 | 1255 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 7 | 17121 | 14854 | 15075 | 18560 | 20393 | 20203 | 20616 | 18115 | 17547 | 22617 | 23450 | 22925 | 23241 | 19216 | 22834 | 24678 | 25374 | 24800 | 21776 | 20535
1256 | 1256 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 8 | 18503 | 15908 | 15826 | 19928 | 21667 | 21640 | 21874 | 19114 | 18209 | 23759 | 24365 | 24147 | 24277 | 19747 | 24048 | 25531 | 26124 | 25749 | 22521 | 21029
1257 | 1257 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 9 | 18682 | 16535 | 16330 | 20096 | 21814 | 21818 | 22062 | 19738 | 18722 | 23952 | 24245 | 24281 | 24314 | 20155 | 24095 | 25583 | 25911 | 25723 | 22999 | 21407
1258 | 1258 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 10 | 18698 | 16936 | 16799 | 20074 | 21773 | 21808 | 21913 | 20114 | 19181 | 24003 | 24125 | 24313 | 24356 | 20602 | 24083 | 25718 | 25804 | 25818 | 23573 | 21896
1259 | 1259 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 11 | 18578 | 17006 | 16766 | 19908 | 21413 | 21600 | 21350 | 19979 | 18959 | 23602 | 23751 | 24054 | 24228 | 20029 | 23438 | 25057 | 25361 | 25752 | 23927 | 21356
1260 | 1260 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 12 | 18563 | 17137 | 16900 | 19910 | 21179 | 21502 | 21027 | 19984 | 18999 | 23278 | 23484 | 23937 | 24064 | 19728 | 23019 | 24387 | 24899 | 25588 | 24107 | 21055
1261 | 1261 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 13 | 18393 | 17040 | 16888 | 19760 | 20860 | 21225 | 20688 | 19822 | 18920 | 22890 | 23231 | 23598 | 23763 | 19480 | 22624 | 23758 | 24482 | 25261 | 23994 | 20791
1262 | 1262 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 14 | 18283 | 16810 | 16665 | 19625 | 20542 | 21102 | 20405 | 19495 | 18637 | 22448 | 22970 | 23394 | 23439 | 19136 | 22347 | 23198 | 24064 | 24897 | 23608 | 20418
1263 | 1263 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 15 | 18241 | 16732 | 16728 | 19599 | 20428 | 21007 | 20314 | 19389 | 18688 | 22248 | 22917 | 23235 | 23227 | 19126 | 22216 | 22865 | 23973 | 24642 | 23375 | 20390
1264 | 1264 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 16 | 18499 | 16817 | 17135 | 19776 | 20933 | 21232 | 20474 | 19431 | 19082 | 22785 | 23085 | 23349 | 22969 | 19543 | 22347 | 23391 | 24187 | 24306 | 22979 | 20780
1265 | 1265 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 17 | 18865 | 17119 | 17987 | 20296 | 21697 | 21545 | 21118 | 19770 | 19806 | 23466 | 23523 | 23560 | 23002 | 20788 | 23154 | 24228 | 25006 | 24353 | 22752 | 22043
1266 | 1266 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 18 | 19547 | 17688 | 18704 | 20950 | 22120 | 22285 | 21758 | 20336 | 20601 | 23894 | 23869 | 24524 | 23978 | 22139 | 24468 | 24995 | 25831 | 25461 | 23786 | 23451
1267 | 1267 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 19 | 20094 | 18154 | 19191 | 21387 | 22818 | 22747 | 22214 | 20830 | 21174 | 24698 | 24743 | 25367 | 24757 | 23195 | 25400 | 26128 | 27142 | 26495 | 24938 | 24659
1268 | 1268 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 20 | 19892 | 17895 | 19237 | 21266 | 23061 | 22734 | 22055 | 20687 | 21398 | 25180 | 25322 | 25819 | 25208 | 23693 | 25808 | 27130 | 28002 | 27230 | 25358 | 25313
1269 | 1269 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 21 | 19510 | 17677 | 19033 | 21007 | 22996 | 22490 | 21895 | 20722 | 21450 | 25501 | 25777 | 26135 | 25668 | 24163 | 26218 | 28089 | 28977 | 28020 | 26240 | 25994
1270 | 1270 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 22 | 18815 | 17162 | 18470 | 20309 | 22355 | 21832 | 21327 | 20361 | 21058 | 25160 | 25508 | 25782 | 25458 | 24017 | 25930 | 28337 | 29026 | 27995 | 26382 | 25970
1271 | 1271 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 23 | 17854 | 16472 | 17833 | 19462 | 21397 | 20970 | 20612 | 19865 | 20583 | 24415 | 24839 | 25153 | 24992 | 23678 | 25337 | 27964 | 28511 | 27641 | 26203 | 25706
1272 | 1272 | 53 | 2 | 22 | Winter | 2 | 22 | Winter | 24 | 16800 | 15563 | 16999 | 18482 | 20301 | 20098 | 19781 | 19188 | 20022 | 23581 | 24051 | 24512 | 24423 | 23185 | 24657 | 27271 | 27839 | 27121 | 25810 | 25258
1273 | 1273 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 1 | 16121 | 15034 | 16905 | 18763 | 19834 | 19633 | 18917 | 18372 | 20130 | 23440 | 23762 | 24250 | 23421 | 23154 | 25834 | 27423 | 26776 | 25992 | 23872 | 25182
1274 | 1274 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 2 | 15673 | 14610 | 16525 | 18370 | 19416 | 19183 | 18421 | 17979 | 19794 | 23019 | 23318 | 23752 | 22825 | 22783 | 25443 | 26903 | 26334 | 25332 | 23395 | 24762
1275 | 1275 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 3 | 15421 | 14332 | 16387 | 18259 | 19233 | 18993 | 18205 | 17772 | 19734 | 22845 | 23162 | 23502 | 22517 | 22603 | 25228 | 26545 | 26514 | 24941 | 23012 | 24532
1276 | 1276 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 4 | 15330 | 14212 | 16427 | 18247 | 19172 | 18871 | 17964 | 17588 | 19673 | 22588 | 22786 | 23034 | 21919 | 22262 | 24705 | 25917 | 26027 | 24124 | 22361 | 24048
1277 | 1277 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 5 | 15351 | 14091 | 16498 | 18351 | 19199 | 18773 | 17620 | 17356 | 19515 | 22246 | 22433 | 22467 | 21096 | 21832 | 24115 | 25136 | 25218 | 23042 | 21515 | 23452
1278 | 1278 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 6 | 15875 | 14074 | 17011 | 18887 | 19743 | 19107 | 17440 | 17167 | 19747 | 22436 | 22392 | 22264 | 20316 | 21765 | 23877 | 24827 | 24739 | 21992 | 20693 | 23225
1279 | 1279 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 7 | 17103 | 14471 | 18295 | 20161 | 20817 | 20185 | 17849 | 17361 | 20888 | 23248 | 23179 | 22977 | 20234 | 22621 | 24505 | 25221 | 25264 | 21720 | 20499 | 23985
1280 | 1280 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 8 | 18275 | 15229 | 19639 | 21440 | 21900 | 21430 | 18849 | 18029 | 22254 | 24174 | 24287 | 24053 | 21069 | 23840 | 25382 | 25989 | 26215 | 22467 | 20990 | 25167
1281 | 1281 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 9 | 18278 | 15648 | 19701 | 21479 | 21794 | 21521 | 19383 | 18472 | 22297 | 23994 | 24282 | 24015 | 21514 | 23793 | 25352 | 25702 | 26161 | 22851 | 21285 | 25083
1282 | 1282 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 10 | 18102 | 16078 | 19642 | 21387 | 21605 | 21355 | 19748 | 18937 | 22295 | 23873 | 24089 | 23938 | 21940 | 23671 | 25385 | 25496 | 25953 | 23320 | 21677 | 24996
1283 | 1283 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 11 | 17908 | 16287 | 19757 | 21312 | 21623 | 21155 | 20010 | 19141 | 22444 | 23952 | 23993 | 23813 | 22256 | 23035 | 24714 | 25045 | 25637 | 23669 | 21130 | 24396
1284 | 1284 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 12 | 17735 | 16438 | 19785 | 21119 | 21444 | 20891 | 20086 | 19268 | 22443 | 23785 | 23792 | 23550 | 22343 | 22523 | 23952 | 24491 | 25219 | 23759 | 20741 | 23881
1285 | 1285 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 13 | 17587 | 16510 | 19737 | 20912 | 21330 | 20678 | 20053 | 19320 | 22370 | 23660 | 23497 | 23295 | 22286 | 22171 | 23366 | 24121 | 24645 | 23691 | 20519 | 23524
1286 | 1286 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 14 | 17507 | 16439 | 19738 | 20751 | 21266 | 20545 | 19877 | 19187 | 22312 | 23553 | 23296 | 23084 | 22042 | 22003 | 22916 | 23811 | 24673 | 23408 | 20248 | 23325
1287 | 1287 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 15 | 17479 | 16525 | 19736 | 20679 | 21259 | 20477 | 19786 | 19244 | 22257 | 23505 | 23223 | 22933 | 21891 | 21928 | 22641 | 23773 | 24758 | 23226 | 20269 | 23226
1288 | 1288 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 16 | 17695 | 16876 | 19855 | 21081 | 21384 | 20522 | 19684 | 19464 | 22202 | 23481 | 23163 | 22781 | 21637 | 22158 | 23258 | 24077 | 24883 | 22914 | 20735 | 23421
1289 | 1289 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 17 | 18232 | 17526 | 20164 | 21591 | 21473 | 20814 | 19614 | 19731 | 22157 | 23387 | 23150 | 22887 | 21468 | 23040 | 24168 | 24959 | 25801 | 22765 | 22068 | 24319
1290 | 1290 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 18 | 18660 | 18198 | 20751 | 22020 | 21876 | 21442 | 20145 | 20486 | 22805 | 23672 | 23983 | 23761 | 22357 | 24270 | 24875 | 25716 | 26388 | 23758 | 23442 | 25618
1291 | 1291 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 19 | 19071 | 18687 | 21191 | 22708 | 22553 | 21888 | 20618 | 21026 | 23132 | 24450 | 24756 | 24441 | 23210 | 25156 | 25954 | 26975 | 27405 | 24879 | 24627 | 26637
1292 | 1292 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 20 | 18826 | 18679 | 21051 | 22906 | 22711 | 21688 | 20423 | 21184 | 23231 | 24936 | 25305 | 24805 | 23401 | 25514 | 26895 | 27784 | 28101 | 25300 | 25280 | 27143
1293 | 1293 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 21 | 18478 | 18482 | 20774 | 22797 | 22653 | 21478 | 20387 | 21188 | 23189 | 25289 | 25512 | 25169 | 23956 | 25874 | 27800 | 28714 | 28804 | 26166 | 25965 | 27699
1294 | 1294 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 22 | 17844 | 17915 | 20057 | 22116 | 22022 | 20859 | 19962 | 20750 | 22633 | 24952 | 25213 | 24883 | 23878 | 25536 | 28000 | 28719 | 28813 | 26282 | 25942 | 27483
1295 | 1295 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 23 | 16979 | 17247 | 19183 | 21133 | 21090 | 20105 | 19428 | 20233 | 21931 | 24237 | 24599 | 24381 | 23580 | 24920 | 27603 | 28185 | 28270 | 26092 | 25666 | 26932
1296 | 1296 | 54 | 2 | 23 | Winter | 2 | 23 | Winter | 24 | 15922 | 16396 | 18179 | 20015 | 20089 | 19250 | 18730 | 19639 | 21201 | 23485 | 23961 | 23764 | 23106 | 24230 | 26882 | 27487 | 27451 | 25679 | 25197 | 26272
1297 | 1297 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 1 | 14611 | 15878 | 18005 | 19108 | 19103 | 17963 | 17569 | 19286 | 21664 | 22759 | 23403 | 22433 | 21228 | 25100 | 26675 | 26065 | 26556 | 23408 | 24747 | 27290
1298 | 1298 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 2 | 14081 | 15492 | 17600 | 18662 | 18679 | 17448 | 17158 | 18936 | 21251 | 22331 | 22936 | 21853 | 20803 | 24659 | 26160 | 25626 | 26092 | 22919 | 24322 | 26847
1299 | 1299 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 3 | 13783 | 15357 | 17475 | 18469 | 18559 | 17221 | 16948 | 18876 | 21196 | 22210 | 22729 | 21574 | 20505 | 24471 | 25827 | 25821 | 26058 | 22549 | 24099 | 26583
1300 | 1300 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 4 | 13598 | 15382 | 17470 | 18421 | 18472 | 17006 | 16795 | 18854 | 21059 | 21915 | 22312 | 21039 | 20045 | 24009 | 25237 | 25376 | 25476 | 21911 | 23623 | 25944
1301 | 1301 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 5 | 13472 | 15495 | 17604 | 18492 | 18495 | 16722 | 16628 | 18769 | 20928 | 21665 | 21924 | 20308 | 19444 | 23500 | 24522 | 24621 | 24797 | 21089 | 23038 | 25209
1302 | 1302 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 6 | 13512 | 16017 | 18150 | 19063 | 18871 | 16594 | 16506 | 19080 | 21130 | 21724 | 21801 | 19622 | 18851 | 23301 | 24253 | 24181 | 24319 | 20282 | 22807 | 24813
1303 | 1303 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 7 | 14023 | 17333 | 19507 | 20219 | 20075 | 17082 | 16795 | 20325 | 22091 | 22632 | 22689 | 19654 | 18848 | 23965 | 24729 | 24772 | 24866 | 20136 | 23604 | 25359
1304 | 1304 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 8 | 15066 | 18696 | 20808 | 21317 | 21349 | 18083 | 17474 | 21710 | 23236 | 23764 | 23985 | 20517 | 19393 | 24904 | 25528 | 25723 | 25948 | 20622 | 24783 | 26146
1305 | 1305 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 9 | 15863 | 19019 | 21126 | 21500 | 21658 | 18879 | 18190 | 22038 | 23610 | 24039 | 24224 | 21252 | 20000 | 25119 | 25533 | 25946 | 26023 | 21184 | 24963 | 26362
1306 | 1306 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 10 | 16382 | 19110 | 21185 | 21472 | 21569 | 19393 | 18805 | 22189 | 23817 | 23985 | 24282 | 21829 | 20507 | 25253 | 25486 | 25892 | 25392 | 21731 | 25040 | 26594
1307 | 1307 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 11 | 16705 | 19279 | 21153 | 21525 | 21445 | 19695 | 19048 | 22380 | 23910 | 23932 | 24191 | 22183 | 19971 | 24603 | 25066 | 25609 | 24975 | 21228 | 24480 | 26018
1308 | 1308 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 12 | 16934 | 19414 | 21069 | 21446 | 21328 | 19868 | 19269 | 22479 | 23777 | 23824 | 24045 | 22366 | 19675 | 23947 | 24615 | 25290 | 24784 | 20934 | 24067 | 25353
1309 | 1309 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 13 | 16813 | 19267 | 20774 | 21230 | 20970 | 19736 | 19221 | 22299 | 23425 | 23436 | 23777 | 22209 | 19351 | 23313 | 24138 | 24620 | 24378 | 20604 | 23601 | 24650
1310 | 1310 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 14 | 16654 | 19208 | 20577 | 21108 | 20789 | 19512 | 19033 | 22188 | 23091 | 23190 | 23449 | 21917 | 19053 | 22841 | 23774 | 24595 | 23854 | 20277 | 23351 | 24111
1311 | 1311 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 15 | 16529 | 19132 | 20441 | 21028 | 20717 | 19351 | 19016 | 22061 | 22826 | 23044 | 23194 | 21696 | 19015 | 22522 | 23660 | 24611 | 23563 | 20218 | 23173 | 23720
1312 | 1312 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 16 | 16435 | 19138 | 20663 | 21023 | 20721 | 19134 | 19112 | 21887 | 23022 | 22866 | 22908 | 21315 | 19369 | 23056 | 23819 | 24595 | 23366 | 20535 | 23219 | 24157
1313 | 1313 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 17 | 16445 | 19383 | 21118 | 21064 | 20932 | 19019 | 19318 | 21785 | 23106 | 22733 | 22786 | 21032 | 20573 | 24135 | 24587 | 25404 | 24241 | 21760 | 24015 | 24969
1314 | 1314 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 18 | 16914 | 19909 | 21522 | 21447 | 21539 | 19520 | 20013 | 22360 | 23472 | 23477 | 23516 | 21822 | 21818 | 25035 | 25284 | 25931 | 25392 | 23096 | 25257 | 25657
1315 | 1315 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 19 | 17327 | 20346 | 22191 | 22090 | 22021 | 19968 | 20520 | 22648 | 24186 | 24131 | 24157 | 22579 | 22779 | 26201 | 26473 | 26886 | 26720 | 24255 | 26254 | 26841
1316 | 1316 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 20 | 17088 | 20201 | 22373 | 22227 | 22191 | 19766 | 20661 | 22713 | 24598 | 24598 | 24478 | 22711 | 23240 | 27058 | 27239 | 27559 | 27283 | 24919 | 26782 | 27973
1317 | 1317 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 21 | 16899 | 19936 | 22261 | 22159 | 21954 | 19706 | 20637 | 22627 | 24868 | 24704 | 24799 | 23194 | 23698 | 27836 | 28131 | 28231 | 28138 | 25630 | 27362 | 29094
1318 | 1318 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 22 | 16366 | 19203 | 21548 | 21510 | 21364 | 19244 | 20153 | 22014 | 24445 | 24344 | 24493 | 23057 | 23499 | 27720 | 28103 | 28212 | 28156 | 25584 | 27138 | 29417
1319 | 1319 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 23 | 15674 | 18310 | 20544 | 20552 | 20535 | 18682 | 19608 | 21287 | 23666 | 23688 | 23839 | 22730 | 23141 | 27097 | 27556 | 27658 | 27532 | 25312 | 26595 | 29111
1320 | 1320 | 55 | 2 | 24 | Winter | 2 | 24 | Winter | 24 | 14744 | 17271 | 19344 | 19489 | 19614 | 17901 | 18941 | 20479 | 22805 | 23017 | 23135 | 22198 | 22597 | 26284 | 26826 | 26813 | 26621 | 24811 | 25913 | 28412
1321 | 1321 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 1 | 14358 | 17451 | 18854 | 18871 | 19250 | 17232 | 19003 | 21229 | 22629 | 22874 | 22381 | 20933 | 22710 | 26381 | 25850 | 26405 | 25401 | 24867 | 27384 | 28768
1322 | 1322 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 2 | 13966 | 17103 | 18454 | 18488 | 18863 | 16871 | 18707 | 20884 | 22272 | 22510 | 21837 | 20544 | 22357 | 25899 | 25442 | 25971 | 24829 | 24452 | 26969 | 28224
1323 | 1323 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 3 | 13680 | 16941 | 18229 | 18335 | 18663 | 16626 | 18617 | 20800 | 22093 | 22312 | 21581 | 20258 | 22194 | 25575 | 25645 | 25941 | 24766 | 24220 | 26697 | 27825
1324 | 1324 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 4 | 13559 | 16935 | 18181 | 18254 | 18529 | 16478 | 18612 | 20695 | 21883 | 21960 | 21118 | 19852 | 21895 | 25037 | 25241 | 25392 | 24175 | 23750 | 26066 | 27103
1325 | 1325 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 5 | 13448 | 17073 | 18271 | 18314 | 18557 | 16354 | 18580 | 20640 | 21636 | 21668 | 20452 | 19320 | 21527 | 24386 | 24542 | 24761 | 23183 | 23182 | 25346 | 26223
1326 | 1326 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 6 | 13406 | 17623 | 18823 | 18705 | 18881 | 16242 | 18913 | 20900 | 21866 | 21614 | 19878 | 18781 | 21474 | 24154 | 24131 | 24309 | 22255 | 22934 | 24950 | 25771
1327 | 1327 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 7 | 13818 | 18985 | 19955 | 19902 | 20019 | 16525 | 20187 | 21910 | 22765 | 22551 | 19864 | 18797 | 22374 | 24643 | 24726 | 24844 | 21959 | 23712 | 25455 | 26059
1328 | 1328 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 8 | 14588 | 20324 | 21055 | 21175 | 21444 | 17211 | 21603 | 23124 | 23741 | 23897 | 20550 | 19358 | 23597 | 25462 | 25693 | 25924 | 22454 | 24881 | 26230 | 26745
1329 | 1329 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 9 | 15086 | 20441 | 21066 | 21281 | 21627 | 17728 | 21755 | 23323 | 23673 | 23960 | 21069 | 19793 | 23652 | 25301 | 25726 | 25818 | 22736 | 24889 | 26242 | 26513
1330 | 1330 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 10 | 15596 | 20399 | 20944 | 21079 | 21486 | 18193 | 21746 | 23345 | 23534 | 23815 | 21418 | 20274 | 23673 | 25229 | 25654 | 25155 | 22542 | 24943 | 26450 | 26483
1331 | 1331 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 11 | 15510 | 19989 | 20571 | 20460 | 20776 | 17805 | 21231 | 22687 | 22837 | 22879 | 21016 | 19711 | 23051 | 24782 | 25344 | 24714 | 22648 | 24351 | 25859 | 26074
1332 | 1332 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 12 | 15507 | 19651 | 20196 | 19995 | 20226 | 17597 | 20854 | 22039 | 22225 | 22168 | 20711 | 19373 | 22598 | 24278 | 24974 | 24488 | 22828 | 23904 | 25152 | 25579
1333 | 1333 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 13 | 15449 | 19328 | 19938 | 19582 | 19881 | 17440 | 20543 | 21542 | 21831 | 21725 | 20366 | 19131 | 22221 | 23890 | 24388 | 24153 | 22596 | 23516 | 24534 | 25179
1334 | 1334 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 14 | 15280 | 19103 | 19766 | 19358 | 19556 | 17190 | 20367 | 21140 | 21585 | 21322 | 20001 | 18819 | 21976 | 23503 | 24347 | 23612 | 22111 | 23239 | 23970 | 24761
1335 | 1335 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 15 | 15409 | 19130 | 19816 | 19428 | 19512 | 17310 | 20380 | 21024 | 21601 | 21215 | 19928 | 18905 | 21941 | 23513 | 24486 | 23445 | 22006 | 23178 | 23701 | 24747
1336 | 1336 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 16 | 15825 | 19569 | 20083 | 19742 | 19747 | 17768 | 20592 | 21604 | 21862 | 21386 | 20087 | 19336 | 22090 | 23746 | 24553 | 23322 | 21916 | 23282 | 24207 | 24942
1337 | 1337 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 17 | 16806 | 20542 | 20717 | 20637 | 20578 | 18815 | 21394 | 22674 | 22687 | 22301 | 20858 | 20566 | 22892 | 24541 | 25387 | 24235 | 22768 | 24104 | 25048 | 25756
1338 | 1338 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 18 | 17570 | 21124 | 21332 | 21460 | 21394 | 19817 | 22285 | 23388 | 23297 | 23370 | 21886 | 21774 | 24084 | 25225 | 25906 | 25376 | 23807 | 25378 | 25755 | 26537
1339 | 1339 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 19 | 18097 | 21879 | 22077 | 22046 | 22035 | 20464 | 22708 | 24221 | 24161 | 24089 | 22697 | 22683 | 24889 | 26366 | 26828 | 26681 | 25001 | 26377 | 26936 | 27876
1340 | 1340 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 20 | 18027 | 21948 | 22108 | 22094 | 21802 | 20490 | 22633 | 24456 | 24457 | 24180 | 22719 | 23044 | 25186 | 27032 | 27403 | 27168 | 25402 | 26865 | 28032 | 28784
1341 | 1341 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 21 | 17821 | 21754 | 21972 | 21795 | 21607 | 20393 | 22472 | 24597 | 24712 | 24360 | 22998 | 23391 | 25492 | 27821 | 27991 | 27940 | 26182 | 27409 | 29103 | 29858
1342 | 1342 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 22 | 17254 | 21098 | 21367 | 21270 | 21009 | 19886 | 21902 | 24187 | 24328 | 24060 | 22834 | 23151 | 25128 | 27819 | 27999 | 27999 | 26326 | 27255 | 29485 | 30040
1343 | 1343 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 23 | 16535 | 20038 | 20352 | 20372 | 20079 | 19260 | 21084 | 23313 | 23525 | 23309 | 22475 | 22734 | 24467 | 27213 | 27393 | 27328 | 26034 | 26679 | 29144 | 29526
1344 | 1344 | 56 | 2 | 25 | Winter | 2 | 25 | Winter | 24 | 15685 | 18799 | 19208 | 19374 | 19131 | 18572 | 20183 | 22348 | 22719 | 22539 | 22000 | 22221 | 23784 | 26454 | 26517 | 26398 | 25379 | 25967 | 28436 | 28824
1345 | 1345 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 1 | 15357 | 17981 | 18292 | 18707 | 18114 | 18347 | 20549 | 21873 | 22111 | 21591 | 21526 | 22043 | 24740 | 25186 | 25796 | 24893 | 24116 | 27079 | 28490 | 27597
1346 | 1346 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 2 | 15007 | 17559 | 17905 | 18300 | 17593 | 18034 | 20189 | 21505 | 21753 | 21069 | 21214 | 21701 | 24326 | 24785 | 25378 | 24329 | 23764 | 26658 | 27939 | 27136
1347 | 1347 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 3 | 14877 | 17341 | 17768 | 18104 | 17381 | 17953 | 20123 | 21349 | 21646 | 20871 | 21128 | 21581 | 24173 | 25035 | 25385 | 24304 | 23878 | 26418 | 27570 | 27312
1348 | 1348 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 4 | 14885 | 17272 | 17685 | 17974 | 17187 | 17953 | 20042 | 21180 | 21390 | 20469 | 20852 | 21330 | 23748 | 24675 | 24871 | 23735 | 23572 | 25778 | 26844 | 26762
1349 | 1349 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 5 | 14990 | 17383 | 17754 | 18018 | 16917 | 17942 | 20031 | 20991 | 21210 | 19869 | 20484 | 21001 | 23291 | 24024 | 24282 | 22769 | 22967 | 25066 | 25953 | 25889
1350 | 1350 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 6 | 15496 | 17957 | 18202 | 18415 | 16867 | 18341 | 20387 | 21326 | 21344 | 19408 | 20162 | 21046 | 23170 | 23686 | 23912 | 21899 | 22323 | 24710 | 25535 | 25333
1351 | 1351 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 7 | 16758 | 19118 | 19425 | 19568 | 17288 | 19628 | 21462 | 22279 | 22293 | 19461 | 20213 | 21990 | 23822 | 24318 | 24470 | 21622 | 22093 | 25222 | 25820 | 25818
1352 | 1352 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 8 | 18197 | 20333 | 20761 | 21066 | 18089 | 21108 | 22793 | 23373 | 23549 | 20203 | 20427 | 23316 | 24879 | 25385 | 25645 | 22144 | 22201 | 26092 | 26601 | 26809
1353 | 1353 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 9 | 18202 | 20238 | 20750 | 21106 | 18496 | 21111 | 22866 | 23197 | 23513 | 20615 | 20668 | 23255 | 24772 | 25296 | 25419 | 22293 | 22322 | 25969 | 26238 | 26704
1354 | 1354 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 10 | 17948 | 19870 | 20311 | 20712 | 18571 | 20842 | 22614 | 22799 | 23020 | 20697 | 20833 | 23008 | 24607 | 24961 | 24491 | 21834 | 21924 | 25913 | 25945 | 26398
1355 | 1355 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 11 | 17624 | 19417 | 19625 | 19945 | 18256 | 20249 | 21857 | 22023 | 22012 | 20155 | 20344 | 22247 | 23802 | 24500 | 23907 | 21802 | 21708 | 25178 | 25401 | 25994
1356 | 1356 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 12 | 17474 | 19049 | 19181 | 19404 | 18078 | 19880 | 21209 | 21396 | 21325 | 19812 | 20039 | 21752 | 23067 | 24088 | 23637 | 21956 | 21773 | 24430 | 24874 | 25602
1357 | 1357 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 13 | 17263 | 18771 | 18766 | 19045 | 17794 | 19550 | 20691 | 20979 | 20732 | 19420 | 19738 | 21336 | 22472 | 23466 | 23262 | 21674 | 21578 | 23772 | 24424 | 24942
1358 | 1358 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 14 | 17204 | 18650 | 18594 | 18783 | 17548 | 19433 | 20357 | 20791 | 20456 | 19108 | 19455 | 21146 | 22028 | 23482 | 22780 | 21237 | 21167 | 23260 | 24060 | 24921
1359 | 1359 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 15 | 17261 | 18711 | 18672 | 18755 | 17522 | 19462 | 20262 | 20819 | 20466 | 19048 | 19438 | 21126 | 21843 | 23639 | 22625 | 21144 | 21117 | 23001 | 24053 | 25038
1360 | 1360 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 16 | 17660 | 19133 | 19151 | 19163 | 17885 | 19848 | 20988 | 21257 | 20902 | 19395 | 19827 | 21464 | 22623 | 23888 | 22690 | 21233 | 21312 | 23681 | 24419 | 25224
1361 | 1361 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 17 | 18586 | 19972 | 20252 | 20214 | 18770 | 20870 | 22281 | 22295 | 22040 | 20390 | 20820 | 22494 | 23976 | 24958 | 23837 | 22316 | 22437 | 24764 | 25477 | 26299
1362 | 1362 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 18 | 19421 | 20728 | 21148 | 21113 | 19564 | 21887 | 23122 | 23022 | 23274 | 21512 | 22033 | 23777 | 25006 | 25595 | 25091 | 23492 | 23890 | 25615 | 26372 | 27060
1363 | 1363 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 19 | 19974 | 21500 | 21762 | 21779 | 20162 | 22348 | 23972 | 23883 | 24086 | 22279 | 23252 | 24564 | 26145 | 26500 | 26376 | 24684 | 25540 | 26818 | 27736 | 28121
1364 | 1364 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 20 | 19764 | 21503 | 21800 | 21540 | 19945 | 22268 | 24167 | 24119 | 24340 | 22198 | 23547 | 24799 | 26917 | 27007 | 26824 | 25045 | 26017 | 27899 | 28643 | 28883
1365 | 1365 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 21 | 19490 | 21328 | 21501 | 21314 | 19772 | 22084 | 24249 | 24293 | 24354 | 22388 | 23785 | 25045 | 27590 | 27530 | 27542 | 25793 | 26663 | 28969 | 29722 | 29655
1366 | 1366 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 22 | 18780 | 20636 | 20882 | 20694 | 19315 | 21413 | 23703 | 23843 | 23932 | 22152 | 23414 | 24629 | 27419 | 27440 | 27492 | 25899 | 26527 | 29262 | 29825 | 29717
1367 | 1367 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 23 | 17822 | 19583 | 19954 | 19739 | 18729 | 20566 | 22781 | 22987 | 23170 | 21749 | 22894 | 23937 | 26739 | 26811 | 26800 | 25588 | 26046 | 28912 | 29317 | 29169
1368 | 1368 | 57 | 2 | 26 | Winter | 2 | 26 | Winter | 24 | 16712 | 18389 | 18882 | 18661 | 17970 | 19598 | 21742 | 22037 | 22376 | 21227 | 22407 | 23152 | 25889 | 25901 | 25839 | 24900 | 25377 | 28177 | 28594 | 28310
1369 | 1369 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 1 | 16645 | 17511 | 18229 | 17700 | 17836 | 19948 | 21256 | 21443 | 22011 | 20936 | 22321 | 24122 | 25731 | 25231 | 24425 | 23761 | 24866 | 28280 | 27441 | 27675
1370 | 1370 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 2 | 16322 | 17148 | 17843 | 17184 | 17512 | 19598 | 20902 | 21105 | 21671 | 20668 | 22127 | 23743 | 25279 | 24844 | 23896 | 23443 | 24658 | 27753 | 27002 | 27226
1371 | 1371 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 3 | 16182 | 16994 | 17640 | 16962 | 17396 | 19524 | 20749 | 21006 | 21510 | 20614 | 22180 | 23615 | 25005 | 24879 | 23893 | 23574 | 24906 | 27392 | 27185 | 27181
1372 | 1372 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 4 | 16160 | 16906 | 17510 | 16769 | 17303 | 19455 | 20607 | 20793 | 21202 | 20384 | 22012 | 23242 | 24501 | 24415 | 23362 | 23283 | 24725 | 26672 | 26626 | 26520
1373 | 1373 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 5 | 16288 | 17002 | 17590 | 16543 | 17301 | 19498 | 20496 | 20701 | 20989 | 20092 | 21899 | 22867 | 23909 | 23886 | 22457 | 22721 | 24346 | 25809 | 25769 | 25771
1374 | 1374 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 6 | 16825 | 17439 | 17998 | 16505 | 17324 | 19869 | 20891 | 20909 | 21028 | 19815 | 22080 | 22783 | 23755 | 23552 | 21609 | 22075 | 24226 | 25396 | 25191 | 25204
1375 | 1375 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 7 | 18225 | 18698 | 19193 | 16968 | 17605 | 21013 | 21908 | 21944 | 22036 | 19931 | 23106 | 23532 | 24294 | 24167 | 21381 | 21871 | 25093 | 25710 | 25689 | 25672
1376 | 1376 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 8 | 19660 | 20047 | 20679 | 17764 | 17912 | 22366 | 23032 | 23231 | 23488 | 20173 | 24349 | 24632 | 25221 | 25353 | 21919 | 21984 | 26214 | 26489 | 26667 | 26782
1377 | 1377 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 9 | 19614 | 19982 | 20698 | 18146 | 18185 | 22410 | 22832 | 23184 | 23400 | 20415 | 24234 | 24531 | 24908 | 25105 | 22052 | 22083 | 25908 | 26095 | 26536 | 26479
1378 | 1378 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 10 | 19350 | 19598 | 20355 | 18269 | 18405 | 22182 | 22462 | 22731 | 23023 | 20612 | 23900 | 24389 | 24593 | 24194 | 21620 | 21715 | 25004 | 25821 | 26262 | 25637
1379 | 1379 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 11 | 18907 | 19070 | 19766 | 18124 | 18270 | 21553 | 21837 | 21874 | 22088 | 20218 | 23185 | 23660 | 24114 | 23705 | 21681 | 21597 | 24789 | 25382 | 25955 | 25179
1380 | 1380 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 12 | 18626 | 18739 | 19339 | 18053 | 18213 | 21011 | 21295 | 21274 | 21411 | 19973 | 22666 | 22978 | 23631 | 23493 | 21886 | 21716 | 24716 | 24918 | 25621 | 24983
1381 | 1381 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 13 | 18285 | 18373 | 19022 | 17812 | 18046 | 20535 | 20913 | 20722 | 20957 | 19691 | 22252 | 22403 | 23210 | 23143 | 21624 | 21539 | 24281 | 24487 | 24981 | 24622
1382 | 1382 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 14 | 18156 | 18246 | 18798 | 17601 | 17869 | 20249 | 20762 | 20486 | 20638 | 19439 | 22051 | 21997 | 22900 | 22688 | 21215 | 21157 | 23889 | 24144 | 24981 | 24135
1383 | 1383 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 15 | 18218 | 18320 | 18780 | 17582 | 17908 | 20177 | 20801 | 20512 | 20552 | 19433 | 22038 | 21830 | 22925 | 22546 | 21131 | 21115 | 23816 | 24144 | 25100 | 23953
1384 | 1384 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 16 | 18733 | 18722 | 19122 | 17869 | 18255 | 20829 | 21177 | 20888 | 20841 | 19766 | 22383 | 22528 | 23278 | 22560 | 21161 | 21248 | 23927 | 24440 | 25219 | 23898
1385 | 1385 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 17 | 19802 | 19695 | 20024 | 18609 | 18942 | 21986 | 22087 | 21888 | 21860 | 20633 | 23129 | 23756 | 24193 | 23582 | 22123 | 22253 | 24830 | 25374 | 26181 | 24927
1386 | 1386 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 18 | 20487 | 20494 | 20812 | 19320 | 19926 | 22801 | 22755 | 23010 | 22990 | 21768 | 24147 | 24718 | 24944 | 24773 | 23244 | 23658 | 25846 | 26238 | 26899 | 26249
1387 | 1387 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 19 | 21261 | 21110 | 21469 | 19893 | 20929 | 23632 | 23580 | 23761 | 23684 | 22898 | 25032 | 25793 | 26041 | 26005 | 24377 | 25270 | 27187 | 27587 | 27959 | 27646
1388 | 1388 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 20 | 21284 | 21123 | 21210 | 19659 | 20981 | 23782 | 23766 | 23946 | 23702 | 23102 | 25384 | 26472 | 26649 | 26377 | 24683 | 25709 | 27847 | 28480 | 28705 | 28241
1389 | 1389 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 21 | 21076 | 20788 | 20922 | 19419 | 20820 | 23787 | 23832 | 23847 | 23763 | 23231 | 25534 | 27028 | 27320 | 26992 | 25337 | 26289 | 28392 | 29503 | 29448 | 29127
1390 | 1390 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 22 | 20342 | 20161 | 20283 | 18946 | 20236 | 23199 | 23317 | 23371 | 23331 | 22808 | 24979 | 26810 | 27198 | 26898 | 25408 | 26134 | 28057 | 29582 | 29506 | 29191
1391 | 1391 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 23 | 19261 | 19221 | 19321 | 18357 | 19521 | 22244 | 22433 | 22568 | 22539 | 22269 | 24146 | 26099 | 26582 | 26192 | 25095 | 25656 | 27273 | 29068 | 28968 | 28560
1392 | 1392 | 58 | 2 | 27 | Winter | 2 | 27 | Winter | 24 | 17996 | 18113 | 18197 | 17565 | 18832 | 21157 | 21436 | 21723 | 21700 | 21770 | 23349 | 25230 | 25801 | 25217 | 24410 | 24983 | 26252 | 28339 | 28110 | 27635
1393 | 1393 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 1 | 17226 | 17477 | 17235 | 17426 | 18640 | 20603 | 20818 | 21347 | 20868 | 21738 | 23363 | 25013 | 24585 | 23836 | 23318 | 24467 | 26210 | 27192 | 27491 | 26163
1394 | 1394 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 2 | 16825 | 17051 | 16708 | 17070 | 18401 | 20223 | 20457 | 20988 | 20359 | 21551 | 22970 | 24571 | 24219 | 23315 | 23005 | 24260 | 25789 | 26741 | 27034 | 25586
1395 | 1395 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 3 | 16613 | 16842 | 16477 | 16934 | 18416 | 20058 | 20360 | 20829 | 20169 | 21624 | 22777 | 24332 | 24508 | 23341 | 23160 | 24526 | 25804 | 26937 | 27010 | 25551
1396 | 1396 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 4 | 16548 | 16733 | 16314 | 16857 | 18451 | 19960 | 20206 | 20595 | 19836 | 21531 | 22450 | 23907 | 24205 | 22868 | 22907 | 24385 | 25362 | 26411 | 26369 | 24894
1397 | 1397 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 5 | 16673 | 16805 | 16102 | 16862 | 18582 | 19887 | 20165 | 20446 | 19314 | 21469 | 22137 | 23380 | 23619 | 22011 | 22370 | 24022 | 24802 | 25564 | 25614 | 23817
1398 | 1398 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 6 | 17241 | 17259 | 16128 | 16938 | 19092 | 20364 | 20480 | 20603 | 18933 | 21743 | 22202 | 23332 | 23351 | 21247 | 21793 | 23953 | 24591 | 25030 | 25071 | 22845
1399 | 1399 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 7 | 18424 | 18473 | 16640 | 17241 | 20435 | 21444 | 21581 | 21700 | 19075 | 22832 | 22950 | 23938 | 24055 | 21075 | 21623 | 24836 | 24998 | 25533 | 25542 | 22488
1400 | 1400 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 8 | 19613 | 19933 | 17436 | 17522 | 21773 | 22566 | 22872 | 23168 | 19825 | 24071 | 23911 | 24888 | 25120 | 21611 | 21729 | 25955 | 25666 | 26506 | 26634 | 22954
1401 | 1401 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 9 | 19538 | 20002 | 17878 | 17843 | 21759 | 22421 | 22886 | 23160 | 20285 | 24032 | 23866 | 24652 | 25061 | 21799 | 21883 | 25702 | 25431 | 26414 | 26387 | 23106
1402 | 1402 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 10 | 19308 | 19779 | 18122 | 18189 | 21543 | 22156 | 22543 | 22897 | 20509 | 23805 | 23789 | 24422 | 24843 | 21453 | 21607 | 24897 | 24832 | 26240 | 25626 | 22805
1403 | 1403 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 11 | 19050 | 19335 | 18155 | 18253 | 21222 | 21746 | 21908 | 22205 | 20305 | 23319 | 23450 | 23920 | 24464 | 21491 | 21471 | 24660 | 24789 | 25906 | 25158 | 22883
1404 | 1404 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 12 | 18767 | 18972 | 18150 | 18280 | 20931 | 21296 | 21394 | 21628 | 20118 | 22885 | 23015 | 23397 | 24066 | 21659 | 21547 | 24542 | 24701 | 25523 | 24909 | 23047
1405 | 1405 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 13 | 18490 | 18652 | 17909 | 18118 | 20610 | 20915 | 20844 | 21178 | 19740 | 22459 | 22552 | 22942 | 23421 | 21363 | 21337 | 24074 | 24335 | 24851 | 24512 | 22740
1406 | 1406 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 14 | 18292 | 18338 | 17596 | 17833 | 20352 | 20641 | 20481 | 20721 | 19309 | 22105 | 22122 | 22574 | 23397 | 20896 | 20891 | 23619 | 23855 | 24786 | 23963 | 22241
1407 | 1407 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 15 | 18378 | 18355 | 17595 | 17905 | 20405 | 20714 | 20550 | 20680 | 19293 | 22134 | 22025 | 22612 | 23571 | 20819 | 20859 | 23552 | 23672 | 24918 | 23789 | 22142
1408 | 1408 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 16 | 18822 | 18774 | 17964 | 18342 | 20868 | 21193 | 21040 | 21082 | 19691 | 22607 | 22624 | 23049 | 23834 | 20927 | 21064 | 23740 | 24008 | 25106 | 23798 | 22209
1409 | 1409 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 17 | 19532 | 19638 | 18665 | 18989 | 21561 | 22057 | 21988 | 22045 | 20511 | 23301 | 23333 | 23980 | 24808 | 21913 | 22091 | 24673 | 24774 | 26092 | 24853 | 23218
1410 | 1410 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 18 | 20110 | 20253 | 19138 | 19748 | 22134 | 22506 | 22826 | 22860 | 21301 | 24014 | 23910 | 24642 | 25315 | 22942 | 23411 | 25606 | 25514 | 26735 | 26103 | 24334
1411 | 1411 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 19 | 20807 | 20840 | 19617 | 20650 | 22679 | 23211 | 23441 | 23396 | 21878 | 24692 | 24666 | 25651 | 26128 | 24012 | 24977 | 26905 | 26906 | 27773 | 27492 | 25580
1412 | 1412 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 20 | 20770 | 20562 | 19363 | 20676 | 22800 | 23341 | 23559 | 23319 | 21702 | 24943 | 25130 | 26162 | 26560 | 24259 | 25370 | 27535 | 27696 | 28508 | 28075 | 26027
1413 | 1413 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 21 | 20526 | 20252 | 19088 | 20493 | 22594 | 23337 | 23386 | 23282 | 21756 | 25002 | 25433 | 26743 | 26980 | 24838 | 25903 | 28040 | 28493 | 29243 | 28957 | 26870
1414 | 1414 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 22 | 19806 | 19602 | 18590 | 19895 | 21835 | 22763 | 22855 | 22796 | 21456 | 24386 | 25112 | 26541 | 26827 | 24860 | 25710 | 27678 | 28473 | 29285 | 29023 | 27042
1415 | 1415 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 23 | 18781 | 18636 | 17998 | 19191 | 20879 | 21882 | 22057 | 21991 | 21063 | 23565 | 24419 | 25905 | 26199 | 24521 | 25219 | 26892 | 27813 | 28774 | 28409 | 26792
1416 | 1416 | 59 | 2 | 28 | Winter | 2 | 28 | Winter | 24 | 17605 | 17483 | 17168 | 18474 | 19885 | 20847 | 21164 | 21101 | 20508 | 22762 | 23721 | 25103 | 25284 | 23823 | 24553 | 25878 | 26954 | 27902 | 27484 | 26149
1417 | 1417 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 1 | 16699 | 16134 | 16601 | 17762 | 19344 | 19552 | 20050 | 19498 | 20262 | 21889 | 22698 | 23826 | 24603 | 22788 | 24022 | 25778 | 26428 | 27239 | 25965 | 24852
1418 | 1418 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 2 | 16350 | 15651 | 16278 | 17555 | 18944 | 19248 | 19759 | 19066 | 19985 | 21608 | 22390 | 23489 | 24232 | 22493 | 23830 | 25367 | 25925 | 26790 | 25403 | 24526
1419 | 1419 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 3 | 16174 | 15585 | 16348 | 17819 | 18737 | 19486 | 19993 | 19302 | 19905 | 21940 | 22596 | 23793 | 24266 | 22649 | 24095 | 25389 | 25982 | 26748 | 25352 | 24633
1420 | 1420 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 4 | 16114 | 15520 | 16398 | 18002 | 18674 | 19547 | 20008 | 19244 | 19744 | 21935 | 22450 | 23571 | 23878 | 22440 | 23989 | 24984 | 25437 | 26139 | 24706 | 24281
1421 | 1421 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 5 | 16226 | 15361 | 16440 | 18175 | 18762 | 19578 | 19947 | 18820 | 19518 | 21723 | 22116 | 23091 | 23425 | 21971 | 23685 | 24482 | 24718 | 25415 | 23650 | 23632
1422 | 1422 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 6 | 16686 | 15406 | 16534 | 18705 | 19224 | 19945 | 20176 | 18525 | 19314 | 21856 | 22150 | 22915 | 23165 | 21417 | 23637 | 24299 | 24356 | 24875 | 22664 | 22908
1423 | 1423 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 7 | 17954 | 15945 | 16863 | 20066 | 20336 | 21066 | 21334 | 18751 | 19490 | 22681 | 22950 | 23687 | 23846 | 21279 | 24552 | 24735 | 24870 | 25365 | 22314 | 22654
1424 | 1424 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 8 | 19305 | 16766 | 17181 | 21420 | 21556 | 22376 | 22846 | 19549 | 19774 | 23706 | 23740 | 24824 | 25096 | 21437 | 25715 | 25460 | 25451 | 26496 | 22823 | 22763
1425 | 1425 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 9 | 19476 | 17422 | 17732 | 21617 | 21822 | 22596 | 23067 | 20244 | 20307 | 23898 | 23752 | 24982 | 25133 | 21820 | 25694 | 25448 | 25265 | 26476 | 23188 | 23118
1426 | 1426 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 10 | 19151 | 17680 | 18092 | 21417 | 21588 | 22266 | 22822 | 20494 | 20571 | 23841 | 23606 | 24700 | 24263 | 21490 | 24831 | 24785 | 25113 | 25664 | 22838 | 22824
1427 | 1427 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 11 | 18769 | 17947 | 18416 | 21368 | 21339 | 21935 | 22445 | 20641 | 20465 | 23830 | 23315 | 24363 | 23788 | 21399 | 24631 | 24780 | 25030 | 25237 | 22962 | 22756
1428 | 1428 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 12 | 18462 | 18044 | 18568 | 21218 | 21040 | 21578 | 22030 | 20630 | 20326 | 23557 | 23048 | 23966 | 23535 | 21478 | 24529 | 24699 | 24856 | 24988 | 23127 | 22831
1429 | 1429 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 13 | 18151 | 17878 | 18484 | 20976 | 20739 | 21104 | 21648 | 20324 | 20099 | 23146 | 22643 | 23386 | 23202 | 21328 | 24120 | 24387 | 24434 | 24648 | 22874 | 22664
1430 | 1430 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 14 | 17718 | 17559 | 18226 | 20782 | 20254 | 20879 | 21360 | 20089 | 19491 | 22961 | 22410 | 23161 | 22473 | 20676 | 23456 | 23700 | 24173 | 23881 | 22162 | 21979
1431 | 1431 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 15 | 17779 | 17589 | 18358 | 20912 | 20207 | 21060 | 21442 | 20203 | 19502 | 23021 | 22520 | 23320 | 22319 | 20624 | 23367 | 23497 | 24241 | 23685 | 22037 | 21903
1432 | 1432 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 16 | 18162 | 17771 | 18600 | 21170 | 20613 | 21346 | 21628 | 20370 | 19835 | 23378 | 22699 | 23492 | 22292 | 20719 | 23442 | 23724 | 24301 | 23577 | 21984 | 21966
1433 | 1433 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 17 | 19133 | 18412 | 19168 | 21780 | 21272 | 22208 | 22487 | 21072 | 20640 | 23979 | 23410 | 24465 | 23334 | 21742 | 24370 | 24492 | 24994 | 24629 | 22988 | 23009
1434 | 1434 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 18 | 19818 | 18653 | 19640 | 22050 | 21856 | 22654 | 22849 | 21353 | 21540 | 24011 | 23543 | 24956 | 24496 | 23106 | 25347 | 25275 | 25201 | 25924 | 24164 | 24454
1435 | 1435 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 19 | 20372 | 19073 | 20458 | 22501 | 22501 | 23147 | 23220 | 21742 | 22506 | 24512 | 24363 | 25707 | 25650 | 24621 | 26603 | 26622 | 26398 | 27309 | 25401 | 26109
1436 | 1436 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 20 | 20331 | 18691 | 20336 | 22460 | 22508 | 23052 | 22889 | 21279 | 22595 | 24619 | 24759 | 26013 | 25918 | 24931 | 27164 | 27332 | 27456 | 27855 | 25818 | 26574
1437 | 1437 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 21 | 20006 | 18412 | 20160 | 22263 | 22360 | 22845 | 22815 | 21281 | 22671 | 24853 | 25153 | 26354 | 26470 | 25439 | 27650 | 28108 | 28380 | 28749 | 26674 | 27287
1438 | 1438 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 22 | 19364 | 17917 | 19556 | 21511 | 21718 | 22289 | 22291 | 20936 | 22200 | 24469 | 24867 | 26151 | 26338 | 25227 | 27277 | 28074 | 28411 | 28823 | 26860 | 27196
1439 | 1439 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 23 | 18431 | 17234 | 18750 | 20447 | 20760 | 21357 | 21336 | 20368 | 21656 | 23602 | 24119 | 25447 | 25596 | 24699 | 26454 | 27390 | 27854 | 28186 | 26603 | 26746
1440 | 1440 | 60 | 3 | 1 | Winter | 2 | 29 | Winter | 24 | 17326 | 16285 | 17873 | 19295 | 19818 | 20262 | 20212 | 19566 | 21132 | 22675 | 23331 | 24514 | 24612 | 24020 | 25428 | 26504 | 27149 | 27240 | 25947 | 26097
1441 | 1441 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 1 | 16348 | 15932 | 17409 | 18494 | 18657 | 19497 | 19021 | 19058 | 20277 | 22063 | 22615 | 23848 | 23228 | 23513 | 25305 | 25971 | 26417 | 25755 | 24681 | 25560
1442 | 1442 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 2 | 15965 | 15592 | 17187 | 18131 | 18334 | 19189 | 18572 | 18849 | 20180 | 21783 | 22233 | 23500 | 22722 | 23335 | 24907 | 25482 | 25800 | 25181 | 24352 | 25349
1443 | 1443 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 3 | 15939 | 15526 | 17303 | 18109 | 18367 | 19244 | 18634 | 19064 | 20718 | 21849 | 22241 | 23565 | 22749 | 23597 | 24926 | 25548 | 25822 | 25111 | 24440 | 25572
1444 | 1444 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 4 | 15950 | 15538 | 17449 | 18181 | 18404 | 19241 | 18567 | 19125 | 20916 | 21734 | 21964 | 23265 | 22346 | 23538 | 24570 | 25051 | 25175 | 24496 | 24104 | 25374
1445 | 1445 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 5 | 16056 | 15617 | 17684 | 18356 | 18469 | 19292 | 18279 | 19040 | 20943 | 21567 | 21692 | 22909 | 21584 | 23287 | 24124 | 24378 | 24414 | 23468 | 23471 | 24953
1446 | 1446 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 6 | 16509 | 15753 | 18269 | 18890 | 18981 | 19613 | 18097 | 18968 | 21274 | 21737 | 21736 | 22750 | 20867 | 23283 | 23990 | 24054 | 23931 | 22496 | 22751 | 24789
1447 | 1447 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 7 | 17732 | 16106 | 19674 | 20061 | 20215 | 20822 | 18422 | 19233 | 22417 | 22627 | 22611 | 23513 | 20763 | 24232 | 24464 | 24603 | 24400 | 22174 | 22504 | 25633
1448 | 1448 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 8 | 19178 | 16422 | 21010 | 21273 | 21155 | 22315 | 19221 | 19490 | 23684 | 23442 | 23382 | 24768 | 21359 | 25401 | 25195 | 25196 | 25056 | 22664 | 22585 | 26750
1449 | 1449 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 9 | 19240 | 16714 | 20960 | 21249 | 21021 | 22262 | 19650 | 19738 | 23664 | 23182 | 23309 | 24601 | 21575 | 25174 | 24976 | 24809 | 25075 | 22825 | 22719 | 26480
1450 | 1450 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 10 | 19026 | 16808 | 20448 | 20658 | 20848 | 21520 | 19346 | 19481 | 23491 | 22347 | 22619 | 23737 | 21197 | 24328 | 24323 | 24665 | 25071 | 22493 | 22441 | 25662
1451 | 1451 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 11 | 18701 | 17080 | 20327 | 20502 | 20520 | 21033 | 19360 | 19550 | 23284 | 21906 | 22271 | 23210 | 21196 | 24067 | 24259 | 24519 | 25020 | 22540 | 22310 | 25432
1452 | 1452 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 12 | 18385 | 17284 | 20241 | 20386 | 20277 | 20712 | 19454 | 19692 | 22985 | 21760 | 22014 | 22891 | 21303 | 23901 | 24120 | 24302 | 24681 | 22653 | 22333 | 25265
1453 | 1453 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 13 | 18194 | 17364 | 20179 | 20272 | 20058 | 20534 | 19360 | 19681 | 22700 | 21572 | 21767 | 22660 | 21147 | 23591 | 23906 | 23974 | 24278 | 22500 | 22271 | 24938
1454 | 1454 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 14 | 18238 | 17288 | 20126 | 20206 | 20167 | 20295 | 19138 | 19484 | 22950 | 21297 | 21512 | 22314 | 20845 | 23308 | 23603 | 24090 | 24415 | 22162 | 21965 | 24627
1455 | 1455 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 15 | 18247 | 17244 | 20073 | 20091 | 20193 | 20156 | 19012 | 19404 | 23062 | 21142 | 21404 | 22102 | 20686 | 23156 | 23336 | 24093 | 24455 | 21970 | 21818 | 24454
1456 | 1456 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 16 | 18438 | 17385 | 20206 | 20267 | 20364 | 20212 | 19030 | 19468 | 23221 | 21174 | 21382 | 22018 | 20604 | 23162 | 23496 | 24072 | 24366 | 21833 | 21803 | 24425
1457 | 1457 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 17 | 19240 | 18013 | 20895 | 20971 | 21029 | 21219 | 19884 | 20344 | 23777 | 22095 | 22133 | 23033 | 21560 | 24059 | 24242 | 24756 | 24862 | 22809 | 22825 | 25347
1458 | 1458 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 18 | 19670 | 18762 | 21455 | 21572 | 21185 | 22037 | 20647 | 21202 | 23984 | 22781 | 22752 | 24145 | 22632 | 25031 | 25005 | 24946 | 25085 | 23985 | 24266 | 26396
1459 | 1459 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 19 | 20181 | 19741 | 22120 | 22338 | 21833 | 22708 | 21340 | 22326 | 24479 | 23881 | 23781 | 25230 | 23650 | 26255 | 26318 | 26111 | 26201 | 25238 | 25927 | 27768
1460 | 1460 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 20 | 19790 | 19689 | 22156 | 22261 | 22014 | 22465 | 20949 | 22284 | 24430 | 24293 | 24212 | 25411 | 23804 | 26766 | 26994 | 27132 | 27011 | 25647 | 26406 | 28430
1461 | 1461 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 21 | 19460 | 19455 | 21908 | 22031 | 21858 | 22297 | 20847 | 22248 | 24414 | 24540 | 24420 | 25826 | 24283 | 27164 | 27674 | 27965 | 27718 | 26464 | 27074 | 29025
1462 | 1462 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 22 | 18798 | 18840 | 21129 | 21342 | 21219 | 21728 | 20455 | 21723 | 23757 | 24164 | 23947 | 25616 | 24278 | 26738 | 27585 | 27951 | 27535 | 26637 | 26959 | 28702
1463 | 1463 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 23 | 17779 | 18037 | 20056 | 20286 | 20278 | 20748 | 19852 | 21025 | 22777 | 23390 | 23124 | 24836 | 23914 | 25908 | 26873 | 27363 | 26896 | 26362 | 26508 | 27920
1464 | 1464 | 61 | 3 | 2 | Winter | 3 | 1 | Winter | 24 | 16515 | 17128 | 18847 | 19133 | 19283 | 19553 | 18975 | 20211 | 21728 | 22520 | 22251 | 23808 | 23190 | 24868 | 25964 | 26631 | 26159 | 25691 | 25877 | 26904
1465 | 1465 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 1 | 15111 | 16381 | 17745 | 17967 | 18086 | 18092 | 18219 | 19505 | 20927 | 21525 | 22041 | 22193 | 21941 | 24398 | 25135 | 25623 | 25824 | 24145 | 25046 | 26635
1466 | 1466 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 2 | 14680 | 16181 | 17411 | 17660 | 17723 | 17661 | 18027 | 19431 | 20683 | 21211 | 21660 | 21752 | 21690 | 24055 | 24694 | 25047 | 25210 | 23840 | 24867 | 26244
1467 | 1467 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 3 | 14561 | 16259 | 17367 | 17558 | 17659 | 17701 | 18226 | 19801 | 20855 | 21263 | 21688 | 21815 | 21857 | 24112 | 24793 | 25087 | 25236 | 23945 | 25107 | 26243
1468 | 1468 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 4 | 14474 | 16364 | 17409 | 17536 | 17592 | 17625 | 18280 | 19955 | 20842 | 21044 | 21450 | 21461 | 21689 | 23784 | 24324 | 24465 | 24632 | 23605 | 24894 | 25742
1469 | 1469 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 5 | 14350 | 16566 | 17575 | 17651 | 17723 | 17358 | 18216 | 20084 | 20759 | 20839 | 21228 | 20764 | 21264 | 23370 | 23667 | 23729 | 23876 | 22962 | 24456 | 25117
1470 | 1470 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 6 | 14448 | 17196 | 18145 | 18255 | 18256 | 17253 | 18234 | 20564 | 21041 | 21009 | 21357 | 20168 | 20792 | 23319 | 23421 | 23317 | 23514 | 22285 | 24319 | 24847
1471 | 1471 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 7 | 14989 | 18566 | 19314 | 19495 | 19370 | 17583 | 18517 | 21754 | 21923 | 21936 | 22236 | 20107 | 20662 | 23798 | 23973 | 23788 | 24087 | 22004 | 25123 | 25169
1472 | 1472 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 8 | 15788 | 19912 | 20558 | 20458 | 20261 | 18389 | 18796 | 23051 | 22963 | 22748 | 23227 | 20733 | 20810 | 24570 | 24598 | 24467 | 24920 | 22091 | 26246 | 25833
1473 | 1473 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 9 | 16197 | 19890 | 20556 | 20281 | 20276 | 18825 | 19062 | 22972 | 22875 | 22684 | 23211 | 20974 | 20991 | 24365 | 24234 | 24485 | 24924 | 22226 | 25981 | 25586
1474 | 1474 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 10 | 16248 | 19467 | 20056 | 19738 | 19854 | 18604 | 18886 | 22218 | 22192 | 22020 | 22668 | 20619 | 20714 | 23735 | 24127 | 24509 | 25090 | 21981 | 25204 | 25022
1475 | 1475 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 11 | 16342 | 19296 | 19827 | 19300 | 19487 | 18547 | 18884 | 21871 | 21954 | 21577 | 22268 | 20524 | 20474 | 23554 | 23885 | 24362 | 25017 | 21756 | 24869 | 24898
1476 | 1476 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 12 | 16480 | 19256 | 19745 | 19201 | 19252 | 18667 | 19047 | 21755 | 21830 | 21334 | 22084 | 20641 | 20517 | 23445 | 23683 | 24038 | 24740 | 21810 | 24727 | 24783
1477 | 1477 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 13 | 16361 | 19073 | 19525 | 18976 | 18965 | 18467 | 18929 | 21495 | 21536 | 20974 | 21680 | 20388 | 20361 | 23114 | 23237 | 23535 | 24219 | 21624 | 24282 | 24440
1478 | 1478 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 14 | 16096 | 18923 | 19370 | 18697 | 18682 | 18140 | 18627 | 21229 | 21176 | 20609 | 21291 | 19972 | 19949 | 22699 | 23237 | 23557 | 24204 | 21200 | 23856 | 23988
1479 | 1479 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 15 | 15921 | 18830 | 19228 | 18550 | 18598 | 17982 | 18518 | 21109 | 20929 | 20472 | 21066 | 19776 | 19783 | 22405 | 23208 | 23559 | 24114 | 21018 | 23648 | 23659
1480 | 1480 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 16 | 15996 | 18969 | 19366 | 18684 | 18721 | 18027 | 18608 | 21209 | 21136 | 20489 | 21039 | 19726 | 19819 | 22596 | 23217 | 23498 | 24018 | 21017 | 23637 | 23800
1481 | 1481 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 17 | 16777 | 19705 | 20116 | 19551 | 19370 | 18930 | 19533 | 22030 | 22008 | 21311 | 21746 | 20749 | 20895 | 23414 | 23964 | 24070 | 24544 | 22110 | 24630 | 24635
1482 | 1482 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 18 | 17398 | 20384 | 20881 | 20244 | 19998 | 19830 | 20504 | 22892 | 22763 | 22033 | 22714 | 21918 | 22389 | 24310 | 24286 | 24423 | 24966 | 23699 | 25823 | 25613
1483 | 1483 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 19 | 18039 | 21115 | 21713 | 21192 | 20818 | 20579 | 21675 | 23778 | 23651 | 23061 | 23783 | 22944 | 23931 | 25645 | 25478 | 25586 | 26121 | 25437 | 27267 | 27138
1484 | 1484 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 20 | 17689 | 21136 | 21610 | 21405 | 20931 | 20159 | 21599 | 23784 | 23797 | 23370 | 24483 | 22993 | 24186 | 26238 | 26424 | 26331 | 27301 | 25902 | 27915 | 27948
1485 | 1485 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 21 | 17339 | 20855 | 21326 | 21172 | 20671 | 19985 | 21489 | 23679 | 23879 | 23450 | 24793 | 23373 | 24567 | 26827 | 27174 | 26966 | 28113 | 26539 | 28487 | 28786
1486 | 1486 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 22 | 16864 | 20037 | 20566 | 20454 | 19940 | 19592 | 20956 | 22933 | 23453 | 22852 | 24559 | 23313 | 24334 | 26651 | 27077 | 26706 | 28257 | 26452 | 28124 | 28763
1487 | 1487 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 23 | 16213 | 18993 | 19526 | 19527 | 18953 | 19000 | 20267 | 21953 | 22587 | 22023 | 23893 | 22927 | 23825 | 25958 | 26513 | 26090 | 27785 | 26035 | 27392 | 28171
1488 | 1488 | 62 | 3 | 3 | Winter | 3 | 2 | Winter | 24 | 15255 | 17844 | 18422 | 18560 | 17940 | 18111 | 19439 | 20898 | 21581 | 21198 | 23115 | 22190 | 23147 | 25118 | 25846 | 25420 | 27063 | 25391 | 26452 | 27370
1489 | 1489 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 1 | 15117 | 17234 | 17725 | 17830 | 18101 | 17897 | 19213 | 20516 | 21150 | 21478 | 22445 | 21546 | 22854 | 24741 | 25313 | 25564 | 26117 | 25046 | 26655 | 27083
1490 | 1490 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 2 | 14778 | 16864 | 17371 | 17418 | 17701 | 17642 | 19084 | 20234 | 20880 | 21103 | 22044 | 21280 | 22694 | 24287 | 24720 | 24935 | 25564 | 24835 | 26226 | 26576
1491 | 1491 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 3 | 14736 | 16821 | 17226 | 17313 | 17675 | 17790 | 19408 | 20377 | 20976 | 21159 | 22051 | 21487 | 23004 | 24420 | 24790 | 24988 | 25449 | 25085 | 26237 | 26648
1492 | 1492 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 4 | 14730 | 16867 | 17216 | 17264 | 17682 | 17871 | 19605 | 20421 | 20899 | 21039 | 21800 | 21381 | 22980 | 24006 | 24221 | 24432 | 24824 | 24898 | 25755 | 26059
1493 | 1493 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 5 | 14790 | 17054 | 17356 | 17436 | 17815 | 17848 | 19791 | 20417 | 20793 | 20922 | 21502 | 21025 | 22768 | 23429 | 23543 | 23729 | 24139 | 24486 | 25151 | 25259
1494 | 1494 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 6 | 14932 | 17610 | 17944 | 17999 | 18329 | 17873 | 20314 | 20758 | 21051 | 21129 | 21268 | 20608 | 22824 | 23229 | 23164 | 23385 | 23496 | 24348 | 24875 | 24826
1495 | 1495 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 7 | 15276 | 18837 | 19210 | 19159 | 19599 | 18199 | 21574 | 21737 | 21994 | 22101 | 21454 | 20561 | 23793 | 23847 | 23701 | 24019 | 23310 | 25177 | 25210 | 25250
1496 | 1496 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 8 | 15590 | 20010 | 20085 | 19966 | 20661 | 18455 | 22791 | 22750 | 22755 | 23033 | 21508 | 20718 | 24887 | 24408 | 24306 | 24776 | 23157 | 26204 | 25784 | 25687
1497 | 1497 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 9 | 15736 | 19848 | 19769 | 19811 | 20576 | 18568 | 22561 | 22529 | 22373 | 22862 | 21554 | 20760 | 24523 | 23899 | 24161 | 24620 | 23164 | 25774 | 25381 | 25103
1498 | 1498 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 10 | 15841 | 19324 | 19233 | 19392 | 20167 | 18386 | 21787 | 21818 | 21549 | 22241 | 21355 | 20415 | 23663 | 23715 | 24112 | 24713 | 23097 | 24924 | 24744 | 24963
1499 | 1499 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 11 | 16142 | 19124 | 18828 | 19032 | 19907 | 18350 | 21390 | 21501 | 21125 | 21729 | 21010 | 20253 | 23404 | 23569 | 24062 | 24725 | 23088 | 24689 | 24719 | 24847
1500 | 1500 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 12 | 16418 | 19053 | 18734 | 18791 | 19750 | 18491 | 21239 | 21329 | 21046 | 21475 | 20829 | 20349 | 23298 | 23416 | 23789 | 24512 | 23059 | 24604 | 24659 | 24699
1501 | 1501 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 13 | 16512 | 18983 | 18658 | 18643 | 19527 | 18522 | 21124 | 21165 | 20877 | 21206 | 20611 | 20320 | 23000 | 23114 | 23417 | 24106 | 22834 | 24296 | 24455 | 24376
1502 | 1502 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 14 | 16372 | 18903 | 18451 | 18453 | 19302 | 18285 | 20924 | 20896 | 20552 | 20876 | 20186 | 19987 | 22658 | 23175 | 23496 | 24170 | 22385 | 23921 | 24052 | 24402
1503 | 1503 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 15 | 16280 | 18772 | 18292 | 18377 | 19132 | 18174 | 20796 | 20660 | 20356 | 20649 | 20002 | 19828 | 22460 | 23138 | 23492 | 24083 | 22164 | 23698 | 23714 | 24341
1504 | 1504 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 16 | 16377 | 18857 | 18399 | 18486 | 19173 | 18242 | 20883 | 20823 | 20355 | 20627 | 20079 | 19823 | 22428 | 23104 | 23387 | 23945 | 22115 | 23624 | 23796 | 24268
1505 | 1505 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 17 | 17066 | 19604 | 19275 | 19144 | 19856 | 19184 | 21727 | 21719 | 21337 | 21388 | 21101 | 20892 | 23404 | 23848 | 23960 | 24482 | 23004 | 24623 | 24633 | 25048
1506 | 1506 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 18 | 17986 | 20446 | 20086 | 19869 | 20644 | 20304 | 22718 | 22641 | 22181 | 22505 | 22408 | 22375 | 24532 | 24176 | 24328 | 24906 | 24301 | 25842 | 25632 | 25492
1507 | 1507 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 19 | 19014 | 21277 | 21025 | 20676 | 21340 | 21473 | 23587 | 23506 | 23300 | 23508 | 23409 | 23849 | 25786 | 25289 | 25431 | 26012 | 25695 | 27266 | 27144 | 26811
1508 | 1508 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 20 | 18914 | 21146 | 21233 | 20787 | 21704 | 21412 | 23606 | 23612 | 23612 | 24128 | 23726 | 24018 | 26225 | 26154 | 26114 | 27129 | 26412 | 27912 | 27933 | 27918
1509 | 1509 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 21 | 18695 | 20876 | 21004 | 20532 | 21586 | 21309 | 23490 | 23653 | 23778 | 24359 | 23961 | 24362 | 26574 | 26865 | 26721 | 27931 | 27138 | 28509 | 28810 | 28907
1510 | 1510 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 22 | 18086 | 20117 | 20290 | 19748 | 21092 | 20735 | 22751 | 23124 | 23331 | 24086 | 23628 | 24057 | 26116 | 26753 | 26463 | 28017 | 27104 | 28180 | 28815 | 28967
1511 | 1511 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 23 | 17270 | 19022 | 19301 | 18718 | 20214 | 19984 | 21704 | 22176 | 22505 | 23337 | 23101 | 23474 | 25252 | 26120 | 25776 | 27490 | 26727 | 27402 | 28172 | 28421
1512 | 1512 | 63 | 3 | 4 | Winter | 3 | 3 | Winter | 24 | 16358 | 17882 | 18320 | 17756 | 19271 | 19137 | 20629 | 21203 | 21688 | 22542 | 22525 | 22767 | 24274 | 25444 | 25100 | 26825 | 26238 | 26461 | 27373 | 27788
1513 | 1513 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 1 | 15809 | 16900 | 17297 | 17639 | 18434 | 18605 | 19898 | 20451 | 20869 | 21653 | 21451 | 22190 | 23951 | 24621 | 24970 | 25617 | 24590 | 26360 | 26807 | 27062
1514 | 1514 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 2 | 15580 | 16545 | 16890 | 17230 | 18006 | 18465 | 19615 | 20181 | 20537 | 21289 | 21162 | 22056 | 23607 | 24062 | 24376 | 25087 | 24183 | 25943 | 26311 | 26440
1515 | 1515 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 3 | 15639 | 16354 | 16736 | 17135 | 17921 | 18729 | 19715 | 20215 | 20573 | 21318 | 21259 | 22381 | 23701 | 24149 | 24445 | 24978 | 24167 | 25951 | 26385 | 26454
1516 | 1516 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 4 | 15751 | 16319 | 16676 | 17155 | 17854 | 18923 | 19784 | 20191 | 20423 | 21143 | 21124 | 22401 | 23427 | 23624 | 23925 | 24386 | 23725 | 25473 | 25791 | 25730
1517 | 1517 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 5 | 15968 | 16467 | 16879 | 17328 | 17936 | 19149 | 19847 | 20164 | 20312 | 20938 | 20829 | 22260 | 23091 | 23017 | 23278 | 23753 | 23065 | 24891 | 25010 | 24900
1518 | 1518 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 6 | 16593 | 17056 | 17461 | 17863 | 18151 | 19683 | 20228 | 20467 | 20561 | 20759 | 20582 | 22388 | 23091 | 22701 | 22988 | 23155 | 22485 | 24635 | 24588 | 24364
1519 | 1519 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 7 | 17975 | 18321 | 18639 | 19143 | 18629 | 20953 | 21272 | 21467 | 21574 | 21008 | 20533 | 23407 | 23641 | 23272 | 23659 | 22989 | 22216 | 24989 | 25024 | 24792
1520 | 1520 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 8 | 19286 | 19308 | 19533 | 20295 | 18877 | 22265 | 22425 | 22374 | 22386 | 21211 | 20336 | 24592 | 24409 | 23965 | 24504 | 22922 | 21881 | 25642 | 25536 | 25407
1521 | 1521 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 9 | 19356 | 19277 | 19646 | 20453 | 19332 | 22290 | 22472 | 22271 | 22425 | 21545 | 20447 | 24498 | 24314 | 24079 | 24607 | 23180 | 21908 | 25489 | 25204 | 25502
1522 | 1522 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 10 | 18867 | 18790 | 19302 | 20089 | 19323 | 21566 | 21785 | 21482 | 21716 | 21339 | 20243 | 23613 | 23597 | 24027 | 24689 | 23088 | 21814 | 24849 | 25055 | 25453
1523 | 1523 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 11 | 18850 | 18667 | 19226 | 19981 | 19246 | 21487 | 21778 | 21202 | 21308 | 21321 | 20219 | 23471 | 23628 | 24088 | 24814 | 23197 | 21700 | 24938 | 25065 | 25568
1524 | 1524 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 12 | 18911 | 18670 | 19120 | 19888 | 19186 | 21486 | 21757 | 21177 | 21084 | 21288 | 20232 | 23455 | 23641 | 23881 | 24659 | 23243 | 21686 | 24946 | 24990 | 25373
1525 | 1525 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 13 | 18345 | 18033 | 18401 | 19087 | 18519 | 20767 | 20976 | 20384 | 20350 | 20418 | 19708 | 22643 | 22930 | 22998 | 23740 | 22496 | 21288 | 24217 | 24156 | 24485
1526 | 1526 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 14 | 18242 | 17811 | 18193 | 18827 | 18194 | 20527 | 20668 | 20000 | 20039 | 19923 | 19248 | 22297 | 22565 | 23076 | 23802 | 22037 | 20868 | 23815 | 24169 | 24530
1527 | 1527 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 15 | 18034 | 17534 | 18003 | 18539 | 17955 | 20277 | 20312 | 19678 | 19800 | 19611 | 19123 | 22000 | 22166 | 22977 | 23615 | 21717 | 20750 | 23376 | 24005 | 24399
1528 | 1528 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 16 | 18165 | 17674 | 18139 | 18635 | 18142 | 20381 | 20460 | 19736 | 19852 | 19702 | 19340 | 22025 | 22335 | 22926 | 23530 | 21715 | 20943 | 23497 | 23968 | 24277
1529 | 1529 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 17 | 18932 | 18503 | 18746 | 19306 | 19028 | 21169 | 21303 | 20707 | 20731 | 20675 | 20488 | 23007 | 23169 | 23516 | 24078 | 22614 | 22151 | 24349 | 24756 | 24876
1530 | 1530 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 18 | 19696 | 19285 | 19370 | 20123 | 20070 | 22087 | 22155 | 21626 | 21616 | 21865 | 21729 | 24097 | 24083 | 23871 | 24497 | 23912 | 23608 | 25354 | 25203 | 25327
1531 | 1531 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 19 | 20455 | 20248 | 20205 | 20859 | 20911 | 23003 | 23050 | 22765 | 22631 | 22847 | 22871 | 25311 | 25392 | 24948 | 25589 | 25302 | 24918 | 26884 | 26548 | 26588
1532 | 1532 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 20 | 20485 | 20457 | 20340 | 21276 | 20853 | 23074 | 23173 | 23112 | 22883 | 23122 | 23310 | 25687 | 25885 | 25557 | 26649 | 25968 | 25731 | 27662 | 27644 | 27445
1533 | 1533 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 21 | 20216 | 20162 | 20036 | 21086 | 20601 | 22889 | 23106 | 23156 | 22878 | 23223 | 23403 | 25929 | 26412 | 26070 | 27350 | 26623 | 26226 | 28495 | 28593 | 28194
1534 | 1534 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 22 | 19424 | 19429 | 19249 | 20576 | 19988 | 22140 | 22535 | 22652 | 22255 | 22827 | 23019 | 25418 | 26224 | 25768 | 27405 | 26563 | 26078 | 28498 | 28655 | 28041
1535 | 1535 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 23 | 18353 | 18448 | 18215 | 19710 | 19295 | 21102 | 21578 | 21812 | 21364 | 22284 | 22489 | 24544 | 25472 | 25075 | 26876 | 26190 | 25682 | 27869 | 28126 | 27438
1536 | 1536 | 64 | 3 | 5 | Winter | 3 | 4 | Winter | 24 | 17191 | 17429 | 17218 | 18739 | 18549 | 19999 | 20557 | 20939 | 20504 | 21681 | 21975 | 23549 | 24600 | 24374 | 26191 | 25678 | 25239 | 27051 | 27481 | 26783
1537 | 1537 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 1 | 16187 | 16274 | 16963 | 17783 | 17773 | 19080 | 19621 | 19953 | 20365 | 20593 | 21532 | 23036 | 23792 | 24109 | 24878 | 23954 | 24680 | 26340 | 26615 | 26551
1538 | 1538 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 2 | 15827 | 15836 | 16530 | 17318 | 17449 | 18759 | 19316 | 19598 | 19995 | 20311 | 21261 | 22691 | 23352 | 23518 | 24344 | 23542 | 24295 | 25828 | 25975 | 25887
1539 | 1539 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 3 | 15802 | 15685 | 16434 | 17225 | 17455 | 18864 | 19373 | 19654 | 20046 | 20493 | 21606 | 22824 | 23528 | 23627 | 24273 | 23554 | 24512 | 25920 | 26008 | 25919
1540 | 1540 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 4 | 15858 | 15609 | 16436 | 17151 | 17455 | 18922 | 19355 | 19541 | 19997 | 20391 | 21589 | 22626 | 23171 | 23176 | 23730 | 23152 | 24254 | 25348 | 25310 | 25266
1541 | 1541 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 5 | 16089 | 15822 | 16645 | 17279 | 17487 | 19044 | 19401 | 19527 | 19999 | 20178 | 21482 | 22388 | 22697 | 22611 | 23163 | 22555 | 23844 | 24599 | 24507 | 24468
1542 | 1542 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 6 | 16653 | 16484 | 17260 | 17547 | 17677 | 19531 | 19823 | 19890 | 20287 | 20064 | 21777 | 22478 | 22584 | 22409 | 22635 | 22016 | 23787 | 24217 | 23988 | 24043
1543 | 1543 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 7 | 17920 | 17684 | 18592 | 18058 | 17980 | 20642 | 20904 | 20987 | 21347 | 20096 | 22842 | 23121 | 23270 | 23133 | 22521 | 21784 | 24618 | 24689 | 24438 | 24631
1544 | 1544 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 8 | 19135 | 18515 | 19663 | 18254 | 17783 | 21737 | 21757 | 21784 | 22368 | 19834 | 23857 | 23887 | 23888 | 23944 | 22417 | 21395 | 25559 | 25160 | 24998 | 25362
1545 | 1545 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 9 | 19476 | 18875 | 20101 | 18984 | 18182 | 22045 | 21945 | 22115 | 22719 | 20240 | 24094 | 24082 | 23921 | 24320 | 22955 | 21701 | 25727 | 25108 | 25356 | 25699
1546 | 1546 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 10 | 19219 | 18889 | 20091 | 19339 | 18448 | 21673 | 21480 | 21753 | 22398 | 20315 | 24274 | 23643 | 24010 | 24677 | 23148 | 21897 | 25948 | 25236 | 25597 | 26094
1547 | 1547 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 11 | 19260 | 18869 | 20055 | 19477 | 18536 | 21705 | 21251 | 21608 | 22269 | 20322 | 24224 | 23700 | 24018 | 24829 | 23292 | 21821 | 25925 | 25283 | 25749 | 26302
1548 | 1548 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 12 | 19256 | 18743 | 19931 | 19439 | 18522 | 21656 | 21196 | 21424 | 22112 | 20307 | 23868 | 23646 | 23883 | 24614 | 23274 | 21734 | 25561 | 25143 | 25495 | 26108
1549 | 1549 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 13 | 18979 | 18484 | 19588 | 19150 | 18469 | 21365 | 20899 | 21070 | 21568 | 20283 | 23303 | 23305 | 23415 | 24062 | 22897 | 21699 | 24906 | 24666 | 24962 | 25547
1550 | 1550 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 14 | 18861 | 18320 | 19382 | 18840 | 18109 | 21135 | 20586 | 20776 | 21158 | 19894 | 23389 | 22946 | 23449 | 24121 | 22435 | 21277 | 24889 | 24677 | 24998 | 25577
1551 | 1551 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 15 | 18690 | 18191 | 19161 | 18647 | 18091 | 20863 | 20344 | 20587 | 20865 | 19849 | 23403 | 22599 | 23377 | 23987 | 22164 | 21205 | 24864 | 24562 | 24909 | 25407
1552 | 1552 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 16 | 18714 | 18280 | 19194 | 18743 | 18298 | 20943 | 20336 | 20549 | 20785 | 19999 | 23467 | 22690 | 23305 | 23843 | 22096 | 21331 | 24857 | 24447 | 24720 | 25208
1553 | 1553 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 17 | 19127 | 18522 | 19512 | 19247 | 18993 | 21445 | 20963 | 21025 | 21169 | 20819 | 23782 | 23203 | 23741 | 24062 | 22676 | 22217 | 25209 | 24912 | 25001 | 25438
1554 | 1554 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 18 | 19586 | 18731 | 19859 | 19793 | 19568 | 21866 | 21429 | 21337 | 21820 | 21568 | 23621 | 23724 | 23696 | 24105 | 23596 | 23304 | 25327 | 24989 | 25088 | 25573
1555 | 1555 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 19 | 20315 | 19367 | 20385 | 20431 | 20322 | 22542 | 22333 | 22112 | 22677 | 22429 | 24328 | 24800 | 24640 | 24991 | 24781 | 24446 | 26364 | 26183 | 26201 | 26653
1556 | 1556 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 20 | 20202 | 19456 | 20746 | 20365 | 20606 | 22579 | 22553 | 22288 | 23295 | 22681 | 24660 | 25241 | 25432 | 25995 | 25408 | 25234 | 27052 | 27276 | 27065 | 27909
1557 | 1557 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 21 | 19842 | 19104 | 20512 | 20061 | 20301 | 22428 | 22502 | 22177 | 23375 | 22660 | 24670 | 25644 | 26007 | 26605 | 25979 | 25668 | 27450 | 28191 | 27790 | 28761
1558 | 1558 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 22 | 19075 | 18331 | 19986 | 19441 | 19702 | 21824 | 21948 | 21508 | 23049 | 22225 | 24061 | 25399 | 25852 | 26607 | 25888 | 25511 | 27068 | 28243 | 27640 | 28917
1559 | 1559 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 23 | 17971 | 17261 | 19085 | 18720 | 18999 | 20812 | 21051 | 20562 | 22267 | 21647 | 23126 | 24598 | 25198 | 26038 | 25486 | 25086 | 26254 | 27675 | 26999 | 28416
1560 | 1560 | 65 | 3 | 6 | Winter | 3 | 5 | Winter | 24 | 16805 | 16248 | 18099 | 17970 | 18333 | 19780 | 20156 | 19673 | 21427 | 21127 | 22192 | 23725 | 24491 | 25347 | 24969 | 24634 | 25366 | 27043 | 26363 | 27789
1561 | 1561 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 1 | 16109 | 16398 | 17558 | 17616 | 18397 | 19171 | 19502 | 19876 | 20862 | 21126 | 22140 | 23317 | 23948 | 24500 | 23743 | 24515 | 25732 | 26581 | 26553 | 26848
1562 | 1562 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 2 | 15756 | 15944 | 17050 | 17228 | 18204 | 18787 | 19070 | 19426 | 20499 | 20899 | 21798 | 22906 | 23407 | 24004 | 23359 | 24153 | 25356 | 25957 | 25908 | 26291
1563 | 1563 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 3 | 15578 | 15869 | 16971 | 17288 | 18270 | 18897 | 19209 | 19609 | 20561 | 21279 | 22043 | 23089 | 23518 | 23934 | 23373 | 24356 | 25272 | 25979 | 25928 | 26159
1564 | 1564 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 4 | 15530 | 15851 | 16881 | 17240 | 18375 | 18874 | 19110 | 19549 | 20409 | 21299 | 21927 | 22791 | 23061 | 23438 | 23003 | 24120 | 24887 | 25294 | 25284 | 25481
1565 | 1565 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 5 | 15678 | 16018 | 16975 | 17218 | 18647 | 18891 | 19076 | 19530 | 20278 | 21238 | 21796 | 22368 | 22527 | 22920 | 22429 | 23723 | 24390 | 24492 | 24484 | 24737
1566 | 1566 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 6 | 16301 | 16619 | 17250 | 17431 | 19371 | 19327 | 19478 | 19908 | 20236 | 21644 | 22189 | 22334 | 22303 | 22446 | 21922 | 23696 | 24373 | 24001 | 24067 | 24039
1567 | 1567 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 7 | 17593 | 17984 | 17793 | 17752 | 20675 | 20461 | 20633 | 21039 | 20576 | 22809 | 23001 | 23101 | 22945 | 22385 | 21728 | 24548 | 24914 | 24460 | 24656 | 23828
1568 | 1568 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 8 | 18515 | 19032 | 18003 | 17512 | 21701 | 21331 | 21453 | 22046 | 20709 | 23791 | 23622 | 23749 | 23605 | 22297 | 21352 | 25497 | 25372 | 25013 | 25374 | 23669
1569 | 1569 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 9 | 18591 | 19317 | 18619 | 17794 | 21723 | 21415 | 21693 | 22328 | 21163 | 23858 | 23647 | 23640 | 23821 | 22664 | 21488 | 25503 | 25266 | 25198 | 25536 | 24001
1570 | 1570 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 10 | 18262 | 19485 | 19216 | 18350 | 21337 | 21315 | 21747 | 22470 | 21130 | 23886 | 23755 | 23577 | 23909 | 22699 | 21530 | 25571 | 25004 | 25296 | 25782 | 24080
1571 | 1571 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 11 | 17982 | 19363 | 19303 | 18394 | 20917 | 21070 | 21597 | 22355 | 20948 | 23614 | 23655 | 23362 | 23800 | 22621 | 21235 | 25339 | 24954 | 25224 | 25771 | 24039
1572 | 1572 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 12 | 17779 | 19052 | 19066 | 18189 | 20545 | 20793 | 21176 | 21971 | 20727 | 23121 | 23241 | 23057 | 23367 | 22449 | 20989 | 24811 | 24542 | 24807 | 25416 | 23863
1573 | 1573 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 13 | 17533 | 18640 | 18684 | 18126 | 20208 | 20380 | 20686 | 21420 | 20327 | 22579 | 22741 | 22552 | 22811 | 22028 | 20908 | 24107 | 23998 | 24225 | 24810 | 23423
1574 | 1574 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 14 | 17267 | 18552 | 18523 | 18014 | 19902 | 20326 | 20685 | 21415 | 19836 | 22610 | 22475 | 22519 | 22814 | 21484 | 20398 | 24026 | 23283 | 24181 | 24756 | 22851
1575 | 1575 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 15 | 17037 | 18440 | 18440 | 18134 | 19760 | 20249 | 20682 | 21333 | 19592 | 22655 | 22338 | 22449 | 22756 | 21227 | 20341 | 23998 | 22894 | 24105 | 24593 | 22569
1576 | 1576 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 16 | 17218 | 18577 | 18661 | 18471 | 19955 | 20388 | 20800 | 21413 | 19726 | 22827 | 22736 | 22501 | 22753 | 21269 | 20568 | 24095 | 23193 | 24007 | 24484 | 22570
1577 | 1577 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 17 | 18028 | 19069 | 19295 | 19278 | 20639 | 21087 | 21334 | 21828 | 20665 | 23433 | 23379 | 23227 | 23319 | 22143 | 21752 | 24736 | 24116 | 24589 | 25020 | 23471
1578 | 1578 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 18 | 18723 | 19386 | 19743 | 19668 | 21283 | 21350 | 21344 | 22039 | 21675 | 23455 | 23328 | 23445 | 23583 | 23348 | 23125 | 25138 | 24850 | 24968 | 25451 | 24739
1579 | 1579 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 19 | 19617 | 19918 | 20355 | 20312 | 22177 | 22141 | 21976 | 22648 | 22517 | 24191 | 23967 | 24447 | 24571 | 24616 | 24369 | 26285 | 25990 | 26212 | 26664 | 26186
1580 | 1580 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 20 | 19749 | 20245 | 20273 | 20509 | 22318 | 22315 | 22095 | 23082 | 22620 | 24414 | 24555 | 25141 | 25114 | 25164 | 25101 | 26937 | 27145 | 27050 | 27899 | 26956
1581 | 1581 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 21 | 19428 | 20050 | 19949 | 20208 | 21992 | 22229 | 21938 | 23093 | 22618 | 24357 | 24830 | 25638 | 25540 | 25678 | 25508 | 27322 | 27908 | 27787 | 28770 | 27722
1582 | 1582 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 22 | 18678 | 19485 | 19301 | 19583 | 21174 | 21619 | 21214 | 22695 | 22168 | 23683 | 24314 | 25405 | 25192 | 25543 | 25299 | 26909 | 27696 | 27621 | 28916 | 27724
1583 | 1583 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 23 | 17682 | 18591 | 18580 | 18886 | 20084 | 20714 | 20259 | 21889 | 21580 | 22739 | 23466 | 24718 | 24464 | 25118 | 24876 | 26092 | 27036 | 27000 | 28435 | 27397
1584 | 1584 | 66 | 3 | 7 | Winter | 3 | 6 | Winter | 24 | 16671 | 17613 | 17829 | 18241 | 18999 | 19828 | 19374 | 21057 | 20957 | 21779 | 22613 | 24001 | 23761 | 24584 | 24415 | 25205 | 26248 | 26354 | 27799 | 26917
1585 | 1585 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 1 | 15831 | 16987 | 17415 | 18149 | 18446 | 19009 | 19431 | 20322 | 20246 | 21597 | 22588 | 23365 | 23834 | 23383 | 24239 | 25454 | 26272 | 26462 | 26791 | 25415
1586 | 1586 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 2 | 15370 | 16474 | 17015 | 17871 | 18093 | 18560 | 18970 | 19858 | 19880 | 21275 | 22269 | 22835 | 23275 | 23008 | 23882 | 25082 | 25683 | 25811 | 26229 | 24997
1587 | 1587 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 3 | 15251 | 16327 | 17005 | 17967 | 18138 | 18641 | 19108 | 20018 | 20171 | 21538 | 22477 | 22967 | 23378 | 23026 | 24083 | 24998 | 25291 | 25821 | 26084 | 24968
1588 | 1588 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 4 | 15195 | 16260 | 16966 | 18072 | 18217 | 18576 | 19100 | 19910 | 20110 | 21510 | 22272 | 22601 | 23007 | 22719 | 23904 | 24667 | 24800 | 25215 | 25437 | 24519
1589 | 1589 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 5 | 15355 | 16342 | 16954 | 18306 | 18398 | 18581 | 19138 | 19774 | 19860 | 21445 | 22050 | 22140 | 22495 | 22178 | 23540 | 24199 | 24409 | 24424 | 24699 | 23795
1590 | 1590 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 6 | 16016 | 16653 | 17208 | 19040 | 19151 | 19042 | 19606 | 19795 | 19772 | 21925 | 22232 | 22018 | 22376 | 21726 | 23558 | 24225 | 24244 | 24034 | 24022 | 23163
1591 | 1591 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 7 | 17217 | 17181 | 17556 | 20354 | 20425 | 20229 | 20796 | 20202 | 19853 | 22815 | 23051 | 22742 | 23168 | 21561 | 24424 | 24802 | 24688 | 24628 | 23810 | 22877
1592 | 1592 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 8 | 17938 | 17325 | 17245 | 21274 | 21247 | 20957 | 21728 | 20287 | 19523 | 23377 | 23767 | 23340 | 23909 | 21110 | 25288 | 25182 | 25162 | 25265 | 23561 | 22383
1593 | 1593 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 9 | 17698 | 17536 | 17120 | 20918 | 20885 | 20779 | 21602 | 20415 | 19426 | 23005 | 23439 | 23151 | 23685 | 20829 | 24883 | 24658 | 24601 | 25008 | 23469 | 22075
1594 | 1594 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 10 | 17536 | 17865 | 17398 | 20659 | 20576 | 20545 | 21446 | 20686 | 19676 | 22804 | 23154 | 22927 | 23579 | 20567 | 24657 | 24088 | 24011 | 24957 | 23249 | 21859
1595 | 1595 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 11 | 17329 | 17910 | 17388 | 20344 | 20285 | 20322 | 21252 | 20668 | 19629 | 22620 | 22895 | 22731 | 23422 | 20195 | 24357 | 23955 | 23664 | 24871 | 23137 | 21521
1596 | 1596 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 12 | 17183 | 17824 | 17341 | 20076 | 20082 | 20062 | 21021 | 20509 | 19521 | 22342 | 22639 | 22446 | 23205 | 20093 | 23966 | 23687 | 23588 | 24658 | 23105 | 21418
1597 | 1597 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 13 | 17001 | 17662 | 17487 | 19868 | 19877 | 19775 | 20667 | 20193 | 19512 | 22040 | 22270 | 22071 | 22771 | 20209 | 23460 | 23321 | 23416 | 24235 | 22861 | 21513
1598 | 1598 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 14 | 17180 | 17720 | 17596 | 20072 | 19876 | 20002 | 20894 | 20345 | 19713 | 22033 | 22390 | 22311 | 22987 | 19949 | 23619 | 22842 | 23119 | 24421 | 22529 | 21223
1599 | 1599 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 15 | 17332 | 17802 | 17877 | 20255 | 19961 | 20176 | 20988 | 20488 | 20058 | 22087 | 22539 | 22468 | 23052 | 20077 | 23774 | 22663 | 22981 | 24447 | 22427 | 21331
1600 | 1600 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 16 | 17646 | 18094 | 18291 | 20557 | 20444 | 20389 | 21164 | 20752 | 20447 | 22570 | 22752 | 22558 | 23106 | 20395 | 23960 | 23044 | 23108 | 24428 | 22509 | 21622
1601 | 1601 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 17 | 18073 | 18717 | 19090 | 21048 | 21176 | 20928 | 21582 | 21424 | 21296 | 23220 | 23458 | 23123 | 23629 | 21581 | 24609 | 23967 | 23929 | 24963 | 23405 | 22829
1602 | 1602 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 18 | 18332 | 19213 | 19523 | 21311 | 21320 | 21020 | 21839 | 21817 | 21702 | 23178 | 23718 | 23371 | 23968 | 22979 | 25033 | 24738 | 25128 | 25423 | 24719 | 24298
1603 | 1603 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 19 | 18995 | 19827 | 20181 | 22034 | 21716 | 21660 | 22427 | 22358 | 22374 | 23739 | 24280 | 24306 | 24936 | 24183 | 26143 | 25853 | 26434 | 26632 | 26169 | 25644
1604 | 1604 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 20 | 19078 | 19777 | 20410 | 22206 | 22021 | 21801 | 22858 | 22433 | 22577 | 24259 | 24938 | 24775 | 25882 | 24893 | 26788 | 26993 | 27570 | 27891 | 26970 | 26529
1605 | 1605 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 21 | 18708 | 19411 | 20066 | 21840 | 21786 | 21580 | 22783 | 22324 | 22485 | 24407 | 25222 | 25096 | 26410 | 25221 | 27107 | 27687 | 28377 | 28726 | 27710 | 27065
1606 | 1606 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 22 | 17915 | 18761 | 19425 | 21007 | 20955 | 20825 | 22338 | 21804 | 21983 | 23812 | 24858 | 24673 | 26353 | 24974 | 26665 | 27448 | 28341 | 28863 | 27710 | 26928
1607 | 1607 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 23 | 16847 | 18022 | 18693 | 19896 | 19896 | 19837 | 21488 | 21172 | 21383 | 22915 | 24058 | 23899 | 25750 | 24514 | 25831 | 26756 | 27681 | 28375 | 27362 | 26542
1608 | 1608 | 67 | 3 | 8 | Winter | 3 | 7 | Winter | 24 | 15850 | 17243 | 18001 | 18816 | 18882 | 18914 | 20615 | 20527 | 20872 | 22046 | 23333 | 23169 | 25042 | 24035 | 24932 | 25947 | 26998 | 27716 | 26867 | 26097
1609 | 1609 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 1 | 15686 | 16628 | 17682 | 17940 | 18431 | 18717 | 19649 | 19613 | 20521 | 21770 | 22893 | 23008 | 23924 | 23631 | 24890 | 25722 | 26551 | 26470 | 25151 | 25647
1610 | 1610 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 2 | 15265 | 16243 | 17416 | 17588 | 18129 | 18267 | 19195 | 19260 | 20312 | 21498 | 22589 | 22484 | 23454 | 23302 | 24551 | 25162 | 25951 | 25931 | 24749 | 25280
1611 | 1611 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 3 | 15183 | 16164 | 17458 | 17577 | 18188 | 18361 | 19319 | 19514 | 20671 | 21743 | 22815 | 22622 | 23402 | 23536 | 24485 | 24788 | 25442 | 25789 | 24718 | 25470
1612 | 1612 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 4 | 15187 | 16124 | 17543 | 17639 | 18189 | 18364 | 19233 | 19473 | 20744 | 21600 | 22668 | 22316 | 22981 | 23390 | 24189 | 24327 | 24989 | 25151 | 24267 | 25184
1613 | 1613 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 5 | 15356 | 16123 | 17796 | 17850 | 18372 | 18454 | 19165 | 19288 | 20736 | 21464 | 22367 | 21886 | 22526 | 23077 | 23770 | 23980 | 24542 | 24433 | 23554 | 24694
1614 | 1614 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 6 | 15994 | 16430 | 18584 | 18665 | 19014 | 19003 | 19294 | 19310 | 21238 | 21762 | 22491 | 21891 | 22156 | 23158 | 23872 | 23884 | 24261 | 23798 | 22960 | 24615
1615 | 1615 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 7 | 17357 | 16799 | 19924 | 19978 | 20158 | 20228 | 19769 | 19456 | 22444 | 22655 | 23347 | 22762 | 22138 | 24059 | 24487 | 24358 | 24895 | 23598 | 22682 | 25417
1616 | 1616 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 8 | 18280 | 16484 | 20825 | 20806 | 21049 | 21156 | 19871 | 19151 | 23345 | 23405 | 24135 | 23523 | 21978 | 24924 | 24883 | 24839 | 25538 | 23346 | 22172 | 26241
1617 | 1617 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 9 | 18133 | 16367 | 20471 | 20440 | 20891 | 21030 | 20005 | 19069 | 23010 | 23099 | 23847 | 23320 | 21955 | 24525 | 24366 | 24301 | 25081 | 23247 | 21857 | 25801
1618 | 1618 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 10 | 18011 | 16670 | 20226 | 20125 | 20578 | 20869 | 20268 | 19330 | 22749 | 22799 | 23377 | 23205 | 21693 | 24290 | 23774 | 23716 | 24550 | 23017 | 21631 | 25590
1619 | 1619 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 11 | 17788 | 16630 | 19898 | 19802 | 20258 | 20635 | 20216 | 19267 | 22380 | 22499 | 23027 | 23018 | 21506 | 23948 | 23593 | 23351 | 24112 | 22867 | 21259 | 25273
1620 | 1620 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 12 | 17638 | 16587 | 19650 | 19613 | 20038 | 20403 | 20065 | 19155 | 22049 | 22231 | 22674 | 22777 | 21482 | 23560 | 23329 | 23255 | 23814 | 22835 | 21155 | 24888
1621 | 1621 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 13 | 17397 | 16744 | 19441 | 19429 | 19739 | 20041 | 19741 | 19158 | 21679 | 21835 | 22196 | 22336 | 21222 | 23026 | 22939 | 23074 | 23713 | 22559 | 21223 | 24333
1622 | 1622 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 14 | 17460 | 16756 | 19533 | 19343 | 19708 | 20160 | 19790 | 19256 | 21851 | 21872 | 22173 | 22475 | 20833 | 23099 | 22372 | 22693 | 23394 | 22140 | 20844 | 24379
1623 | 1623 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 15 | 17421 | 16889 | 19582 | 19316 | 19705 | 20127 | 19806 | 19468 | 21958 | 21905 | 22174 | 22430 | 20647 | 23142 | 22080 | 22445 | 23139 | 21919 | 20830 | 24398
1624 | 1624 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 16 | 17598 | 17247 | 19838 | 19743 | 19946 | 20270 | 20033 | 19815 | 22169 | 22089 | 22292 | 22456 | 20731 | 23290 | 22431 | 22529 | 23162 | 21954 | 21073 | 24514
1625 | 1625 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 17 | 18208 | 18149 | 20451 | 20602 | 20734 | 20818 | 20827 | 20780 | 22872 | 22918 | 23138 | 23107 | 21708 | 24056 | 23475 | 23465 | 24098 | 22976 | 22406 | 25308
1626 | 1626 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 18 | 18700 | 18745 | 20848 | 20947 | 21285 | 21246 | 21357 | 21321 | 23095 | 23283 | 23703 | 23534 | 23069 | 24601 | 24369 | 24784 | 25409 | 24425 | 24011 | 25928
1627 | 1627 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 19 | 19292 | 19445 | 21631 | 21376 | 21811 | 21878 | 21922 | 22007 | 23866 | 23796 | 24416 | 24457 | 24349 | 25707 | 25465 | 26085 | 26625 | 25908 | 25382 | 27181
1628 | 1628 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 20 | 19621 | 19643 | 21795 | 21661 | 22048 | 22295 | 21968 | 22180 | 24059 | 24344 | 24940 | 25307 | 24857 | 26294 | 26549 | 27174 | 27666 | 26696 | 26271 | 27923
1629 | 1629 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 21 | 19410 | 19304 | 21423 | 21391 | 21823 | 22177 | 21800 | 22024 | 23910 | 24529 | 25331 | 25746 | 25267 | 26571 | 27186 | 27940 | 28563 | 27426 | 26799 | 28394
1630 | 1630 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 22 | 18830 | 18655 | 20575 | 20538 | 21124 | 21713 | 21243 | 21482 | 23187 | 24099 | 24887 | 25634 | 25080 | 26099 | 26910 | 27885 | 28415 | 27433 | 26682 | 28029
1631 | 1631 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 23 | 17878 | 17858 | 19400 | 19410 | 20078 | 20785 | 20528 | 20797 | 22158 | 23208 | 24143 | 24943 | 24576 | 25193 | 26152 | 27156 | 27792 | 27027 | 26237 | 27183
1632 | 1632 | 68 | 3 | 9 | Winter | 3 | 8 | Winter | 24 | 16925 | 17182 | 18321 | 18394 | 19206 | 19906 | 19875 | 20272 | 21194 | 22488 | 23401 | 24224 | 24042 | 24317 | 25368 | 26482 | 26939 | 26554 | 25814 | 26327
1633 | 1633 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 1 | 16246 | 17075 | 17606 | 18113 | 18743 | 19166 | 19246 | 20132 | 20844 | 22259 | 22790 | 23306 | 22841 | 24392 | 25294 | 26191 | 26417 | 25028 | 25538 | 26636
1634 | 1634 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 2 | 15760 | 16837 | 17276 | 17835 | 18465 | 18743 | 18931 | 19970 | 20541 | 22052 | 22474 | 22848 | 22494 | 24055 | 24738 | 25591 | 25738 | 24613 | 25161 | 26262
1635 | 1635 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 3 | 15620 | 16763 | 17137 | 17751 | 18564 | 18705 | 19020 | 20152 | 20800 | 22154 | 22560 | 22828 | 22548 | 24016 | 24393 | 25100 | 25349 | 24591 | 25361 | 26174
1636 | 1636 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 4 | 15552 | 16817 | 17177 | 17740 | 18633 | 18622 | 18987 | 20239 | 20807 | 22076 | 22383 | 22471 | 22279 | 23766 | 23960 | 24674 | 24908 | 24143 | 25072 | 25756
1637 | 1637 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 5 | 15656 | 17112 | 17440 | 17993 | 18754 | 18648 | 18901 | 20341 | 20833 | 21921 | 22202 | 22105 | 21812 | 23416 | 23677 | 24280 | 24457 | 23460 | 24601 | 25197
1638 | 1638 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 6 | 15978 | 17882 | 18230 | 18636 | 19359 | 18794 | 18955 | 20891 | 21385 | 22110 | 22425 | 21797 | 21414 | 23536 | 23594 | 24008 | 24164 | 22844 | 24494 | 25106
1639 | 1639 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 7 | 16487 | 19195 | 19564 | 19804 | 20580 | 19284 | 19136 | 22141 | 22329 | 23022 | 23278 | 21843 | 21275 | 24172 | 24094 | 24663 | 24646 | 22556 | 25281 | 25585
1640 | 1640 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 8 | 16614 | 20094 | 20412 | 20701 | 21459 | 19380 | 18839 | 23066 | 22920 | 23845 | 23870 | 21705 | 20821 | 24570 | 24587 | 25302 | 25163 | 22034 | 26083 | 25871
1641 | 1641 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 9 | 16814 | 19730 | 20033 | 20509 | 21202 | 19480 | 18733 | 22699 | 22553 | 23528 | 23445 | 21675 | 20539 | 24057 | 24060 | 24831 | 24649 | 21707 | 25633 | 25312
1642 | 1642 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 10 | 17164 | 19279 | 19434 | 19864 | 20742 | 19326 | 18531 | 21932 | 22339 | 22478 | 22525 | 21396 | 20268 | 23462 | 23473 | 24293 | 24005 | 21479 | 25426 | 24775
1643 | 1643 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 11 | 17280 | 18993 | 19103 | 19531 | 20455 | 19232 | 18409 | 21503 | 22198 | 22035 | 22043 | 21277 | 19943 | 23352 | 23174 | 23924 | 23675 | 21181 | 25187 | 24717
1644 | 1644 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 12 | 17189 | 18829 | 19017 | 19408 | 20145 | 19207 | 18431 | 21297 | 21919 | 21829 | 21684 | 21261 | 19831 | 23108 | 23119 | 23636 | 23277 | 21100 | 24826 | 24471
1645 | 1645 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 13 | 17009 | 18703 | 18912 | 19196 | 19787 | 18989 | 18545 | 21054 | 21599 | 21477 | 21264 | 20991 | 19916 | 22705 | 22924 | 23528 | 22818 | 21159 | 24254 | 24057
1646 | 1646 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 14 | 17000 | 18612 | 18624 | 18915 | 19764 | 18722 | 18294 | 20852 | 21530 | 21051 | 20887 | 20631 | 19599 | 22164 | 22555 | 23231 | 22442 | 20796 | 24314 | 23467
1647 | 1647 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 15 | 16984 | 18582 | 18526 | 18805 | 19791 | 18610 | 18366 | 20799 | 21493 | 20891 | 20649 | 20475 | 19633 | 21910 | 22337 | 22990 | 22096 | 20810 | 24361 | 23170
1648 | 1648 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 16 | 17188 | 18783 | 18846 | 18992 | 19998 | 18778 | 18646 | 20946 | 21898 | 20953 | 20619 | 20546 | 19876 | 22235 | 22395 | 23002 | 21982 | 21016 | 24440 | 23441
1649 | 1649 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 17 | 17921 | 19472 | 19811 | 19936 | 20827 | 19739 | 19793 | 21871 | 22661 | 22027 | 21442 | 21536 | 21178 | 23264 | 23313 | 23948 | 22698 | 22327 | 25225 | 24479
1650 | 1650 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 18 | 18503 | 20155 | 20521 | 20889 | 21301 | 20768 | 20849 | 22631 | 22739 | 23173 | 22388 | 22803 | 22655 | 24116 | 24579 | 25202 | 24130 | 23895 | 25821 | 25415
1651 | 1651 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 19 | 19163 | 21061 | 21124 | 21567 | 21850 | 21556 | 21766 | 23608 | 23315 | 24076 | 23445 | 24012 | 23862 | 25180 | 25848 | 26380 | 25711 | 25293 | 27089 | 26678
1652 | 1652 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 20 | 19076 | 21203 | 21377 | 21768 | 22146 | 21571 | 21902 | 23751 | 23742 | 24474 | 24131 | 24406 | 24489 | 26173 | 26853 | 27363 | 26903 | 26147 | 27806 | 27894
1653 | 1653 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 21 | 18688 | 20816 | 21044 | 21474 | 22022 | 21331 | 21664 | 23524 | 23777 | 24723 | 24550 | 24711 | 24741 | 26725 | 27535 | 28196 | 27853 | 26653 | 28254 | 28697
1654 | 1654 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 22 | 18029 | 19929 | 20157 | 20744 | 21289 | 20746 | 21091 | 22762 | 23119 | 24209 | 24169 | 24459 | 24451 | 26395 | 27425 | 28019 | 27782 | 26523 | 27880 | 28518
1655 | 1655 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 23 | 17280 | 18799 | 19056 | 19717 | 20399 | 20045 | 20416 | 21726 | 22180 | 23454 | 23422 | 23952 | 23957 | 25646 | 26717 | 27403 | 27141 | 26115 | 27071 | 27869
1656 | 1656 | 69 | 3 | 10 | Winter | 3 | 9 | Winter | 24 | 16503 | 17676 | 17969 | 18777 | 19435 | 19314 | 19808 | 20664 | 21276 | 22646 | 22590 | 23373 | 23467 | 24823 | 26013 | 26523 | 26261 | 25667 | 26200 | 27086
1657 | 1657 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 1 | 16044 | 16862 | 17628 | 18303 | 18653 | 18702 | 19629 | 20258 | 21112 | 22007 | 21826 | 22219 | 23180 | 24660 | 25636 | 25937 | 25277 | 25321 | 26420 | 27021
1658 | 1658 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 2 | 15687 | 16524 | 17337 | 18043 | 18341 | 18364 | 19449 | 20010 | 20908 | 21719 | 21422 | 21882 | 22863 | 24118 | 25049 | 25262 | 24530 | 24938 | 26036 | 26427
1659 | 1659 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 3 | 15532 | 16320 | 17195 | 17967 | 18337 | 18385 | 19568 | 20059 | 20984 | 21805 | 21361 | 21945 | 23108 | 23787 | 24570 | 24879 | 24014 | 25128 | 25946 | 26038
1660 | 1660 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 4 | 15509 | 16359 | 17207 | 18060 | 18400 | 18389 | 19701 | 20130 | 20904 | 21745 | 21094 | 21747 | 23021 | 23431 | 24216 | 24491 | 23471 | 24871 | 25546 | 25498
1661 | 1661 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 5 | 15526 | 16614 | 17460 | 18219 | 18630 | 18321 | 19831 | 20241 | 20880 | 21637 | 20847 | 21331 | 22754 | 23188 | 23856 | 24062 | 22924 | 24396 | 24978 | 25031
1662 | 1662 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 6 | 15825 | 17423 | 18131 | 18874 | 19339 | 18430 | 20461 | 20878 | 21241 | 21972 | 20663 | 21022 | 22865 | 23181 | 23651 | 23822 | 22276 | 24320 | 24909 | 24791
1663 | 1663 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 7 | 16220 | 18832 | 19334 | 20131 | 20511 | 18663 | 21795 | 21917 | 22211 | 22933 | 20780 | 20969 | 23815 | 23758 | 24374 | 24357 | 22140 | 25139 | 25416 | 25170
1664 | 1664 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 8 | 15926 | 19697 | 20241 | 21030 | 21255 | 18382 | 22736 | 22580 | 23007 | 23573 | 20698 | 20556 | 24705 | 24293 | 25044 | 24903 | 21945 | 25958 | 25733 | 25586
1665 | 1665 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 9 | 15802 | 19347 | 20092 | 20786 | 20949 | 18298 | 22407 | 22242 | 22704 | 23194 | 20583 | 20316 | 24315 | 23808 | 24608 | 24422 | 21653 | 25534 | 25203 | 25024
1666 | 1666 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 10 | 15815 | 18716 | 19448 | 19953 | 20153 | 18076 | 21614 | 21456 | 21786 | 22200 | 20134 | 19972 | 24006 | 23159 | 24002 | 23710 | 21471 | 25259 | 24594 | 24409
1667 | 1667 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 11 | 15759 | 18293 | 19004 | 19435 | 19663 | 17781 | 20988 | 20942 | 21373 | 21470 | 19674 | 19597 | 23710 | 22820 | 23602 | 23332 | 21377 | 24984 | 24499 | 24107
1668 | 1668 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 12 | 15811 | 18192 | 18852 | 19199 | 19320 | 17737 | 20721 | 20732 | 21279 | 21018 | 19450 | 19528 | 23365 | 22767 | 23332 | 22985 | 21257 | 24643 | 24267 | 24062
1669 | 1669 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 13 | 16021 | 18124 | 18659 | 18943 | 18962 | 17870 | 20498 | 20543 | 21011 | 20610 | 19113 | 19610 | 22820 | 22582 | 23233 | 22515 | 20859 | 24076 | 23853 | 23863
1670 | 1670 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 14 | 15875 | 17864 | 18387 | 18641 | 18694 | 17632 | 20307 | 20070 | 20647 | 20237 | 18662 | 19287 | 22915 | 22218 | 22936 | 22132 | 20409 | 24144 | 23272 | 23475
1671 | 1671 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 15 | 15917 | 17753 | 18246 | 18520 | 18493 | 17678 | 20229 | 19832 | 20487 | 19978 | 18466 | 19299 | 22959 | 21974 | 22676 | 21769 | 20126 | 24161 | 22948 | 23212
1672 | 1672 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 16 | 16270 | 18129 | 18514 | 18790 | 18662 | 18050 | 20472 | 20258 | 20660 | 20066 | 18580 | 19610 | 23141 | 22096 | 22748 | 21721 | 20152 | 24292 | 23278 | 23300
1673 | 1673 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 17 | 17262 | 19077 | 19461 | 19783 | 19336 | 19216 | 21420 | 21284 | 21724 | 20946 | 19579 | 20902 | 23906 | 23017 | 23703 | 22432 | 21086 | 25066 | 24320 | 24246
1674 | 1674 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 18 | 18091 | 19888 | 20515 | 20771 | 20149 | 20394 | 22286 | 22125 | 22694 | 22011 | 20775 | 22341 | 24395 | 24275 | 24939 | 23848 | 22437 | 25664 | 25261 | 25601
1675 | 1675 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 19 | 18885 | 20460 | 21205 | 21472 | 20897 | 21312 | 23264 | 22930 | 23417 | 22989 | 21700 | 23480 | 25451 | 25476 | 26061 | 25382 | 23792 | 26919 | 26507 | 27009
1676 | 1676 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 20 | 19029 | 20713 | 21412 | 21774 | 21261 | 21474 | 23418 | 23317 | 23858 | 23605 | 22310 | 24038 | 25961 | 26406 | 26977 | 26522 | 24914 | 27636 | 27707 | 28183
1677 | 1677 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 21 | 18675 | 20342 | 21092 | 21618 | 21186 | 21205 | 23137 | 23277 | 23930 | 23909 | 22650 | 24212 | 26159 | 27011 | 27746 | 27418 | 25780 | 28070 | 28509 | 29064
1678 | 1678 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 22 | 18001 | 19441 | 20327 | 20870 | 20504 | 20597 | 22345 | 22567 | 23436 | 23456 | 22268 | 23862 | 25648 | 26844 | 27525 | 27313 | 25701 | 27689 | 28318 | 29067
1679 | 1679 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 23 | 17206 | 18317 | 19277 | 19971 | 19531 | 19907 | 21282 | 21581 | 22530 | 22676 | 21686 | 23346 | 24745 | 26114 | 26890 | 26660 | 25223 | 26877 | 27670 | 28429
1680 | 1680 | 70 | 3 | 11 | Winter | 3 | 10 | Winter | 24 | 16485 | 17208 | 18313 | 18979 | 18528 | 19282 | 20204 | 20609 | 21710 | 21813 | 21098 | 22845 | 23836 | 25400 | 25998 | 25776 | 24559 | 26003 | 26887 | 27759
1681 | 1681 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 1 | 16288 | 16821 | 17739 | 18137 | 17847 | 19008 | 19604 | 20357 | 21387 | 20988 | 20104 | 22522 | 23722 | 24955 | 25355 | 24756 | 23064 | 26133 | 26760 | 27381
1682 | 1682 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 2 | 16046 | 16471 | 17439 | 17768 | 17440 | 18758 | 19280 | 20080 | 21173 | 20544 | 19726 | 22221 | 23395 | 24387 | 24705 | 24019 | 22432 | 25756 | 26168 | 26757
1683 | 1683 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 3 | 15978 | 16382 | 17434 | 17823 | 17342 | 18979 | 19453 | 20284 | 21274 | 20706 | 19874 | 22524 | 23414 | 23968 | 24375 | 23566 | 21964 | 25697 | 25812 | 26262
1684 | 1684 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 4 | 16043 | 16391 | 17517 | 17893 | 17274 | 19117 | 19545 | 20262 | 21275 | 20515 | 19720 | 22482 | 23213 | 23650 | 24024 | 23046 | 21618 | 25306 | 25269 | 25753
1685 | 1685 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 5 | 16309 | 16616 | 17664 | 18112 | 17359 | 19236 | 19666 | 20255 | 21170 | 20304 | 19385 | 22250 | 22893 | 23337 | 23633 | 22525 | 21194 | 24736 | 24797 | 25215
1686 | 1686 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 6 | 17082 | 17273 | 18328 | 18823 | 17577 | 19858 | 20325 | 20642 | 21450 | 20158 | 19054 | 22416 | 23075 | 23173 | 23426 | 21898 | 20615 | 24667 | 24547 | 24827
1687 | 1687 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 7 | 18375 | 18476 | 19591 | 19969 | 18061 | 21167 | 21404 | 21633 | 22420 | 20306 | 19024 | 23371 | 23748 | 23900 | 23955 | 21735 | 20303 | 25142 | 24895 | 25417
1688 | 1688 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 8 | 19291 | 19436 | 20523 | 20736 | 18185 | 22155 | 22157 | 22509 | 23305 | 20314 | 19079 | 24298 | 24214 | 24610 | 24534 | 21564 | 20145 | 25484 | 25330 | 26045
1689 | 1689 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 9 | 19213 | 19585 | 20570 | 20734 | 18425 | 22105 | 22120 | 22542 | 23296 | 20524 | 19335 | 24218 | 24017 | 24446 | 24337 | 21571 | 20231 | 25226 | 25044 | 25837
1690 | 1690 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 10 | 19084 | 19569 | 20430 | 20694 | 18513 | 22127 | 22172 | 22531 | 22571 | 20991 | 19678 | 24263 | 23706 | 24182 | 23968 | 21741 | 20221 | 24968 | 24777 | 25597
1691 | 1691 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 11 | 18825 | 19444 | 20262 | 20451 | 18296 | 21939 | 22089 | 22403 | 22025 | 21029 | 19766 | 24082 | 23673 | 23892 | 23707 | 21761 | 20002 | 24996 | 24598 | 25361
1692 | 1692 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 12 | 18672 | 19317 | 20054 | 20062 | 18128 | 21672 | 21886 | 22184 | 21762 | 20784 | 19726 | 23768 | 23475 | 23658 | 23392 | 21659 | 20147 | 24800 | 24585 | 25134
1693 | 1693 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 13 | 18625 | 19122 | 19765 | 19650 | 17922 | 21348 | 21573 | 21774 | 21493 | 20263 | 19448 | 23310 | 23156 | 23642 | 23003 | 21352 | 20199 | 24468 | 24467 | 25104
1694 | 1694 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 14 | 18636 | 19123 | 19773 | 19716 | 17663 | 21553 | 21531 | 21847 | 21178 | 20290 | 19532 | 23522 | 22723 | 23465 | 22733 | 21013 | 19987 | 23995 | 24193 | 24891
1695 | 1695 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 15 | 18700 | 19182 | 19867 | 19745 | 17639 | 21730 | 21569 | 21963 | 21127 | 20394 | 19706 | 23700 | 22577 | 23342 | 22497 | 20862 | 19946 | 23804 | 24058 | 24731
1696 | 1696 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 16 | 18873 | 19337 | 20040 | 19846 | 17728 | 21877 | 21875 | 22081 | 21198 | 20423 | 19944 | 23781 | 22864 | 23331 | 22357 | 20783 | 20087 | 24029 | 24032 | 24651
1697 | 1697 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 17 | 19226 | 19777 | 20510 | 19996 | 18330 | 22237 | 22287 | 22545 | 21968 | 20771 | 20474 | 24183 | 23540 | 23934 | 22729 | 21355 | 20681 | 24728 | 24628 | 25267
1698 | 1698 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 18 | 19517 | 20053 | 20621 | 20011 | 18830 | 22095 | 22075 | 22572 | 22800 | 20752 | 20778 | 24187 | 23929 | 24712 | 23688 | 22255 | 21876 | 25208 | 25529 | 26127
1699 | 1699 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 19 | 20233 | 20442 | 21010 | 20431 | 19200 | 22698 | 22458 | 22882 | 23479 | 21156 | 21394 | 24992 | 24728 | 25577 | 24961 | 23397 | 23213 | 26244 | 26736 | 27177
1700 | 1700 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 20 | 20379 | 20637 | 21339 | 20840 | 19498 | 22900 | 22858 | 23356 | 23832 | 21705 | 21838 | 25430 | 25629 | 26424 | 26034 | 24460 | 24177 | 27423 | 27895 | 28242
1701 | 1701 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 21 | 19968 | 20277 | 21134 | 20692 | 19341 | 22562 | 22727 | 23305 | 23962 | 21926 | 21937 | 25521 | 26087 | 27093 | 26839 | 25257 | 24679 | 28189 | 28745 | 29185
1702 | 1702 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 22 | 19066 | 19496 | 20375 | 19989 | 18683 | 21745 | 21974 | 22742 | 23392 | 21477 | 21527 | 24966 | 25711 | 26842 | 26719 | 25152 | 24519 | 27998 | 28752 | 29080
1703 | 1703 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 23 | 17937 | 18435 | 19452 | 19019 | 17937 | 20669 | 20952 | 21820 | 22613 | 20865 | 20995 | 24052 | 24952 | 26181 | 26041 | 24678 | 24048 | 27338 | 28111 | 28508
1704 | 1704 | 71 | 3 | 12 | Winter | 3 | 11 | Winter | 24 | 16837 | 17489 | 18463 | 18056 | 17209 | 19628 | 20007 | 21029 | 21778 | 20316 | 20612 | 23146 | 24138 | 25297 | 25163 | 24029 | 23550 | 26579 | 27459 | 27676
1705 | 1705 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 1 | 15895 | 16889 | 17590 | 17321 | 16694 | 18924 | 19672 | 20582 | 20993 | 19413 | 19860 | 22915 | 23868 | 24622 | 24144 | 22554 | 22753 | 26401 | 27047 | 27036
1706 | 1706 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 2 | 15553 | 16629 | 17264 | 16912 | 16310 | 18647 | 19458 | 20380 | 20658 | 19143 | 19699 | 22629 | 23358 | 24001 | 23433 | 21939 | 22287 | 25819 | 26435 | 26346
1707 | 1707 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 3 | 15399 | 16478 | 17157 | 16742 | 16270 | 18613 | 19467 | 20422 | 20886 | 19131 | 19911 | 22631 | 23054 | 23657 | 22960 | 21455 | 22051 | 25436 | 25913 | 25932
1708 | 1708 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 4 | 15427 | 16543 | 17220 | 16685 | 16255 | 18714 | 19471 | 20481 | 20886 | 19045 | 19932 | 22499 | 22745 | 23362 | 22487 | 21138 | 21890 | 24905 | 25414 | 25443
1709 | 1709 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 5 | 15691 | 16767 | 17517 | 16830 | 16280 | 18945 | 19602 | 20486 | 20839 | 18854 | 19946 | 22284 | 22584 | 23067 | 22050 | 20779 | 21743 | 24487 | 24920 | 24927
1710 | 1710 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 6 | 16479 | 17464 | 18289 | 17085 | 16350 | 19684 | 20087 | 20851 | 21226 | 18620 | 20418 | 22559 | 22636 | 22945 | 21496 | 20246 | 21928 | 24280 | 24561 | 24579
1711 | 1711 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 7 | 17890 | 18773 | 19501 | 17616 | 16589 | 20850 | 21161 | 21922 | 22242 | 18676 | 21565 | 23335 | 23252 | 23540 | 21397 | 19978 | 22929 | 24670 | 25176 | 25038
1712 | 1712 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 8 | 18868 | 19768 | 20344 | 17836 | 16806 | 21704 | 22145 | 22953 | 23042 | 18835 | 22564 | 23930 | 23909 | 24210 | 21317 | 19904 | 23786 | 25191 | 25877 | 25626
1713 | 1713 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 9 | 18995 | 19994 | 20544 | 18286 | 17380 | 21834 | 22369 | 23172 | 23177 | 19289 | 22811 | 23954 | 23933 | 24222 | 21529 | 20202 | 23856 | 25119 | 25860 | 25579
1714 | 1714 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 10 | 18916 | 19668 | 20291 | 18472 | 17680 | 21513 | 21963 | 22562 | 23079 | 19148 | 22498 | 23604 | 23598 | 23835 | 21689 | 20163 | 23627 | 24838 | 25610 | 25227
1715 | 1715 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 11 | 18673 | 19404 | 19953 | 18402 | 17659 | 21290 | 21705 | 22255 | 22755 | 19095 | 22252 | 23459 | 23279 | 23482 | 21608 | 19842 | 23106 | 24568 | 25271 | 24919
1716 | 1716 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 12 | 18381 | 19030 | 19370 | 18021 | 17446 | 20900 | 21302 | 21763 | 22066 | 18866 | 21955 | 23037 | 23037 | 22930 | 21289 | 19761 | 22959 | 24333 | 24814 | 24390
1717 | 1717 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 13 | 18060 | 18581 | 18786 | 17487 | 17077 | 20440 | 20742 | 21117 | 21256 | 18432 | 21501 | 22468 | 22693 | 22282 | 20715 | 19559 | 22756 | 23953 | 24523 | 23734
1718 | 1718 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 14 | 17820 | 18170 | 18414 | 17013 | 16856 | 19901 | 20279 | 20602 | 21090 | 17935 | 21191 | 21795 | 22179 | 21752 | 20114 | 19099 | 22478 | 23408 | 24044 | 23173
1719 | 1719 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 15 | 17730 | 17998 | 18178 | 16822 | 16809 | 19658 | 20093 | 20400 | 20930 | 17793 | 21117 | 21469 | 21875 | 21332 | 19774 | 18869 | 22316 | 23083 | 23703 | 22717
1720 | 1720 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 16 | 18006 | 18156 | 18275 | 16896 | 17104 | 19947 | 20190 | 20459 | 20940 | 18005 | 21303 | 21755 | 21905 | 21217 | 19712 | 19019 | 22439 | 23062 | 23633 | 22534
1721 | 1721 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 17 | 18718 | 18938 | 18742 | 17636 | 17843 | 20733 | 21032 | 21330 | 21414 | 18943 | 22247 | 22674 | 22714 | 21830 | 20526 | 19856 | 23364 | 23894 | 24485 | 23149
1722 | 1722 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 18 | 19165 | 19707 | 19434 | 18417 | 18518 | 21414 | 21985 | 22383 | 21668 | 20213 | 22945 | 23404 | 23868 | 23127 | 21769 | 21407 | 24309 | 25156 | 25717 | 24538
1723 | 1723 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 19 | 19581 | 20278 | 20029 | 18796 | 19210 | 21980 | 22470 | 22996 | 22313 | 20962 | 23392 | 24271 | 24947 | 24486 | 23007 | 22843 | 25254 | 26483 | 26907 | 26094
1724 | 1724 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 20 | 19841 | 20613 | 20424 | 19131 | 19343 | 22367 | 22898 | 23354 | 22899 | 21328 | 23740 | 25100 | 25789 | 25506 | 24020 | 23780 | 26168 | 27632 | 27981 | 27346
1725 | 1725 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 21 | 19415 | 20402 | 20257 | 18948 | 19064 | 22186 | 22795 | 23407 | 23084 | 21340 | 23692 | 25462 | 26296 | 26248 | 24764 | 24269 | 26488 | 28485 | 28931 | 28358
1726 | 1726 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 22 | 18484 | 19627 | 19528 | 18254 | 18407 | 21386 | 22174 | 22769 | 22553 | 20871 | 22915 | 25011 | 26064 | 26057 | 24605 | 24080 | 25925 | 28467 | 28809 | 28323
1727 | 1727 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 23 | 17346 | 18677 | 18538 | 17490 | 17720 | 20336 | 21211 | 21941 | 21736 | 20315 | 21962 | 24208 | 25318 | 25349 | 24107 | 23580 | 25039 | 27816 | 28228 | 27698
1728 | 1728 | 72 | 3 | 13 | Winter | 3 | 12 | Winter | 24 | 16263 | 17651 | 17534 | 16763 | 17174 | 19347 | 20374 | 21101 | 20899 | 19901 | 21070 | 23364 | 24621 | 24447 | 23445 | 23071 | 24027 | 27147 | 27384 | 26851
1729 | 1729 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 1 | 15939 | 16836 | 16859 | 16322 | 16503 | 18975 | 19887 | 20278 | 20165 | 19156 | 20085 | 23156 | 24215 | 23557 | 22137 | 22376 | 23446 | 26815 | 26836 | 25875
1730 | 1730 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 2 | 15613 | 16377 | 16316 | 15814 | 16291 | 18555 | 19467 | 19786 | 19789 | 18767 | 19647 | 22640 | 23653 | 22854 | 21521 | 21894 | 22909 | 26195 | 26127 | 25103
1731 | 1731 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 3 | 15449 | 16155 | 16011 | 15510 | 16414 | 18363 | 19304 | 19642 | 19783 | 18777 | 19524 | 22398 | 23247 | 22424 | 21082 | 21705 | 22638 | 25703 | 25741 | 24609
1732 | 1732 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 4 | 15474 | 16216 | 15963 | 15500 | 16556 | 18395 | 19407 | 19702 | 19651 | 18877 | 19413 | 22162 | 23000 | 22013 | 20803 | 21577 | 22253 | 25231 | 25267 | 24010
1733 | 1733 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 5 | 15747 | 16564 | 16186 | 15642 | 16852 | 18663 | 19571 | 19880 | 19576 | 19079 | 19394 | 22074 | 22783 | 21626 | 20474 | 21452 | 21895 | 24745 | 24754 | 23398
1734 | 1734 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 6 | 16427 | 17361 | 16497 | 15770 | 17726 | 19228 | 20043 | 20403 | 19541 | 19648 | 19833 | 22212 | 22712 | 21128 | 19975 | 21667 | 21951 | 24399 | 24407 | 22671
1735 | 1735 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 7 | 17665 | 18589 | 17063 | 16030 | 19176 | 20362 | 21179 | 21507 | 19778 | 20858 | 20537 | 22893 | 23512 | 21067 | 19729 | 22676 | 22295 | 25015 | 24861 | 22459
1736 | 1736 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 8 | 18722 | 19432 | 17292 | 16234 | 20176 | 21350 | 22214 | 22316 | 19905 | 21857 | 20783 | 23604 | 24330 | 21022 | 19681 | 23555 | 22348 | 25727 | 25461 | 22341
1737 | 1737 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 9 | 19209 | 19746 | 17888 | 16906 | 20550 | 21697 | 22567 | 22549 | 20463 | 22229 | 20793 | 23789 | 24527 | 21394 | 20137 | 23772 | 22239 | 25874 | 25562 | 22680
1738 | 1738 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 10 | 19126 | 19726 | 18316 | 17153 | 20496 | 21538 | 22215 | 22286 | 20602 | 22155 | 20699 | 23581 | 24372 | 21670 | 20219 | 23679 | 22152 | 25750 | 25339 | 22997
1739 | 1739 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 11 | 19043 | 19523 | 18380 | 17227 | 20400 | 21370 | 21986 | 22006 | 20662 | 21967 | 20629 | 23415 | 24141 | 21741 | 20053 | 23316 | 21921 | 25571 | 25186 | 23115
1740 | 1740 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 12 | 18919 | 19258 | 18306 | 17357 | 20347 | 21303 | 21846 | 21710 | 20434 | 22041 | 20533 | 23381 | 23877 | 21634 | 20190 | 23384 | 21654 | 25323 | 24861 | 23007
1741 | 1741 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 13 | 18674 | 18972 | 18091 | 17372 | 20157 | 21121 | 21595 | 21389 | 19927 | 22004 | 20392 | 23178 | 23759 | 21226 | 20153 | 23323 | 21468 | 25194 | 24368 | 22580
1742 | 1742 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 14 | 18259 | 18602 | 17607 | 16927 | 19911 | 20654 | 21080 | 20918 | 19366 | 21687 | 20075 | 22641 | 23308 | 20603 | 19661 | 23014 | 21149 | 24688 | 23784 | 21927
1743 | 1743 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 15 | 18057 | 18317 | 17350 | 16730 | 19848 | 20387 | 20797 | 20550 | 19138 | 21515 | 19941 | 22327 | 22986 | 20248 | 19416 | 22832 | 21004 | 24323 | 23317 | 21547
1744 | 1744 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 16 | 18146 | 18352 | 17394 | 16971 | 20052 | 20471 | 20853 | 20522 | 19085 | 21699 | 20347 | 22323 | 22942 | 20145 | 19517 | 22915 | 21404 | 24202 | 23082 | 21402
1745 | 1745 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 17 | 18651 | 18567 | 17861 | 17554 | 20668 | 21048 | 21459 | 20889 | 19593 | 22387 | 20756 | 22889 | 23547 | 20718 | 20110 | 23597 | 21862 | 24820 | 23464 | 21994
1746 | 1746 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 18 | 19184 | 18854 | 18219 | 18269 | 20706 | 21643 | 22125 | 21353 | 20172 | 22699 | 20740 | 23637 | 24279 | 21564 | 21270 | 24141 | 22256 | 25657 | 24456 | 22921
1747 | 1747 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 19 | 19595 | 19343 | 18512 | 18925 | 20860 | 22073 | 22669 | 21990 | 20568 | 23075 | 21527 | 24494 | 25062 | 22585 | 22523 | 24900 | 23514 | 26677 | 25858 | 24118
1748 | 1748 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 20 | 19727 | 19635 | 18743 | 18947 | 21036 | 22349 | 22866 | 22385 | 21024 | 23180 | 22127 | 25199 | 25799 | 23497 | 23355 | 25745 | 24527 | 27696 | 27063 | 25252
1749 | 1749 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 21 | 19357 | 19437 | 18506 | 18643 | 20629 | 22171 | 22833 | 22467 | 21143 | 23025 | 22289 | 25595 | 26384 | 24147 | 23780 | 26027 | 25177 | 28615 | 28055 | 26168
1750 | 1750 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 22 | 18538 | 18705 | 17796 | 17979 | 19661 | 21511 | 22147 | 21889 | 20623 | 22201 | 21816 | 25308 | 26064 | 23945 | 23557 | 25452 | 25018 | 28485 | 28017 | 26109
1751 | 1751 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 23 | 17478 | 17708 | 17023 | 17274 | 18575 | 20527 | 21302 | 21022 | 19979 | 21230 | 20999 | 24535 | 25392 | 23436 | 23056 | 24557 | 24294 | 27911 | 27405 | 25685
1752 | 1752 | 73 | 3 | 14 | Winter | 3 | 13 | Winter | 24 | 16532 | 16708 | 16267 | 16699 | 17556 | 19651 | 20404 | 20122 | 19406 | 20304 | 20311 | 23811 | 24500 | 22774 | 22552 | 23554 | 23572 | 27083 | 26579 | 25067
1753 | 1753 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 1 | 15961 | 16021 | 15847 | 15946 | 16395 | 19097 | 19523 | 19273 | 18577 | 19235 | 20530 | 23372 | 23905 | 21526 | 21852 | 22942 | 24118 | 26498 | 25574 | 23519
1754 | 1754 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 2 | 15615 | 15481 | 15346 | 15582 | 16035 | 18665 | 19022 | 18676 | 18090 | 18805 | 20199 | 22858 | 23290 | 20936 | 21404 | 22426 | 23734 | 25813 | 24819 | 22882
1755 | 1755 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 3 | 15389 | 15112 | 14950 | 15427 | 15920 | 18381 | 18752 | 18295 | 17854 | 18570 | 20092 | 22478 | 22995 | 20509 | 21225 | 22154 | 23573 | 25426 | 24321 | 22406
1756 | 1756 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 4 | 15460 | 15048 | 14909 | 15551 | 15977 | 18473 | 18819 | 18196 | 17813 | 18505 | 20021 | 22287 | 22766 | 20277 | 21123 | 21790 | 23266 | 24960 | 23721 | 22013
1757 | 1757 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 5 | 15763 | 15300 | 15121 | 16015 | 16349 | 18757 | 19141 | 18409 | 17822 | 18674 | 20169 | 22176 | 22555 | 20013 | 21059 | 21494 | 22942 | 24486 | 23141 | 21569
1758 | 1758 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 6 | 16487 | 15677 | 15305 | 16960 | 17232 | 19310 | 19780 | 18535 | 17703 | 19226 | 20695 | 22204 | 22512 | 19570 | 21313 | 21593 | 23077 | 24160 | 22431 | 20944
1759 | 1759 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 7 | 17819 | 16286 | 15654 | 18488 | 18316 | 20548 | 21024 | 18943 | 17834 | 20094 | 21569 | 23097 | 23189 | 19379 | 22364 | 21997 | 23636 | 24649 | 22241 | 20638
1760 | 1760 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 8 | 18747 | 16482 | 15836 | 19400 | 18765 | 21553 | 21819 | 19028 | 17955 | 20347 | 22175 | 23920 | 23851 | 19311 | 23217 | 22043 | 24033 | 25218 | 22084 | 20518
1761 | 1761 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 9 | 19073 | 17073 | 16519 | 19728 | 18886 | 21918 | 22074 | 19570 | 18515 | 20395 | 22179 | 24116 | 24009 | 19753 | 23422 | 21923 | 23837 | 25308 | 22396 | 20940
1762 | 1762 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 10 | 18940 | 17657 | 16924 | 19914 | 18844 | 21766 | 22021 | 20043 | 18637 | 20514 | 22123 | 23951 | 23742 | 19831 | 23331 | 21828 | 23492 | 25086 | 22725 | 21062
1763 | 1763 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 11 | 18717 | 17664 | 16932 | 19685 | 18658 | 21445 | 21646 | 19932 | 18561 | 20340 | 21994 | 23627 | 23446 | 19567 | 22872 | 21507 | 23136 | 24832 | 22743 | 20835
1764 | 1764 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 12 | 18502 | 17388 | 16849 | 19537 | 18408 | 21062 | 21091 | 19597 | 18556 | 19959 | 21802 | 23220 | 22959 | 19550 | 22784 | 21088 | 23044 | 24354 | 22489 | 20828
1765 | 1765 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 13 | 18234 | 17147 | 16859 | 19540 | 18187 | 20851 | 20821 | 19408 | 18439 | 19902 | 21664 | 23016 | 22375 | 19418 | 22634 | 20813 | 22677 | 23770 | 21965 | 20679
1766 | 1766 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 14 | 17854 | 16806 | 16554 | 19443 | 18003 | 20515 | 20537 | 19043 | 17985 | 19793 | 21527 | 22623 | 21872 | 18995 | 22393 | 20547 | 22385 | 23245 | 21383 | 20231
1767 | 1767 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 15 | 17777 | 16704 | 16530 | 19498 | 18074 | 20425 | 20361 | 18919 | 17896 | 19850 | 21506 | 22460 | 21590 | 18906 | 22366 | 20552 | 22316 | 22926 | 21155 | 20122
1768 | 1768 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 16 | 17859 | 16729 | 16743 | 19716 | 18371 | 20483 | 20338 | 18911 | 18057 | 20253 | 21663 | 22398 | 21394 | 18972 | 22406 | 20913 | 22319 | 22650 | 20964 | 20157
1769 | 1769 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 17 | 18442 | 17196 | 17321 | 20318 | 18689 | 21086 | 20697 | 19391 | 18777 | 20652 | 22102 | 23048 | 21814 | 19611 | 23137 | 21434 | 22899 | 23071 | 21593 | 20817
1770 | 1770 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 18 | 18921 | 17506 | 17934 | 20296 | 18753 | 21639 | 20998 | 19819 | 19771 | 20446 | 22321 | 23811 | 22790 | 20841 | 23748 | 21899 | 23503 | 24159 | 22612 | 22118
1771 | 1771 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 19 | 19492 | 17837 | 18617 | 20556 | 19377 | 22182 | 21606 | 20304 | 20550 | 21139 | 23100 | 24618 | 24017 | 22124 | 24557 | 23210 | 24911 | 25635 | 23904 | 23551
1772 | 1772 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 20 | 19770 | 18089 | 18669 | 20691 | 19700 | 22390 | 21996 | 20627 | 20744 | 21651 | 23849 | 25294 | 24948 | 22961 | 25394 | 24211 | 26421 | 26867 | 25070 | 24551
1773 | 1773 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 21 | 19541 | 17816 | 18333 | 20265 | 19381 | 22310 | 22003 | 20652 | 20686 | 21702 | 24059 | 25785 | 25591 | 23326 | 25629 | 24810 | 27157 | 27843 | 25977 | 25128
1774 | 1774 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 22 | 18770 | 17124 | 17659 | 19314 | 18636 | 21605 | 21376 | 20088 | 20180 | 21200 | 23671 | 25410 | 25361 | 23072 | 25036 | 24633 | 27103 | 27807 | 25928 | 24990
1775 | 1775 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 23 | 17796 | 16300 | 16909 | 18182 | 17577 | 20688 | 20433 | 19346 | 19574 | 20271 | 22905 | 24693 | 24621 | 22550 | 24117 | 23896 | 26505 | 27187 | 25499 | 24544
1776 | 1776 | 74 | 3 | 15 | Winter | 3 | 14 | Winter | 24 | 16759 | 15442 | 16214 | 17020 | 16741 | 19636 | 19355 | 18549 | 19101 | 19398 | 22163 | 23771 | 23725 | 22016 | 23101 | 23153 | 25849 | 26339 | 24868 | 24049
1777 | 1777 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 1 | 15956 | 15187 | 15594 | 16006 | 16815 | 18920 | 18717 | 17987 | 18353 | 19821 | 22066 | 23174 | 22876 | 21354 | 22482 | 23698 | 25855 | 25357 | 23364 | 23346
1778 | 1778 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 2 | 15517 | 14731 | 15263 | 15654 | 16563 | 18456 | 18162 | 17514 | 17964 | 19562 | 21730 | 22588 | 22202 | 20926 | 21991 | 23331 | 25421 | 24621 | 22732 | 22878
1779 | 1779 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 3 | 15233 | 14365 | 15150 | 15494 | 16507 | 18256 | 17864 | 17231 | 17839 | 19591 | 21675 | 22313 | 21790 | 20764 | 21737 | 23176 | 25197 | 24118 | 22248 | 22668
1780 | 1780 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 4 | 15275 | 14316 | 15271 | 15556 | 16618 | 18359 | 17822 | 17235 | 17944 | 19630 | 21617 | 22142 | 21422 | 20687 | 21404 | 22891 | 24841 | 23527 | 21855 | 22458
1781 | 1781 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 5 | 15681 | 14478 | 15690 | 15948 | 17021 | 18646 | 18018 | 17300 | 18300 | 19780 | 21572 | 22016 | 21129 | 20670 | 21157 | 22609 | 24466 | 22970 | 21422 | 22263
1782 | 1782 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 6 | 16481 | 14651 | 16625 | 16832 | 17890 | 19278 | 18162 | 17215 | 18946 | 20315 | 21718 | 22060 | 20692 | 20957 | 21296 | 22767 | 24293 | 22279 | 20796 | 22396
1783 | 1783 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 7 | 17740 | 14944 | 18116 | 17936 | 19149 | 20470 | 18557 | 17395 | 20280 | 21177 | 22488 | 22790 | 20694 | 22025 | 21719 | 23344 | 24742 | 22078 | 20474 | 23375
1784 | 1784 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 8 | 18398 | 15034 | 18921 | 18306 | 19851 | 21177 | 18568 | 17451 | 21123 | 21733 | 23013 | 23369 | 20502 | 22757 | 21658 | 23631 | 25013 | 21787 | 20216 | 24061
1785 | 1785 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 9 | 18118 | 15137 | 18673 | 17848 | 19399 | 20845 | 18521 | 17445 | 20943 | 21157 | 22558 | 22959 | 20294 | 22399 | 20969 | 22874 | 24459 | 21525 | 20060 | 23665
1786 | 1786 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 10 | 17775 | 15032 | 18337 | 17393 | 18899 | 20209 | 18376 | 17152 | 20661 | 20427 | 21779 | 22244 | 20128 | 21856 | 20424 | 22078 | 23616 | 21401 | 19737 | 23168
1787 | 1787 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 11 | 17381 | 14984 | 18060 | 17144 | 18663 | 19777 | 18218 | 17036 | 20275 | 20244 | 21406 | 21840 | 19992 | 21285 | 19983 | 21610 | 22937 | 21309 | 19408 | 22636
1788 | 1788 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 12 | 17010 | 15013 | 18016 | 16925 | 18551 | 19347 | 18012 | 17035 | 20146 | 20175 | 21123 | 21414 | 19804 | 21274 | 19647 | 21579 | 22683 | 21128 | 19459 | 22618
1789 | 1789 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 13 | 16849 | 15047 | 17992 | 16788 | 18511 | 18976 | 17700 | 16953 | 20331 | 19864 | 20667 | 20979 | 19447 | 21258 | 19515 | 21369 | 22316 | 20754 | 19453 | 22598
1790 | 1790 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 14 | 16726 | 14780 | 17937 | 16743 | 18506 | 18704 | 17334 | 16631 | 20333 | 19702 | 20331 | 20619 | 19009 | 21141 | 19374 | 21212 | 21963 | 20286 | 19125 | 22453
1791 | 1791 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 15 | 16521 | 14645 | 17888 | 16736 | 18428 | 18426 | 17100 | 16460 | 20263 | 19564 | 20180 | 20261 | 18720 | 21032 | 19294 | 21060 | 21776 | 19971 | 18926 | 22321
1792 | 1792 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 16 | 16700 | 15010 | 18249 | 17176 | 18816 | 18554 | 17234 | 16797 | 20620 | 19864 | 20269 | 20259 | 18754 | 21252 | 19840 | 21234 | 21714 | 19951 | 19131 | 22507
1793 | 1793 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 17 | 17241 | 15882 | 19138 | 17755 | 19580 | 19216 | 18010 | 17760 | 21584 | 20611 | 21061 | 20970 | 19673 | 22278 | 20654 | 22103 | 22459 | 20875 | 20085 | 23556
1794 | 1794 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 18 | 17898 | 17007 | 19646 | 18274 | 20183 | 20164 | 19083 | 19173 | 22131 | 21534 | 22249 | 22305 | 20981 | 23285 | 21513 | 23108 | 23828 | 22292 | 21794 | 24640
1795 | 1795 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 19 | 18581 | 17927 | 20178 | 19102 | 20808 | 21081 | 19885 | 20179 | 22620 | 22604 | 23196 | 23630 | 22197 | 24217 | 22939 | 24637 | 25263 | 23736 | 23394 | 25709
1796 | 1796 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 20 | 18886 | 18022 | 20367 | 19460 | 21222 | 21535 | 20264 | 20423 | 22694 | 23369 | 24039 | 24445 | 23067 | 24991 | 23877 | 26091 | 26729 | 24887 | 24388 | 26640
1797 | 1797 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 21 | 18689 | 17688 | 19938 | 19108 | 20926 | 21490 | 20223 | 20286 | 22486 | 23470 | 24554 | 24992 | 23647 | 25181 | 24413 | 26780 | 27794 | 25782 | 24960 | 27021
1798 | 1798 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 22 | 17953 | 17013 | 18962 | 18320 | 20204 | 20832 | 19608 | 19720 | 21616 | 23006 | 24129 | 24692 | 23410 | 24549 | 24201 | 26689 | 27658 | 25720 | 24819 | 26503
1799 | 1799 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 23 | 16916 | 16233 | 17818 | 17218 | 19260 | 19861 | 18833 | 19039 | 20552 | 22189 | 23315 | 23919 | 22860 | 23615 | 23437 | 26081 | 26990 | 25279 | 24364 | 25625
1800 | 1800 | 75 | 3 | 16 | Winter | 3 | 15 | Winter | 24 | 15858 | 15552 | 16678 | 16311 | 18421 | 18803 | 18049 | 18431 | 19449 | 21462 | 22612 | 23015 | 22175 | 22604 | 22710 | 25438 | 26360 | 24666 | 23890 | 24642
1801 | 1801 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 1 | 15526 | 15153 | 15877 | 16693 | 18344 | 18379 | 17760 | 18066 | 18767 | 21564 | 22140 | 22405 | 21266 | 22178 | 23452 | 25649 | 25925 | 23414 | 23407 | 24346
1802 | 1802 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 2 | 15027 | 14830 | 15536 | 16463 | 18061 | 17825 | 17286 | 17718 | 18394 | 21258 | 21649 | 21754 | 20700 | 21698 | 23104 | 25225 | 25318 | 22780 | 22933 | 23815
1803 | 1803 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 3 | 14707 | 14675 | 15353 | 16447 | 18026 | 17500 | 16980 | 17673 | 18260 | 21223 | 21525 | 21359 | 20276 | 21453 | 22947 | 24991 | 25085 | 22283 | 22717 | 23507
1804 | 1804 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 4 | 14674 | 14779 | 15402 | 16580 | 18169 | 17468 | 17000 | 17842 | 18286 | 21246 | 21435 | 21062 | 20081 | 21172 | 22716 | 24675 | 24610 | 21905 | 22514 | 23059
1805 | 1805 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 5 | 14893 | 15192 | 15801 | 16947 | 18471 | 17700 | 17107 | 18171 | 18443 | 21294 | 21339 | 20849 | 19884 | 20982 | 22484 | 24348 | 24137 | 21491 | 22328 | 22655
1806 | 1806 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 6 | 15262 | 16155 | 16713 | 17835 | 19099 | 17913 | 17103 | 18865 | 19011 | 21551 | 21624 | 20531 | 19500 | 21190 | 22705 | 24239 | 24050 | 20888 | 22474 | 22642
1807 | 1807 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 7 | 15835 | 17663 | 17874 | 19078 | 20168 | 18352 | 17346 | 20196 | 19871 | 22408 | 22528 | 20611 | 19343 | 21656 | 23329 | 24716 | 24632 | 20579 | 23454 | 22952
1808 | 1808 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 8 | 15877 | 18404 | 18221 | 19770 | 20757 | 18314 | 17366 | 21043 | 20029 | 22923 | 23100 | 20402 | 19110 | 21572 | 23588 | 24950 | 24958 | 20277 | 24086 | 22752
1809 | 1809 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 9 | 15958 | 18250 | 17894 | 19398 | 20535 | 18366 | 17471 | 20941 | 19575 | 22566 | 22687 | 20308 | 19069 | 20994 | 22935 | 24480 | 24409 | 20206 | 23785 | 22116
1810 | 1810 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 10 | 16252 | 18180 | 17697 | 18998 | 20092 | 18469 | 17421 | 20691 | 19261 | 21995 | 22064 | 20349 | 18918 | 20661 | 22355 | 23843 | 23851 | 20100 | 23508 | 21833
1811 | 1811 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 11 | 16227 | 17955 | 17493 | 18845 | 19735 | 18349 | 17339 | 20404 | 19063 | 21641 | 21640 | 20233 | 18569 | 20240 | 21909 | 23194 | 23469 | 19791 | 23005 | 21465
1812 | 1812 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 12 | 16120 | 17983 | 17346 | 18835 | 19521 | 18209 | 17402 | 20402 | 18887 | 21419 | 21372 | 20099 | 18686 | 19966 | 21947 | 22994 | 23262 | 19918 | 23056 | 21193
1813 | 1813 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 13 | 15805 | 17896 | 17135 | 18509 | 19068 | 17827 | 17244 | 20208 | 18581 | 20884 | 20921 | 19655 | 18613 | 19750 | 21646 | 22541 | 22925 | 19827 | 22940 | 20962
1814 | 1814 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 14 | 15460 | 17797 | 17034 | 18349 | 18770 | 17406 | 16867 | 20014 | 18385 | 20494 | 20529 | 19162 | 18244 | 19548 | 21426 | 22130 | 22549 | 19434 | 22729 | 20727
1815 | 1815 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 15 | 15247 | 17742 | 17023 | 18248 | 18701 | 17175 | 16696 | 19914 | 18323 | 20344 | 20261 | 18875 | 18064 | 19468 | 21270 | 21943 | 22260 | 19229 | 22590 | 20619
1816 | 1816 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 16 | 15430 | 18099 | 17397 | 18610 | 18913 | 17319 | 17039 | 20239 | 18850 | 20457 | 20306 | 18930 | 18310 | 20027 | 21454 | 21895 | 22182 | 19433 | 22776 | 21132
1817 | 1817 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 17 | 16160 | 18934 | 17939 | 19354 | 19623 | 18064 | 17967 | 21186 | 19524 | 21221 | 21186 | 19824 | 19213 | 20818 | 22304 | 22616 | 22987 | 20358 | 23798 | 21944
1818 | 1818 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 18 | 16918 | 19316 | 18377 | 20091 | 20460 | 19038 | 19257 | 21909 | 19954 | 22291 | 22123 | 21014 | 20750 | 21584 | 23210 | 23902 | 24043 | 21995 | 24807 | 22787
1819 | 1819 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 19 | 17430 | 19774 | 19132 | 20765 | 21106 | 19751 | 20166 | 22485 | 20903 | 23087 | 22950 | 22098 | 22103 | 22892 | 24628 | 25246 | 25205 | 23523 | 25817 | 24282
1820 | 1820 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 20 | 17707 | 19952 | 19463 | 21221 | 21538 | 20103 | 20376 | 22618 | 21448 | 23816 | 23671 | 22864 | 22861 | 23752 | 26005 | 26661 | 26412 | 24497 | 26737 | 25367
1821 | 1821 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 21 | 17418 | 19524 | 19069 | 20868 | 21533 | 19999 | 20186 | 22339 | 21416 | 24198 | 23923 | 23332 | 23158 | 24216 | 26625 | 27655 | 27178 | 25058 | 27115 | 26087
1822 | 1822 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 22 | 16707 | 18529 | 18255 | 20107 | 20840 | 19355 | 19585 | 21428 | 20836 | 23713 | 23448 | 23023 | 22865 | 23959 | 26485 | 27496 | 27027 | 24912 | 26586 | 25973
1823 | 1823 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 23 | 15863 | 17361 | 17134 | 19145 | 19850 | 18557 | 18867 | 20325 | 19857 | 22853 | 22601 | 22433 | 22313 | 23160 | 25846 | 26805 | 26339 | 24442 | 25699 | 25267
1824 | 1824 | 76 | 3 | 17 | Winter | 3 | 16 | Winter | 24 | 15011 | 16212 | 16185 | 18295 | 18999 | 17732 | 18214 | 19202 | 18982 | 22098 | 21762 | 21714 | 21769 | 22392 | 25165 | 26155 | 25594 | 23935 | 24689 | 24546
1825 | 1825 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 1 | 14529 | 14994 | 16084 | 17718 | 17905 | 17035 | 17375 | 17973 | 19086 | 21161 | 20814 | 20450 | 20855 | 22651 | 24901 | 25250 | 24473 | 22987 | 23916 | 24901
1826 | 1826 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 2 | 14093 | 14663 | 15873 | 17444 | 17516 | 16566 | 17032 | 17618 | 18855 | 20708 | 20282 | 19906 | 20444 | 22322 | 24506 | 24664 | 23824 | 22520 | 23394 | 24520
1827 | 1827 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 3 | 13720 | 14463 | 15838 | 17385 | 17439 | 16229 | 16955 | 17465 | 18891 | 20590 | 20047 | 19517 | 20286 | 22196 | 24306 | 24455 | 23491 | 22301 | 23109 | 24340
1828 | 1828 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 4 | 13672 | 14495 | 15970 | 17532 | 17561 | 16269 | 17159 | 17541 | 18981 | 20611 | 19878 | 19375 | 20266 | 22013 | 24036 | 24001 | 22971 | 22112 | 22661 | 23984
1829 | 1829 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 5 | 13825 | 14889 | 16338 | 17847 | 17817 | 16399 | 17525 | 17753 | 19193 | 20608 | 19686 | 19233 | 20295 | 21832 | 23753 | 23556 | 22414 | 21938 | 22259 | 23583
1830 | 1830 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 6 | 14031 | 15841 | 17262 | 18561 | 18644 | 16472 | 18322 | 18447 | 19831 | 21035 | 19705 | 18940 | 20654 | 22122 | 23702 | 23536 | 21974 | 22111 | 22267 | 23640
1831 | 1831 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 7 | 14333 | 17041 | 18530 | 19660 | 19955 | 16752 | 19713 | 19394 | 20769 | 22032 | 19825 | 18843 | 21756 | 22800 | 24220 | 24146 | 21727 | 23093 | 22583 | 24121
1832 | 1832 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 8 | 14469 | 17478 | 19270 | 20286 | 20678 | 16814 | 20614 | 19635 | 21379 | 22675 | 19730 | 18706 | 22528 | 23166 | 24544 | 24558 | 21558 | 23801 | 22463 | 24368
1833 | 1833 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 9 | 14915 | 17417 | 19162 | 20319 | 20575 | 17161 | 20764 | 19476 | 21171 | 22515 | 19986 | 18934 | 22517 | 22770 | 24324 | 24265 | 21725 | 23746 | 22076 | 23905
1834 | 1834 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 10 | 15167 | 17357 | 18893 | 20000 | 20190 | 17208 | 20597 | 19247 | 20793 | 21932 | 20067 | 18897 | 22309 | 22302 | 23807 | 23819 | 21870 | 23583 | 21913 | 23487
1835 | 1835 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 11 | 15173 | 17048 | 18629 | 19514 | 19766 | 16937 | 20095 | 18818 | 20652 | 21228 | 19713 | 18552 | 21774 | 21859 | 23161 | 23445 | 21778 | 23081 | 21553 | 23084
1836 | 1836 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 12 | 15216 | 16883 | 18594 | 19279 | 19439 | 16983 | 20071 | 18627 | 20592 | 20951 | 19499 | 18611 | 21771 | 21841 | 22906 | 23171 | 21489 | 23077 | 21225 | 23076
1837 | 1837 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 13 | 15201 | 16753 | 18368 | 18945 | 19078 | 16950 | 20010 | 18459 | 20217 | 20655 | 19164 | 18556 | 21692 | 21557 | 22471 | 22856 | 20988 | 22985 | 21009 | 22781
1838 | 1838 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 14 | 14835 | 16680 | 18221 | 18680 | 18742 | 16607 | 19857 | 18310 | 19967 | 20313 | 18663 | 18168 | 21483 | 21314 | 22038 | 22459 | 20351 | 22748 | 20748 | 22513
1839 | 1839 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 15 | 14546 | 16549 | 17998 | 18500 | 18403 | 16326 | 19649 | 18141 | 19684 | 19945 | 18298 | 17852 | 21225 | 21023 | 21717 | 22033 | 19900 | 22469 | 20503 | 22202
1840 | 1840 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 16 | 14805 | 16770 | 18247 | 18606 | 18462 | 16554 | 19859 | 18505 | 19890 | 19885 | 18352 | 18009 | 21349 | 21115 | 21578 | 21862 | 19877 | 22551 | 20916 | 22255
1841 | 1841 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 17 | 15535 | 17164 | 18856 | 19191 | 19174 | 17351 | 20671 | 19052 | 20496 | 20638 | 19158 | 18797 | 22236 | 21845 | 22181 | 22556 | 20744 | 23457 | 21602 | 23006
1842 | 1842 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 18 | 16470 | 17473 | 19475 | 19861 | 19671 | 18491 | 21217 | 19328 | 21244 | 21381 | 20024 | 20201 | 23072 | 22641 | 23361 | 23520 | 21967 | 24373 | 22362 | 23909
1843 | 1843 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 19 | 17322 | 18238 | 20150 | 20490 | 20180 | 19402 | 21788 | 20244 | 22187 | 22148 | 20873 | 21503 | 23900 | 24015 | 24672 | 24653 | 23198 | 25389 | 23873 | 25483
1844 | 1844 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 20 | 17389 | 18613 | 20661 | 20999 | 20594 | 19722 | 22030 | 20859 | 22855 | 22909 | 21502 | 22196 | 24607 | 25334 | 26031 | 25817 | 24052 | 26316 | 24944 | 27042
1845 | 1845 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 21 | 17020 | 18178 | 20249 | 20915 | 20319 | 19470 | 21668 | 20716 | 22828 | 23022 | 21702 | 22396 | 24698 | 25847 | 26935 | 26507 | 24761 | 26658 | 25641 | 27841
1846 | 1846 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 22 | 16320 | 17325 | 19454 | 20193 | 19517 | 18834 | 20720 | 20066 | 22286 | 22465 | 21272 | 22035 | 24026 | 25652 | 26727 | 26325 | 24634 | 26123 | 25510 | 27812
1847 | 1847 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 23 | 15533 | 16216 | 18502 | 19225 | 18522 | 18121 | 19622 | 19083 | 21448 | 21605 | 20566 | 21464 | 23082 | 25012 | 26042 | 25641 | 24098 | 25260 | 24826 | 27265
1848 | 1848 | 77 | 3 | 18 | Winter | 3 | 17 | Winter | 24 | 14805 | 15253 | 17637 | 18362 | 17538 | 17460 | 18482 | 18172 | 20678 | 20742 | 19881 | 20897 | 22037 | 24315 | 25382 | 24876 | 23521 | 24246 | 24102 | 26624
1849 | 1849 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 1 | 14237 | 15449 | 17327 | 17558 | 17030 | 16894 | 17483 | 18528 | 20570 | 20118 | 18954 | 20297 | 21378 | 24314 | 24757 | 24071 | 22094 | 23736 | 24733 | 26695
1850 | 1850 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 2 | 13934 | 15260 | 17078 | 17183 | 16578 | 16559 | 17142 | 18315 | 20300 | 19628 | 18586 | 19912 | 20934 | 23950 | 24205 | 23443 | 21645 | 23224 | 24365 | 26267
1851 | 1851 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 3 | 13750 | 15204 | 17004 | 17065 | 16368 | 16458 | 16978 | 18316 | 20238 | 19424 | 18442 | 19770 | 20709 | 23764 | 24004 | 23121 | 21439 | 22929 | 24178 | 26008
1852 | 1852 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 4 | 13876 | 15333 | 17147 | 17211 | 16381 | 16666 | 17084 | 18474 | 20351 | 19342 | 18318 | 19813 | 20493 | 23564 | 23616 | 22654 | 21011 | 22508 | 23841 | 25615
1853 | 1853 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 5 | 14280 | 15677 | 17468 | 17487 | 16568 | 17048 | 17339 | 18746 | 20467 | 19227 | 18187 | 19898 | 20354 | 23339 | 23220 | 22126 | 20536 | 22121 | 23445 | 25166
1854 | 1854 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 6 | 15289 | 16618 | 18233 | 18399 | 17069 | 17896 | 18119 | 19508 | 20876 | 19348 | 18048 | 20348 | 20652 | 23368 | 23265 | 21739 | 20097 | 22163 | 23525 | 24971
1855 | 1855 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 7 | 16804 | 17919 | 19341 | 19728 | 17488 | 19293 | 19127 | 20505 | 21808 | 19526 | 18012 | 21493 | 21172 | 23910 | 23888 | 21504 | 19888 | 22473 | 23998 | 25368
1856 | 1856 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 8 | 17548 | 18641 | 19935 | 20390 | 17501 | 20149 | 19377 | 21071 | 22344 | 19433 | 17958 | 22255 | 21160 | 24216 | 24285 | 21302 | 19713 | 22331 | 24215 | 25601
1857 | 1857 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 9 | 17406 | 18346 | 19776 | 20076 | 17650 | 20082 | 19028 | 20683 | 22030 | 19512 | 17937 | 22045 | 20627 | 23787 | 23793 | 21257 | 19551 | 21729 | 23549 | 25131
1858 | 1858 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 10 | 17073 | 17784 | 19151 | 19329 | 17482 | 19580 | 18454 | 19907 | 21159 | 19223 | 17611 | 21467 | 20040 | 22898 | 22975 | 21035 | 19271 | 21197 | 22761 | 24270
1859 | 1859 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 11 | 16701 | 17486 | 18669 | 18708 | 17183 | 19054 | 17987 | 19469 | 20502 | 18809 | 17302 | 20871 | 19567 | 22196 | 22549 | 20886 | 18995 | 20778 | 22310 | 23624
1860 | 1860 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 12 | 16689 | 17432 | 18428 | 18408 | 16950 | 19017 | 17782 | 19438 | 20252 | 18575 | 17260 | 20851 | 19220 | 21923 | 22258 | 20590 | 18810 | 20442 | 22283 | 23368
1861 | 1861 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 13 | 16665 | 17217 | 18097 | 18134 | 16651 | 18959 | 17617 | 19181 | 19861 | 18239 | 17039 | 20768 | 19015 | 21490 | 21938 | 20084 | 18543 | 20227 | 21992 | 22925
1862 | 1862 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 14 | 16679 | 17172 | 17949 | 17961 | 16320 | 18921 | 17583 | 19111 | 19630 | 17851 | 16850 | 20676 | 18897 | 21172 | 21653 | 19553 | 18283 | 20074 | 21830 | 22567
1863 | 1863 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 15 | 16746 | 17202 | 18022 | 17899 | 16259 | 18964 | 17664 | 19111 | 19633 | 17740 | 16828 | 20675 | 18935 | 21104 | 21476 | 19357 | 18221 | 20076 | 21764 | 22464
1864 | 1864 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 16 | 17124 | 17566 | 18265 | 18081 | 16533 | 19311 | 18129 | 19436 | 19771 | 17935 | 17117 | 20942 | 19523 | 21109 | 21447 | 19469 | 18494 | 20615 | 21942 | 22402
1865 | 1865 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 17 | 17926 | 18251 | 18927 | 18870 | 17288 | 20210 | 18764 | 20119 | 20508 | 18833 | 17986 | 21914 | 20286 | 21818 | 22247 | 20422 | 19536 | 21399 | 22783 | 23116
1866 | 1866 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 18 | 18267 | 18944 | 19624 | 19373 | 18057 | 20827 | 19118 | 20878 | 21488 | 19741 | 18929 | 22785 | 21042 | 23069 | 23272 | 21729 | 20733 | 22244 | 23771 | 24459
1867 | 1867 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 19 | 18774 | 19612 | 20260 | 19889 | 18617 | 21416 | 20028 | 21815 | 22260 | 20545 | 19630 | 23593 | 22340 | 24347 | 24391 | 22967 | 21703 | 23778 | 25365 | 25926
1868 | 1868 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 20 | 19014 | 20073 | 20737 | 20377 | 18853 | 21646 | 20591 | 22553 | 23066 | 21058 | 20395 | 24245 | 23118 | 25640 | 25491 | 23784 | 22626 | 24835 | 26921 | 27448
1869 | 1869 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 21 | 18563 | 19646 | 20627 | 20056 | 18567 | 21254 | 20387 | 22439 | 23335 | 21153 | 20601 | 24266 | 23497 | 26466 | 26115 | 24453 | 23233 | 25521 | 27714 | 28571
1870 | 1870 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 22 | 17551 | 18831 | 19888 | 19222 | 17839 | 20285 | 19684 | 21831 | 22770 | 20645 | 20148 | 23541 | 23167 | 26209 | 25877 | 24289 | 23030 | 25374 | 27673 | 28440
1871 | 1871 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 23 | 16388 | 17850 | 18898 | 18228 | 16943 | 19173 | 18665 | 20960 | 21883 | 19905 | 19427 | 22573 | 22366 | 25491 | 25169 | 23738 | 22454 | 24678 | 27122 | 27804
1872 | 1872 | 78 | 3 | 19 | Winter | 3 | 18 | Winter | 24 | 15255 | 16989 | 18034 | 17249 | 16179 | 18042 | 17749 | 20167 | 21114 | 19212 | 18878 | 21519 | 21587 | 24828 | 24406 | 23165 | 21954 | 23963 | 26485 | 27190
1873 | 1873 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 1 | 14287 | 16604 | 17144 | 16673 | 15631 | 16948 | 17979 | 19945 | 20358 | 18342 | 18066 | 20720 | 22020 | 24108 | 23542 | 21704 | 20736 | 24479 | 26465 | 26509
1874 | 1874 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 2 | 13981 | 16386 | 16797 | 16240 | 15302 | 16628 | 17790 | 19713 | 19938 | 18022 | 17797 | 20305 | 21727 | 23579 | 22936 | 21266 | 20499 | 24112 | 26039 | 25910
1875 | 1875 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 3 | 13787 | 16336 | 16713 | 16073 | 15175 | 16508 | 17852 | 19727 | 19836 | 17980 | 17827 | 20121 | 21635 | 23417 | 22644 | 21087 | 20197 | 23947 | 25793 | 25667
1876 | 1876 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 4 | 13824 | 16440 | 16828 | 16054 | 15154 | 16592 | 18000 | 19844 | 19917 | 17884 | 17903 | 19967 | 21515 | 23082 | 22216 | 20685 | 19619 | 23620 | 25404 | 25132
1877 | 1877 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 5 | 14234 | 16782 | 17141 | 16283 | 15250 | 16912 | 18355 | 20058 | 20002 | 17862 | 18120 | 19917 | 21412 | 22764 | 21752 | 20257 | 19307 | 23257 | 24978 | 24592
1878 | 1878 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 6 | 15201 | 17588 | 18096 | 16827 | 15426 | 17764 | 19208 | 20583 | 20534 | 17822 | 18780 | 20274 | 21777 | 22860 | 21402 | 19837 | 19661 | 23345 | 24775 | 24459
1879 | 1879 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 7 | 16407 | 18710 | 19476 | 17281 | 15724 | 18844 | 20284 | 21611 | 21591 | 17868 | 19755 | 20861 | 22485 | 23537 | 21211 | 19643 | 20360 | 23840 | 25188 | 24988
1880 | 1880 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 8 | 16783 | 19250 | 20091 | 17246 | 15790 | 19068 | 20832 | 22132 | 22179 | 17793 | 20081 | 20853 | 22800 | 23906 | 20982 | 19424 | 20521 | 24020 | 25370 | 25270
1881 | 1881 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 9 | 16467 | 19028 | 19724 | 17331 | 15810 | 18636 | 20371 | 21756 | 21777 | 17698 | 19637 | 20304 | 22169 | 23368 | 20900 | 19227 | 20136 | 23305 | 24850 | 24691
1882 | 1882 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 10 | 16050 | 18477 | 19026 | 17216 | 15614 | 18084 | 19616 | 20925 | 20845 | 17368 | 18993 | 19705 | 21330 | 22545 | 20668 | 18945 | 20033 | 22515 | 23989 | 23895
1883 | 1883 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 11 | 15775 | 18099 | 18543 | 17044 | 15516 | 17716 | 19277 | 20377 | 20198 | 17133 | 18540 | 19307 | 20914 | 22192 | 20605 | 18760 | 20048 | 22141 | 23412 | 23594
1884 | 1884 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 12 | 15652 | 17837 | 18213 | 16770 | 15526 | 17437 | 19157 | 20026 | 19951 | 16975 | 18280 | 18998 | 20926 | 21946 | 20348 | 18602 | 19932 | 22160 | 23193 | 23362
1885 | 1885 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 13 | 15543 | 17561 | 17956 | 16496 | 15372 | 17286 | 18909 | 19651 | 19671 | 16762 | 18127 | 18818 | 20660 | 21646 | 19865 | 18359 | 19777 | 21886 | 22773 | 23058
1886 | 1886 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 14 | 15569 | 17407 | 17759 | 16140 | 15230 | 17227 | 18807 | 19393 | 19429 | 16539 | 17944 | 18690 | 20510 | 21348 | 19318 | 18083 | 19515 | 21699 | 22400 | 22731
1887 | 1887 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 15 | 15644 | 17411 | 17649 | 16027 | 15220 | 17261 | 18761 | 19346 | 19273 | 16470 | 17885 | 18678 | 20428 | 21129 | 19078 | 17969 | 19401 | 21586 | 22249 | 22480
1888 | 1888 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 16 | 15969 | 17691 | 17871 | 16335 | 15585 | 17767 | 19141 | 19547 | 19356 | 16829 | 18154 | 19250 | 20652 | 21118 | 19201 | 18243 | 19511 | 21764 | 22183 | 22400
1889 | 1889 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 17 | 16485 | 18406 | 18725 | 17168 | 16509 | 18502 | 19922 | 20382 | 20227 | 17820 | 19042 | 20058 | 21504 | 21955 | 20199 | 19332 | 20260 | 22650 | 22949 | 23253
1890 | 1890 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 18 | 16897 | 19133 | 19245 | 18002 | 17230 | 18980 | 20808 | 21448 | 21031 | 18893 | 20038 | 20795 | 22381 | 22964 | 21485 | 20525 | 21224 | 23635 | 24294 | 24357
1891 | 1891 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 19 | 17674 | 19688 | 19689 | 18490 | 17581 | 19817 | 21659 | 22122 | 21739 | 19473 | 20547 | 21994 | 23697 | 23996 | 22650 | 21444 | 22143 | 25188 | 25730 | 25577
1892 | 1892 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 20 | 18028 | 20049 | 20029 | 18572 | 18059 | 20184 | 22160 | 22667 | 22430 | 19931 | 21181 | 22692 | 24940 | 25024 | 23403 | 22334 | 23394 | 26721 | 27241 | 26867
1893 | 1893 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 21 | 17578 | 19924 | 19683 | 18236 | 17878 | 19919 | 21974 | 22830 | 22423 | 20047 | 21342 | 22966 | 25381 | 25569 | 24005 | 22908 | 23959 | 27502 | 28354 | 27668
1894 | 1894 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 22 | 16682 | 19153 | 18814 | 17467 | 17177 | 19165 | 21299 | 22195 | 21774 | 19527 | 20633 | 22569 | 25107 | 25273 | 23794 | 22669 | 23486 | 27432 | 28210 | 27527
1895 | 1895 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 23 | 15531 | 18166 | 17790 | 16564 | 16328 | 18112 | 20394 | 21269 | 20857 | 18767 | 19671 | 21714 | 24423 | 24534 | 23211 | 22074 | 22642 | 26863 | 27565 | 26869
1896 | 1896 | 79 | 3 | 20 | Winter | 3 | 19 | Winter | 24 | 14568 | 17292 | 16792 | 15792 | 15677 | 17178 | 19574 | 20467 | 19981 | 18193 | 18874 | 20907 | 23715 | 23748 | 22623 | 21560 | 21802 | 26211 | 26941 | 26139
1897 | 1897 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 1 | 14919 | 16613 | 16476 | 15527 | 15091 | 17608 | 19553 | 19949 | 19553 | 17654 | 18843 | 21538 | 23842 | 23149 | 21452 | 20571 | 22294 | 26417 | 26487 | 25436
1898 | 1898 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 2 | 14746 | 16290 | 16046 | 15205 | 14832 | 17410 | 19317 | 19557 | 19097 | 17404 | 18417 | 21257 | 23490 | 22555 | 21023 | 20336 | 21727 | 25985 | 25884 | 24785
1899 | 1899 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 3 | 14734 | 16167 | 15830 | 15070 | 14850 | 17413 | 19281 | 19467 | 18979 | 17408 | 18309 | 21185 | 23344 | 22269 | 20854 | 20040 | 21463 | 25736 | 25636 | 24440
1900 | 1900 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 4 | 14856 | 16277 | 15830 | 15046 | 15036 | 17604 | 19464 | 19605 | 18920 | 17593 | 18305 | 21139 | 23205 | 21894 | 20492 | 19497 | 21047 | 25369 | 25124 | 23881
1901 | 1901 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 5 | 15227 | 16619 | 16077 | 15171 | 15499 | 18005 | 19742 | 19790 | 18918 | 17891 | 18423 | 21116 | 23072 | 21497 | 20116 | 19219 | 20867 | 24961 | 24597 | 23256
1902 | 1902 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 6 | 16160 | 17596 | 16657 | 15390 | 16502 | 18912 | 20346 | 20449 | 19145 | 18628 | 19058 | 21551 | 23145 | 21206 | 19729 | 19591 | 21147 | 24777 | 24465 | 22740
1903 | 1903 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 7 | 17528 | 19020 | 17178 | 15754 | 17738 | 20072 | 21465 | 21636 | 19437 | 19688 | 19901 | 22361 | 23769 | 21096 | 19595 | 20344 | 21758 | 25219 | 25024 | 22467
1904 | 1904 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 8 | 18245 | 19666 | 17211 | 15859 | 18203 | 20685 | 22050 | 22301 | 19364 | 20090 | 19972 | 22759 | 24095 | 20934 | 19435 | 20551 | 21620 | 25454 | 25351 | 22233
1905 | 1905 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 9 | 17928 | 19343 | 17363 | 15891 | 17976 | 20274 | 21737 | 21916 | 19411 | 19711 | 19629 | 22184 | 23676 | 20894 | 19278 | 20202 | 21151 | 24973 | 24802 | 22156
1906 | 1906 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 10 | 17452 | 18727 | 17330 | 15766 | 17534 | 19556 | 20942 | 21019 | 19207 | 19056 | 19148 | 21393 | 22839 | 20714 | 19055 | 20161 | 21043 | 24174 | 24071 | 22025
1907 | 1907 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 11 | 17204 | 18242 | 17135 | 15628 | 17162 | 19150 | 20317 | 20291 | 18857 | 18489 | 18773 | 20925 | 22184 | 20597 | 18819 | 20131 | 21193 | 23558 | 23725 | 21949
1908 | 1908 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 12 | 17128 | 17980 | 16938 | 15625 | 16949 | 19131 | 20081 | 20012 | 18512 | 18359 | 18590 | 20935 | 21949 | 20347 | 18673 | 20015 | 21009 | 23349 | 23497 | 21691
1909 | 1909 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 13 | 16904 | 17697 | 16643 | 15443 | 16805 | 18857 | 19681 | 19693 | 18160 | 18178 | 18408 | 20639 | 21507 | 19843 | 18403 | 19830 | 20994 | 22890 | 23158 | 21163
1910 | 1910 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 14 | 16839 | 17524 | 16306 | 15303 | 16699 | 18771 | 19444 | 19447 | 17756 | 18011 | 18117 | 20501 | 21198 | 19312 | 18140 | 19576 | 20736 | 22527 | 22851 | 20609
1911 | 1911 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 15 | 16823 | 17435 | 16207 | 15302 | 16690 | 18742 | 19420 | 19298 | 17597 | 17968 | 17914 | 20431 | 21090 | 19089 | 18044 | 19469 | 20468 | 22386 | 22612 | 20358
1912 | 1912 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 16 | 17248 | 17675 | 16522 | 15715 | 17056 | 19121 | 19624 | 19439 | 17899 | 18228 | 18419 | 20718 | 21152 | 19266 | 18365 | 19630 | 20954 | 22373 | 22577 | 20492
1913 | 1913 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 17 | 17899 | 18356 | 17185 | 16543 | 17742 | 19734 | 20290 | 20223 | 18798 | 18942 | 19197 | 21471 | 21796 | 20145 | 19340 | 20280 | 21688 | 23018 | 23314 | 21396
1914 | 1914 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 18 | 18620 | 18709 | 17813 | 17198 | 18405 | 20448 | 21136 | 20938 | 19778 | 19711 | 19582 | 22269 | 22968 | 21366 | 20470 | 21181 | 21784 | 24309 | 24359 | 22700
1915 | 1915 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 19 | 19237 | 19161 | 18282 | 17523 | 18761 | 21297 | 21795 | 21581 | 20468 | 20185 | 20302 | 23503 | 24139 | 22466 | 21357 | 22054 | 22521 | 25727 | 25575 | 23975
1916 | 1916 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 20 | 19561 | 19575 | 18459 | 17961 | 19087 | 21928 | 22467 | 22180 | 20694 | 20947 | 21125 | 24635 | 25357 | 23153 | 22180 | 23258 | 23555 | 27226 | 26850 | 24883
1917 | 1917 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 21 | 19108 | 19181 | 18073 | 17748 | 18837 | 21668 | 22547 | 22083 | 20667 | 21004 | 21427 | 24961 | 26079 | 23659 | 22697 | 23775 | 24338 | 28302 | 27633 | 25664
1918 | 1918 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 22 | 18272 | 18314 | 17303 | 17048 | 17903 | 20965 | 21883 | 21391 | 20100 | 20254 | 20798 | 24639 | 25776 | 23417 | 22434 | 23298 | 24003 | 28174 | 27508 | 25570
1919 | 1919 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 23 | 17273 | 17282 | 16378 | 16202 | 16825 | 20031 | 20931 | 20437 | 19328 | 19259 | 19899 | 23921 | 25033 | 22811 | 21822 | 22457 | 23298 | 27521 | 26843 | 25048
1920 | 1920 | 80 | 3 | 21 | Winter | 3 | 20 | Winter | 24 | 16400 | 16293 | 15610 | 15567 | 15948 | 19211 | 20118 | 19544 | 18611 | 18460 | 19134 | 23201 | 24351 | 22226 | 21321 | 21619 | 22602 | 26903 | 26128 | 24504
1921 | 1921 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 1 | 16129 | 15874 | 15252 | 14863 | 15261 | 19018 | 19436 | 19022 | 17955 | 18231 | 18962 | 23179 | 23737 | 21010 | 20219 | 21940 | 22578 | 26313 | 25306 | 23014
1922 | 1922 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 2 | 15916 | 15449 | 14935 | 14604 | 14907 | 18781 | 19046 | 18577 | 17644 | 17833 | 18583 | 22849 | 23218 | 20595 | 19996 | 21390 | 22030 | 25710 | 24656 | 22548
1923 | 1923 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 3 | 15844 | 15222 | 14790 | 14568 | 14825 | 18743 | 18958 | 18408 | 17559 | 17761 | 18472 | 22725 | 23066 | 20446 | 19719 | 21120 | 21734 | 25467 | 24314 | 22349
1924 | 1924 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 4 | 15967 | 15189 | 14737 | 14756 | 14963 | 18921 | 19114 | 18409 | 17541 | 17820 | 18469 | 22644 | 22790 | 20114 | 19199 | 20731 | 21301 | 24966 | 23757 | 21874
1925 | 1925 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 5 | 16326 | 15437 | 14863 | 15231 | 15387 | 19230 | 19351 | 18477 | 17582 | 18012 | 18628 | 22594 | 22551 | 19782 | 18962 | 20589 | 21143 | 24455 | 23144 | 21358
1926 | 1926 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 6 | 17125 | 16018 | 15099 | 16258 | 16457 | 19870 | 20079 | 18785 | 17589 | 18715 | 19393 | 22759 | 22706 | 19429 | 19359 | 20908 | 21494 | 24337 | 22625 | 20823
1927 | 1927 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 7 | 18258 | 16548 | 15479 | 17508 | 17747 | 20996 | 21322 | 19152 | 17700 | 19611 | 20350 | 23455 | 23455 | 19315 | 20125 | 21543 | 22138 | 24890 | 22341 | 20592
1928 | 1928 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 8 | 18886 | 16643 | 15656 | 18031 | 18074 | 21645 | 22062 | 19169 | 17742 | 19783 | 20500 | 23875 | 23950 | 19217 | 20402 | 21475 | 22126 | 25275 | 22155 | 20444
1929 | 1929 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 9 | 18805 | 16903 | 15828 | 17920 | 17908 | 21458 | 21814 | 19354 | 17823 | 19578 | 20148 | 23567 | 23575 | 19183 | 20172 | 21118 | 21734 | 24837 | 22183 | 20376
1930 | 1930 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 10 | 18343 | 16959 | 15794 | 17508 | 17534 | 20742 | 20980 | 19145 | 17538 | 19113 | 19623 | 22749 | 22828 | 18981 | 20150 | 21025 | 21571 | 24128 | 22076 | 20227
1931 | 1931 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 11 | 17821 | 16731 | 15632 | 17050 | 17138 | 20060 | 20192 | 18676 | 17136 | 18645 | 19109 | 21995 | 22345 | 18659 | 20035 | 21069 | 21546 | 23701 | 21917 | 19936
1932 | 1932 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 12 | 17540 | 16452 | 15543 | 16841 | 16876 | 19729 | 19814 | 18363 | 17027 | 18375 | 18865 | 21669 | 22012 | 18421 | 19823 | 20800 | 21323 | 23373 | 21566 | 19687
1933 | 1933 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 13 | 17256 | 16178 | 15375 | 16711 | 16737 | 19342 | 19503 | 18021 | 16790 | 18202 | 18684 | 21238 | 21686 | 18168 | 19647 | 20794 | 21305 | 23040 | 21044 | 19414
1934 | 1934 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 14 | 17089 | 15833 | 15223 | 16588 | 16512 | 19098 | 19248 | 17603 | 16556 | 17901 | 18437 | 20907 | 21374 | 17892 | 19377 | 20515 | 21097 | 22709 | 20460 | 19106
1935 | 1935 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 15 | 17145 | 15762 | 15262 | 16632 | 16423 | 19125 | 19145 | 17497 | 16543 | 17744 | 18393 | 20860 | 21213 | 17839 | 19311 | 20300 | 21022 | 22510 | 20247 | 19027
1936 | 1936 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 16 | 17507 | 16151 | 15745 | 17035 | 16954 | 19415 | 19371 | 17824 | 16948 | 18319 | 18697 | 21014 | 21316 | 18240 | 19548 | 20866 | 21254 | 22541 | 20449 | 19392
1937 | 1937 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 17 | 18129 | 16827 | 16589 | 17703 | 17732 | 20109 | 20182 | 18690 | 17810 | 19132 | 19433 | 21686 | 22088 | 19248 | 20226 | 21625 | 21969 | 23315 | 21390 | 20408
1938 | 1938 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 18 | 18674 | 17357 | 17120 | 18186 | 17880 | 20877 | 20793 | 19422 | 18612 | 19440 | 19744 | 22746 | 22960 | 20315 | 21068 | 21657 | 22070 | 24314 | 22654 | 21541
1939 | 1939 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 19 | 19169 | 17741 | 17360 | 18478 | 18240 | 21446 | 21333 | 20025 | 19116 | 20017 | 20509 | 23805 | 23864 | 21099 | 21854 | 22313 | 22955 | 25468 | 23878 | 22462
1940 | 1940 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 20 | 19585 | 17889 | 17767 | 18909 | 18732 | 22081 | 21864 | 20378 | 19706 | 20732 | 21476 | 24915 | 24796 | 21870 | 23006 | 23298 | 24026 | 26721 | 24776 | 23410
1941 | 1941 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 21 | 19434 | 17477 | 17526 | 18631 | 18559 | 22105 | 21696 | 20266 | 19740 | 20925 | 21735 | 25544 | 25249 | 22328 | 23478 | 24039 | 24806 | 27497 | 25552 | 24072
1942 | 1942 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 22 | 18657 | 16687 | 16801 | 17680 | 17626 | 21402 | 20948 | 19636 | 19172 | 20222 | 21215 | 25169 | 24907 | 22024 | 22964 | 23675 | 24605 | 27355 | 25449 | 23888
1943 | 1943 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 23 | 17670 | 15756 | 15945 | 16579 | 16538 | 20444 | 19967 | 18811 | 18374 | 19291 | 20312 | 24388 | 24128 | 21393 | 22111 | 22933 | 23857 | 26685 | 24925 | 23337
1944 | 1944 | 81 | 3 | 22 | Winter | 3 | 21 | Winter | 24 | 16806 | 14982 | 15291 | 15711 | 15648 | 19611 | 19047 | 18082 | 17801 | 18506 | 19564 | 23679 | 23336 | 20877 | 21262 | 22224 | 23200 | 25958 | 24378 | 22852
1945 | 1945 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 1 | 15884 | 14539 | 14469 | 14848 | 15182 | 18789 | 18420 | 17386 | 17026 | 18209 | 19221 | 19910 | 22537 | 19674 | 21419 | 22079 | 22942 | 25026 | 22794 | 21619
1946 | 1946 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 2 | 15593 | 14244 | 14227 | 14504 | 14866 | 18410 | 17986 | 17085 | 16798 | 17869 | 18830 | 19454 | 21972 | 19475 | 20898 | 21548 | 22367 | 24386 | 22345 | 21379
1947 | 1947 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 3 | 15469 | 14107 | 14208 | 14447 | 14774 | 18361 | 17866 | 17054 | 16810 | 17858 | 18752 | 19366 | 21709 | 19209 | 20636 | 21254 | 21983 | 24034 | 22124 | 21053
1948 | 1948 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 4 | 15586 | 14049 | 14348 | 14542 | 14943 | 18484 | 17843 | 17007 | 17030 | 17872 | 18662 | 19238 | 21400 | 18743 | 20293 | 20872 | 21533 | 23507 | 21668 | 20446
1949 | 1949 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 5 | 15940 | 14151 | 14815 | 14974 | 15459 | 18746 | 17951 | 17083 | 17379 | 18100 | 18817 | 18961 | 21075 | 18552 | 20199 | 20758 | 21278 | 22919 | 21161 | 20084
1950 | 1950 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 6 | 16925 | 14403 | 15875 | 16095 | 16655 | 19535 | 18354 | 17185 | 18171 | 18962 | 19436 | 18708 | 20857 | 18995 | 20568 | 21164 | 21422 | 22431 | 20650 | 20368
1951 | 1951 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 7 | 18366 | 14793 | 17177 | 17449 | 17953 | 20819 | 18804 | 17387 | 19302 | 20013 | 20326 | 18435 | 20803 | 19813 | 21264 | 21864 | 22083 | 22168 | 20429 | 21080
1952 | 1952 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 8 | 18943 | 14871 | 17601 | 17697 | 18173 | 21466 | 18739 | 17354 | 19681 | 20090 | 20541 | 18513 | 20616 | 19995 | 21112 | 21765 | 22204 | 21878 | 20170 | 21203
1953 | 1953 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 9 | 18681 | 15036 | 17494 | 17502 | 17913 | 21205 | 18912 | 17427 | 19392 | 19735 | 20227 | 18350 | 20654 | 19749 | 20734 | 21352 | 21893 | 21876 | 20070 | 20912
1954 | 1954 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 10 | 18074 | 15081 | 17150 | 17170 | 17464 | 20433 | 18758 | 17211 | 18755 | 19237 | 19735 | 17856 | 20460 | 19693 | 20602 | 21149 | 21750 | 21733 | 19882 | 20893
1955 | 1955 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 11 | 17575 | 15131 | 16948 | 17026 | 17091 | 19943 | 18605 | 17155 | 18175 | 19054 | 19463 | 17652 | 20301 | 19646 | 20711 | 21189 | 21745 | 21637 | 19655 | 20869
1956 | 1956 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 12 | 17267 | 15100 | 16796 | 16816 | 16876 | 19614 | 18335 | 17080 | 17994 | 18845 | 19237 | 17546 | 19999 | 19491 | 20500 | 21014 | 21529 | 21349 | 19470 | 20712
1957 | 1957 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 13 | 17025 | 14974 | 16699 | 16721 | 16748 | 19338 | 18029 | 16884 | 17858 | 18690 | 19064 | 17298 | 19534 | 19344 | 20523 | 21030 | 21402 | 20852 | 19217 | 20548
1958 | 1958 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 14 | 16900 | 14877 | 16636 | 16579 | 16614 | 19151 | 17679 | 16729 | 17742 | 18509 | 18852 | 17087 | 19054 | 19135 | 20305 | 20894 | 21164 | 20332 | 18967 | 20309
1959 | 1959 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 15 | 16890 | 14971 | 16722 | 16546 | 16640 | 19098 | 17621 | 16760 | 17781 | 18510 | 18830 | 16952 | 18910 | 19115 | 20136 | 20860 | 21055 | 20163 | 18927 | 20265
1960 | 1960 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 16 | 17217 | 15445 | 17124 | 17070 | 17031 | 19343 | 17963 | 17193 | 18122 | 18836 | 19063 | 17255 | 19168 | 19348 | 20698 | 21092 | 21197 | 20346 | 19278 | 20463
1961 | 1961 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 17 | 17895 | 16225 | 17728 | 17789 | 17593 | 20105 | 18776 | 17992 | 18824 | 19536 | 19610 | 18025 | 20050 | 19984 | 21411 | 21752 | 21743 | 21243 | 20255 | 21122
1962 | 1962 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 18 | 18134 | 16664 | 18086 | 17878 | 17817 | 20621 | 19395 | 18667 | 19468 | 19744 | 20154 | 18586 | 21151 | 20760 | 21381 | 21807 | 22068 | 22454 | 21343 | 21984
1963 | 1963 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 19 | 18520 | 16854 | 18322 | 18174 | 18269 | 21083 | 19896 | 19062 | 19839 | 20348 | 20748 | 19107 | 22133 | 21505 | 21994 | 22662 | 22897 | 23673 | 22270 | 22873
1964 | 1964 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 20 | 18896 | 17146 | 18598 | 18481 | 18811 | 21390 | 19994 | 19378 | 20522 | 20960 | 21532 | 20059 | 22742 | 22602 | 22927 | 23681 | 24199 | 24565 | 23223 | 24136
1965 | 1965 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 21 | 18497 | 16868 | 18289 | 18258 | 18547 | 21158 | 19801 | 19328 | 20508 | 21105 | 21784 | 20601 | 23169 | 23016 | 23611 | 24403 | 24974 | 25320 | 23872 | 24751
1966 | 1966 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 22 | 17614 | 16132 | 17311 | 17298 | 17692 | 20373 | 19124 | 18722 | 19698 | 20506 | 21194 | 20414 | 22869 | 22469 | 23204 | 24169 | 24683 | 25208 | 23688 | 24311
1967 | 1967 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 23 | 16562 | 15273 | 16198 | 16203 | 16576 | 19371 | 18266 | 17900 | 18674 | 19558 | 20306 | 19745 | 22220 | 21579 | 22439 | 23417 | 23975 | 24670 | 23117 | 23495
1968 | 1968 | 82 | 3 | 23 | Winter | 3 | 22 | Winter | 24 | 15567 | 14594 | 15299 | 15286 | 15729 | 18408 | 17493 | 17277 | 17843 | 18772 | 19611 | 19274 | 21606 | 20697 | 21698 | 22729 | 23348 | 24099 | 22615 | 22647
1969 | 1969 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 1 | 15163 | 13866 | 14492 | 14894 | 15280 | 17885 | 16956 | 16589 | 17503 | 18522 | 19259 | 21879 | 20477 | 20893 | 21630 | 22558 | 22947 | 22631 | 21477 | 23085
1970 | 1970 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 2 | 14753 | 13630 | 14152 | 14562 | 14949 | 17442 | 16644 | 16356 | 17124 | 18153 | 18930 | 21328 | 20080 | 20379 | 21110 | 21978 | 22471 | 22164 | 21228 | 22516
1971 | 1971 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 3 | 14559 | 13583 | 14078 | 14494 | 14907 | 17290 | 16583 | 16410 | 17133 | 18082 | 18843 | 21113 | 19948 | 20155 | 20848 | 21607 | 22259 | 21965 | 20923 | 22223
1972 | 1972 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 4 | 14499 | 13712 | 14163 | 14612 | 15003 | 17287 | 16563 | 16602 | 17165 | 18092 | 18773 | 20864 | 19666 | 19852 | 20495 | 21177 | 21779 | 21507 | 20308 | 21748
1973 | 1973 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 5 | 14753 | 14192 | 14598 | 15134 | 15444 | 17429 | 16678 | 16989 | 17414 | 18340 | 18907 | 20627 | 19388 | 19813 | 20428 | 20972 | 21502 | 21016 | 19957 | 21500
1974 | 1974 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 6 | 15360 | 15259 | 15719 | 16335 | 16480 | 17861 | 16823 | 17833 | 18212 | 19015 | 19411 | 20507 | 19108 | 20244 | 20885 | 21160 | 21613 | 20519 | 20243 | 21710
1975 | 1975 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 7 | 15903 | 16577 | 17085 | 17632 | 17715 | 18324 | 17054 | 18991 | 19177 | 19969 | 20261 | 20506 | 19034 | 20967 | 21608 | 21829 | 22070 | 20295 | 20935 | 22263
1976 | 1976 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 8 | 16001 | 17142 | 17489 | 17995 | 18209 | 18399 | 17177 | 19535 | 19389 | 20370 | 20777 | 20439 | 18949 | 20950 | 21633 | 22058 | 22332 | 20138 | 21156 | 22132
1977 | 1977 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 9 | 16458 | 17286 | 17560 | 18000 | 18241 | 18812 | 17500 | 19525 | 19407 | 20296 | 20718 | 20740 | 19121 | 20818 | 21473 | 21998 | 22251 | 20270 | 21100 | 21952
1978 | 1978 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 10 | 16787 | 17258 | 17524 | 17896 | 18139 | 18943 | 17565 | 19248 | 19246 | 20046 | 20427 | 20790 | 19135 | 20931 | 21517 | 22102 | 22099 | 20326 | 21337 | 22116
1979 | 1979 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 11 | 16732 | 17065 | 17379 | 17722 | 17863 | 18783 | 17500 | 18954 | 19110 | 19748 | 20184 | 20618 | 18851 | 20995 | 21525 | 22091 | 21992 | 20076 | 21287 | 22235
1980 | 1980 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 12 | 16486 | 16881 | 17133 | 17462 | 17610 | 18469 | 17370 | 18710 | 18844 | 19452 | 19981 | 20290 | 18648 | 20745 | 21316 | 21848 | 21881 | 19855 | 21099 | 21989
1981 | 1981 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 13 | 16182 | 16654 | 16908 | 17187 | 17414 | 18005 | 17006 | 18387 | 18640 | 19082 | 19609 | 19751 | 18354 | 20700 | 21262 | 21650 | 21646 | 19535 | 20865 | 21927
1982 | 1982 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 14 | 15922 | 16594 | 16771 | 17033 | 17314 | 17638 | 16828 | 18238 | 18434 | 18836 | 19376 | 19299 | 18163 | 20517 | 21150 | 21437 | 21456 | 19318 | 20654 | 21712
1983 | 1983 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 15 | 15842 | 16628 | 16686 | 17002 | 17327 | 17521 | 16797 | 18215 | 18278 | 18746 | 19250 | 19122 | 18110 | 20312 | 21081 | 21291 | 21320 | 19236 | 20567 | 21472
1984 | 1984 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 16 | 16036 | 16854 | 16975 | 17220 | 17493 | 17698 | 17064 | 18394 | 18667 | 18829 | 19269 | 19207 | 18314 | 20711 | 21144 | 21253 | 21208 | 19403 | 20586 | 21819
1985 | 1985 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 17 | 16501 | 17254 | 17506 | 17601 | 17906 | 18326 | 17681 | 18905 | 19276 | 19213 | 19715 | 19910 | 19123 | 21263 | 21633 | 21631 | 21578 | 20217 | 21073 | 22397
1986 | 1986 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 18 | 16864 | 17488 | 17543 | 17748 | 18111 | 18894 | 18291 | 19446 | 19411 | 19695 | 20431 | 20871 | 20037 | 21129 | 21578 | 21845 | 22404 | 21211 | 21840 | 22341
1987 | 1987 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 19 | 17194 | 17748 | 17858 | 18164 | 18322 | 19417 | 18710 | 19761 | 19860 | 20265 | 21118 | 21782 | 20769 | 21690 | 22382 | 22641 | 23467 | 22138 | 22729 | 23075
1988 | 1988 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 20 | 17206 | 18040 | 18192 | 18566 | 18807 | 19566 | 19078 | 20236 | 20227 | 21044 | 21993 | 22296 | 21479 | 22550 | 23333 | 23892 | 24706 | 23073 | 23983 | 24154
1989 | 1989 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 21 | 16764 | 17693 | 17928 | 18250 | 18551 | 19313 | 18969 | 20139 | 20321 | 21178 | 22228 | 22608 | 21853 | 23150 | 23984 | 24602 | 25469 | 23708 | 24589 | 25004
1990 | 1990 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 22 | 15965 | 16710 | 16950 | 17363 | 17659 | 18610 | 18335 | 19293 | 19560 | 20512 | 21727 | 22249 | 21516 | 22703 | 23715 | 24287 | 25278 | 23524 | 24154 | 24705
1991 | 1991 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 23 | 15031 | 15587 | 15849 | 16243 | 16627 | 17738 | 17498 | 18245 | 18594 | 19590 | 20896 | 21570 | 20863 | 21903 | 22933 | 23566 | 24598 | 22954 | 23342 | 24003
1992 | 1992 | 83 | 3 | 24 | Winter | 3 | 23 | Winter | 24 | 14251 | 14708 | 14931 | 15396 | 15821 | 16964 | 16870 | 17392 | 17776 | 18891 | 20258 | 20929 | 20322 | 21166 | 22247 | 22930 | 24042 | 22457 | 22508 | 23310
1993 | 1993 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 1 | 13841 | 13736 | 14438 | 14829 | 15336 | 16382 | 16079 | 16862 | 17448 | 18456 | 19344 | 19810 | 19136 | 20992 | 21968 | 22440 | 22922 | 21222 | 22831 | 23212
1994 | 1994 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 2 | 13550 | 13423 | 14122 | 14494 | 15059 | 16066 | 15843 | 16494 | 17119 | 18158 | 18933 | 19426 | 18947 | 20490 | 21405 | 21973 | 22372 | 20971 | 22264 | 22653
1995 | 1995 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 3 | 13403 | 13327 | 14040 | 14416 | 15002 | 15996 | 15888 | 16481 | 17087 | 18112 | 18829 | 19316 | 18701 | 20248 | 21057 | 21777 | 22036 | 20656 | 21967 | 22352
1996 | 1996 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 4 | 13365 | 13395 | 14145 | 14529 | 15146 | 15969 | 16087 | 16570 | 17177 | 18115 | 18733 | 19105 | 18278 | 19954 | 20686 | 21339 | 21553 | 20065 | 21508 | 21880
1997 | 1997 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 5 | 13476 | 13829 | 14674 | 14993 | 15623 | 16111 | 16513 | 16883 | 17482 | 18343 | 18594 | 18899 | 18146 | 19953 | 20540 | 21116 | 21104 | 19734 | 21272 | 21660
1998 | 1998 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 6 | 13738 | 14992 | 15924 | 16082 | 16618 | 16334 | 17471 | 17761 | 18413 | 18999 | 18599 | 18702 | 18670 | 20478 | 20789 | 21280 | 20723 | 20053 | 21508 | 21965
1999 | 1999 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 7 | 14108 | 16385 | 17221 | 17341 | 17771 | 16594 | 18685 | 18804 | 19496 | 19934 | 18644 | 18687 | 19503 | 21250 | 21494 | 21771 | 20550 | 20748 | 22062 | 22545
2000 | 2000 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 8 | 14180 | 16648 | 17417 | 17686 | 18255 | 16546 | 19069 | 18927 | 19608 | 20304 | 18464 | 18492 | 19662 | 21168 | 21599 | 21899 | 20204 | 20836 | 21789 | 22341
2001 | 2001 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 9 | 14364 | 16510 | 17215 | 17493 | 18154 | 16643 | 18847 | 18755 | 19293 | 20022 | 18480 | 18455 | 19444 | 20792 | 21318 | 21592 | 20110 | 20547 | 21383 | 21895
2002 | 2002 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 10 | 14487 | 16314 | 16944 | 17225 | 17758 | 16527 | 18381 | 18407 | 18855 | 19499 | 18194 | 18252 | 19429 | 20616 | 21203 | 21227 | 20111 | 20563 | 21332 | 21763
2003 | 2003 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 11 | 14567 | 16114 | 16722 | 16878 | 17551 | 16355 | 17954 | 18125 | 18701 | 19061 | 17798 | 17990 | 19390 | 20649 | 21216 | 21143 | 20147 | 20545 | 21481 | 21841
2004 | 2004 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 12 | 14572 | 15910 | 16497 | 16644 | 17424 | 16244 | 17718 | 17830 | 18509 | 18854 | 17570 | 17850 | 19278 | 20505 | 21045 | 21096 | 20051 | 20423 | 21306 | 21711
2005 | 2005 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 13 | 14377 | 15806 | 16356 | 16514 | 17155 | 16052 | 17574 | 17682 | 18205 | 18670 | 17221 | 17616 | 19111 | 20510 | 20903 | 20913 | 19856 | 20250 | 21301 | 21713
2006 | 2006 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 14 | 14177 | 15637 | 16161 | 16343 | 16910 | 15854 | 17408 | 17399 | 17890 | 18432 | 16817 | 17350 | 18835 | 20317 | 20610 | 20651 | 19479 | 19956 | 21003 | 21496
2007 | 2007 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 15 | 14201 | 15591 | 16125 | 16345 | 16836 | 15837 | 17397 | 17237 | 17802 | 18324 | 16662 | 17281 | 18754 | 20225 | 20448 | 20490 | 19280 | 19846 | 20745 | 21385
2008 | 2008 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 16 | 14577 | 15938 | 16442 | 16642 | 17054 | 16221 | 17696 | 17721 | 18043 | 18484 | 16830 | 17597 | 18898 | 20384 | 20503 | 20480 | 19315 | 19944 | 21174 | 21506
2009 | 2009 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 17 | 15392 | 16677 | 17045 | 17274 | 17648 | 17080 | 18454 | 18564 | 18779 | 19192 | 17753 | 18609 | 19578 | 21081 | 21094 | 21047 | 20137 | 20642 | 21954 | 22222
2010 | 2010 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 18 | 15922 | 16931 | 17407 | 17699 | 18247 | 17905 | 19190 | 18990 | 19128 | 20117 | 18688 | 19652 | 20413 | 21180 | 21469 | 22027 | 20694 | 21577 | 22069 | 22423
2011 | 2011 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 19 | 16176 | 17248 | 17849 | 17964 | 18732 | 18337 | 19493 | 19475 | 19781 | 20743 | 19402 | 20377 | 21161 | 21988 | 22267 | 23119 | 21482 | 22517 | 22862 | 23425
2012 | 2012 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 20 | 16491 | 17540 | 18204 | 18469 | 19156 | 18653 | 19904 | 19825 | 20414 | 21440 | 20090 | 21013 | 22203 | 22868 | 23471 | 24318 | 22613 | 23782 | 23937 | 24555
2013 | 2013 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 21 | 16200 | 17255 | 17857 | 18187 | 18925 | 18518 | 19759 | 19853 | 20460 | 21583 | 20436 | 21334 | 22554 | 23455 | 24130 | 25043 | 23491 | 24387 | 24799 | 25422
2014 | 2014 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 22 | 15442 | 16250 | 16933 | 17265 | 18091 | 17845 | 18864 | 19030 | 19787 | 20985 | 20024 | 20929 | 21962 | 23122 | 23762 | 24809 | 23379 | 23936 | 24480 | 25259
2015 | 2015 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 23 | 14581 | 15130 | 15798 | 16223 | 17117 | 16992 | 17792 | 18028 | 18810 | 20125 | 19397 | 20244 | 21057 | 22313 | 23018 | 24108 | 22901 | 23105 | 23775 | 24543
2016 | 2016 | 84 | 3 | 25 | Winter | 3 | 24 | Winter | 24 | 13893 | 14199 | 14929 | 15415 | 16344 | 16352 | 16921 | 17184 | 18010 | 19459 | 18884 | 19681 | 20185 | 21621 | 22383 | 23554 | 22458 | 22271 | 23078 | 23887
2017 | 2017 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 1 | 13154 | 13789 | 14421 | 15006 | 15596 | 15624 | 16371 | 16890 | 17704 | 18662 | 18132 | 18380 | 20288 | 21400 | 21977 | 22523 | 20897 | 22631 | 23058 | 23752
2018 | 2018 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 2 | 12931 | 13485 | 14106 | 14626 | 15272 | 15390 | 16002 | 16569 | 17359 | 18290 | 17825 | 18192 | 19791 | 20867 | 21530 | 21993 | 20632 | 22069 | 22505 | 23157
2019 | 2019 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 3 | 12877 | 13399 | 14033 | 14590 | 15179 | 15438 | 16005 | 16577 | 17311 | 18245 | 17756 | 18318 | 19587 | 20537 | 21350 | 21671 | 20152 | 21785 | 22197 | 22754
2020 | 2020 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 4 | 13015 | 13471 | 14124 | 14746 | 15271 | 15616 | 16096 | 16665 | 17369 | 18202 | 17729 | 18471 | 19350 | 20218 | 20961 | 21230 | 19484 | 21340 | 21736 | 22244
2021 | 2021 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 5 | 13497 | 13981 | 14581 | 14905 | 15452 | 16050 | 16443 | 17010 | 17683 | 18134 | 17669 | 18651 | 19367 | 20121 | 20773 | 20810 | 19012 | 21117 | 21516 | 21923
2022 | 2022 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 6 | 14590 | 15225 | 15702 | 15253 | 15945 | 17041 | 17393 | 18042 | 18505 | 18228 | 17715 | 19054 | 19870 | 20429 | 20985 | 20458 | 18656 | 21370 | 21822 | 22001
2023 | 2023 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 7 | 15927 | 16542 | 16990 | 15389 | 16413 | 18283 | 18513 | 19190 | 19514 | 18342 | 17614 | 19518 | 20639 | 21169 | 21506 | 20307 | 18231 | 21927 | 22399 | 22593
2024 | 2024 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 8 | 16383 | 16802 | 17379 | 15675 | 16400 | 18714 | 18727 | 19345 | 19805 | 18247 | 17299 | 19882 | 20561 | 21340 | 21700 | 20022 | 17819 | 21714 | 22244 | 22694
2025 | 2025 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 9 | 16562 | 16885 | 17464 | 16010 | 16760 | 18761 | 18838 | 19317 | 19786 | 18556 | 17444 | 20058 | 20483 | 21322 | 21660 | 20185 | 17992 | 21565 | 22072 | 22640
2026 | 2026 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 10 | 16461 | 16796 | 17377 | 15830 | 16712 | 18457 | 18634 | 19031 | 19463 | 18390 | 17332 | 19831 | 20494 | 21327 | 21406 | 20303 | 18254 | 21637 | 22067 | 22684
2027 | 2027 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 11 | 16352 | 16822 | 17311 | 15787 | 16560 | 18336 | 18649 | 19003 | 19121 | 18327 | 17330 | 19752 | 20717 | 21456 | 21443 | 20451 | 18441 | 21908 | 22277 | 22866
2028 | 2028 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 12 | 16218 | 16670 | 17151 | 15683 | 16367 | 18197 | 18458 | 18828 | 18830 | 18199 | 17345 | 19671 | 20538 | 21301 | 21409 | 20354 | 18446 | 21744 | 22145 | 22719
2029 | 2029 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 13 | 16155 | 16592 | 17088 | 15481 | 16110 | 18115 | 18371 | 18718 | 18710 | 17908 | 17250 | 19610 | 20607 | 21215 | 21279 | 20224 | 18347 | 21795 | 22198 | 22623
2030 | 2030 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 14 | 16092 | 16477 | 16984 | 15325 | 15821 | 18015 | 18158 | 18543 | 18510 | 17565 | 17106 | 19471 | 20398 | 20983 | 21071 | 19915 | 18200 | 21545 | 22033 | 22359
2031 | 2031 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 15 | 16186 | 16508 | 17065 | 15268 | 15791 | 18085 | 18078 | 18561 | 18511 | 17492 | 17200 | 19508 | 20248 | 20904 | 20988 | 19797 | 18278 | 21364 | 21996 | 22242
2032 | 2032 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 16 | 16562 | 16818 | 17387 | 15660 | 16075 | 18398 | 18541 | 18851 | 18776 | 17671 | 17592 | 19870 | 20775 | 21015 | 21038 | 19880 | 18593 | 21834 | 22155 | 22286
2033 | 2033 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 17 | 16987 | 17168 | 17779 | 16215 | 16714 | 18914 | 19139 | 19385 | 19217 | 18350 | 18187 | 20406 | 21338 | 21418 | 21419 | 20516 | 19072 | 22420 | 22682 | 22701
2034 | 2034 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 18 | 17028 | 17074 | 17686 | 16160 | 16891 | 19133 | 19050 | 19275 | 19552 | 18708 | 18530 | 20751 | 20992 | 21409 | 22008 | 20698 | 19713 | 22176 | 22516 | 22777
2035 | 2035 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 19 | 17138 | 17299 | 17725 | 16229 | 17106 | 19213 | 19284 | 19636 | 19883 | 19121 | 19280 | 20753 | 21357 | 21962 | 22856 | 21255 | 20850 | 22766 | 23318 | 23510
2036 | 2036 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 20 | 17352 | 17583 | 18170 | 16620 | 17520 | 19559 | 19539 | 20072 | 20477 | 19633 | 19980 | 21332 | 22096 | 23053 | 23969 | 22302 | 22118 | 23791 | 24401 | 24818
2037 | 2037 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 21 | 16972 | 17175 | 17838 | 16489 | 17362 | 19353 | 19478 | 20007 | 20503 | 19856 | 20138 | 21641 | 22624 | 23617 | 24599 | 23108 | 22711 | 24621 | 25240 | 25662
2038 | 2038 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 22 | 15967 | 16225 | 16904 | 15895 | 16656 | 18438 | 18610 | 19279 | 19779 | 19383 | 19740 | 21009 | 22124 | 23221 | 24343 | 22986 | 22576 | 24310 | 25081 | 25406
2039 | 2039 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 23 | 14829 | 15089 | 15835 | 15056 | 15877 | 17344 | 17566 | 18256 | 18811 | 18707 | 19015 | 20053 | 21294 | 22443 | 23618 | 22488 | 21985 | 23587 | 24355 | 24714
2040 | 2040 | 85 | 3 | 26 | Winter | 3 | 25 | Winter | 24 | 13958 | 14230 | 15019 | 14457 | 15237 | 16472 | 16708 | 17438 | 18091 | 18178 | 18606 | 19485 | 20546 | 21786 | 23055 | 22046 | 21577 | 22897 | 23707 | 24124
2041 | 2041 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 1 | 12818 | 13501 | 14421 | 15052 | 14765 | 15641 | 16167 | 16894 | 17446 | 17350 | 17956 | 19420 | 20216 | 21174 | 21840 | 20330 | 20605 | 22639 | 23346 | 23343
2042 | 2042 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 2 | 12539 | 13190 | 14137 | 14709 | 14497 | 15245 | 15818 | 16527 | 17067 | 17033 | 17762 | 18949 | 19736 | 20749 | 21325 | 20080 | 20485 | 22083 | 22753 | 22770
2043 | 2043 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 3 | 12467 | 13045 | 14029 | 14555 | 14426 | 15147 | 15732 | 16407 | 17080 | 16884 | 17756 | 18773 | 19529 | 20597 | 21033 | 19617 | 20248 | 21792 | 22358 | 22559
2044 | 2044 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 4 | 12538 | 13113 | 14124 | 14606 | 14527 | 15224 | 15818 | 16454 | 17162 | 16889 | 17836 | 18601 | 19299 | 20267 | 20631 | 18968 | 19732 | 21345 | 21861 | 22077
2045 | 2045 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 5 | 12958 | 13616 | 14663 | 14858 | 14753 | 15678 | 16293 | 16915 | 17139 | 16998 | 18295 | 18708 | 19346 | 20148 | 20273 | 18536 | 19518 | 21153 | 21562 | 21404
2046 | 2046 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 6 | 14117 | 14769 | 15765 | 15408 | 15151 | 16706 | 17419 | 17864 | 17183 | 17153 | 19178 | 19283 | 19931 | 20431 | 19973 | 18212 | 19980 | 21485 | 21658 | 20736
2047 | 2047 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 7 | 15518 | 16086 | 17005 | 15919 | 15291 | 17909 | 18666 | 18989 | 17107 | 17160 | 20224 | 20105 | 20739 | 20980 | 19840 | 17785 | 20755 | 22056 | 22236 | 20102
2048 | 2048 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 8 | 15905 | 16512 | 17556 | 15951 | 15184 | 18195 | 18889 | 19351 | 17361 | 16918 | 20455 | 20120 | 20797 | 21242 | 19615 | 17425 | 20899 | 21957 | 22368 | 20077
2049 | 2049 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 9 | 15940 | 16547 | 17673 | 16261 | 15384 | 18253 | 18827 | 19303 | 17426 | 17032 | 20244 | 19981 | 20622 | 21129 | 19706 | 17519 | 20728 | 21709 | 22229 | 20039
2050 | 2050 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 10 | 15763 | 16486 | 17488 | 16285 | 15273 | 18120 | 18632 | 19102 | 16962 | 17031 | 19958 | 19874 | 20445 | 20752 | 19705 | 17673 | 20760 | 21587 | 22158 | 19680
2051 | 2051 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 11 | 15604 | 16344 | 17351 | 16222 | 15153 | 18080 | 18567 | 18942 | 16698 | 17011 | 19730 | 19921 | 20430 | 20617 | 19683 | 17692 | 20636 | 21625 | 22177 | 19541
2052 | 2052 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 12 | 15364 | 16111 | 17150 | 16014 | 15073 | 17795 | 18295 | 18661 | 16534 | 16935 | 19448 | 19640 | 20202 | 20468 | 19485 | 17596 | 20381 | 21394 | 21923 | 19408
2053 | 2053 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 13 | 15298 | 16129 | 17115 | 15855 | 14984 | 17834 | 18320 | 18691 | 16313 | 17010 | 19415 | 19694 | 20243 | 20321 | 19337 | 17480 | 20159 | 21424 | 21808 | 19174
2054 | 2054 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 14 | 15246 | 16131 | 17083 | 15671 | 14931 | 17746 | 18266 | 18629 | 16162 | 17002 | 19383 | 19544 | 20152 | 20167 | 19090 | 17382 | 19961 | 21310 | 21590 | 18963
2055 | 2055 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 15 | 15405 | 16322 | 17217 | 15759 | 15168 | 17786 | 18399 | 18753 | 16171 | 17208 | 19440 | 19515 | 20250 | 20199 | 19081 | 17574 | 19964 | 21386 | 21583 | 18890
2056 | 2056 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 16 | 15766 | 16657 | 17501 | 16024 | 15620 | 18262 | 18708 | 19000 | 16483 | 17623 | 19733 | 20031 | 20463 | 20272 | 19182 | 17892 | 20143 | 21542 | 21636 | 19021
2057 | 2057 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 17 | 16313 | 17039 | 17864 | 16610 | 16082 | 18833 | 19203 | 19347 | 17118 | 18173 | 20203 | 20622 | 20981 | 20680 | 19836 | 18408 | 20683 | 22100 | 22074 | 19692
2058 | 2058 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 18 | 16299 | 16872 | 17890 | 16567 | 16424 | 18595 | 18900 | 19261 | 17431 | 18223 | 20259 | 20412 | 20853 | 21402 | 20150 | 19200 | 21275 | 22081 | 22304 | 20312
2059 | 2059 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 19 | 16467 | 16889 | 18065 | 16694 | 16996 | 18734 | 19139 | 19409 | 17665 | 18784 | 20619 | 20774 | 21468 | 22261 | 20733 | 20381 | 22148 | 22931 | 23104 | 21094
2060 | 2060 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 20 | 16673 | 17275 | 18303 | 17024 | 17445 | 18917 | 19481 | 19873 | 18287 | 19327 | 21258 | 21430 | 22217 | 23289 | 21712 | 21606 | 23457 | 23986 | 24407 | 22415
2061 | 2061 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 21 | 16324 | 16918 | 17978 | 16814 | 17200 | 18782 | 19332 | 19787 | 18474 | 19377 | 21176 | 21840 | 22703 | 23829 | 22442 | 22140 | 23801 | 24800 | 25224 | 23451
2062 | 2062 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 22 | 15323 | 15987 | 17126 | 16096 | 16574 | 17893 | 18555 | 19001 | 18076 | 18929 | 20366 | 21291 | 22324 | 23532 | 22277 | 21996 | 23231 | 24633 | 24974 | 23560
2063 | 2063 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 23 | 14185 | 14920 | 16135 | 15317 | 15732 | 16832 | 17506 | 18001 | 17296 | 18181 | 19357 | 20424 | 21495 | 22789 | 21772 | 21396 | 22360 | 23907 | 24287 | 23020
2064 | 2064 | 86 | 3 | 27 | Winter | 3 | 26 | Winter | 24 | 13260 | 14105 | 15350 | 14666 | 15242 | 15955 | 16660 | 17242 | 16782 | 17741 | 18686 | 19659 | 20789 | 22207 | 21324 | 20990 | 21669 | 23255 | 23687 | 22675
2065 | 2065 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 1 | 12707 | 13587 | 14489 | 14299 | 14629 | 15436 | 16138 | 16733 | 17562 | 17187 | 18758 | 19353 | 20390 | 21082 | 19726 | 20074 | 21853 | 22930 | 23119 | 23318
2066 | 2066 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 2 | 12395 | 13282 | 14146 | 13993 | 14459 | 15071 | 15761 | 16421 | 17163 | 17003 | 18448 | 18878 | 19869 | 20570 | 19477 | 19947 | 21633 | 22321 | 22622 | 22759
2067 | 2067 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 3 | 12283 | 13167 | 13998 | 13837 | 14477 | 14983 | 15652 | 16327 | 17032 | 17030 | 18368 | 18700 | 19576 | 20303 | 19038 | 19722 | 21240 | 21937 | 22407 | 22431
2068 | 2068 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 4 | 12316 | 13236 | 14016 | 13878 | 14650 | 15052 | 15701 | 16355 | 16985 | 17144 | 18345 | 18502 | 19295 | 19930 | 18398 | 19204 | 20547 | 21431 | 21863 | 21875
2069 | 2069 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 5 | 12908 | 13791 | 14298 | 14207 | 15291 | 15583 | 16236 | 16820 | 17109 | 17703 | 18635 | 18674 | 19313 | 19661 | 18038 | 19066 | 20318 | 21181 | 21563 | 21384
2070 | 2070 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 6 | 14166 | 14929 | 14899 | 14673 | 16456 | 16772 | 17275 | 17703 | 17333 | 18672 | 19427 | 19360 | 19697 | 19434 | 17768 | 19567 | 20716 | 21307 | 21635 | 20939
2071 | 2071 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 7 | 15519 | 16231 | 15474 | 14887 | 17812 | 18087 | 18486 | 18860 | 17577 | 19798 | 20243 | 20246 | 20493 | 19375 | 17398 | 20376 | 21107 | 21920 | 22064 | 20710
2072 | 2072 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 8 | 15904 | 16849 | 15610 | 14844 | 18268 | 18413 | 18949 | 19455 | 17639 | 20131 | 20424 | 20405 | 20812 | 19250 | 17130 | 20585 | 21031 | 22137 | 22315 | 20513
2073 | 2073 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 9 | 16118 | 17154 | 16138 | 15276 | 18352 | 18553 | 19115 | 19622 | 18125 | 20125 | 20411 | 20452 | 20928 | 19543 | 17422 | 20617 | 21030 | 22195 | 22346 | 20766
2074 | 2074 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 10 | 16176 | 17141 | 16341 | 15491 | 18251 | 18506 | 19071 | 19496 | 18225 | 19979 | 20393 | 20414 | 20965 | 19674 | 17711 | 20789 | 21333 | 22268 | 22157 | 20942
2075 | 2075 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 11 | 16143 | 17057 | 16339 | 15536 | 18057 | 18479 | 18952 | 19423 | 18194 | 19794 | 20370 | 20436 | 20967 | 19695 | 17773 | 20709 | 21475 | 22319 | 22124 | 20996
2076 | 2076 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 12 | 15953 | 16913 | 16189 | 15509 | 17836 | 18261 | 18716 | 19280 | 18034 | 19567 | 20142 | 20244 | 20754 | 19539 | 17719 | 20496 | 21202 | 22111 | 22043 | 20845
2077 | 2077 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 13 | 15983 | 16938 | 16072 | 15586 | 17819 | 18329 | 18791 | 19355 | 17956 | 19590 | 20143 | 20342 | 20704 | 19449 | 17660 | 20328 | 21013 | 22051 | 21947 | 20740
2078 | 2078 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 14 | 15952 | 16897 | 15890 | 15582 | 17808 | 18272 | 18733 | 19311 | 17752 | 19561 | 19951 | 20254 | 20527 | 19205 | 17559 | 20132 | 20683 | 21830 | 21765 | 20461
2079 | 2079 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 15 | 15890 | 16839 | 15787 | 15630 | 17707 | 18217 | 18676 | 19208 | 17595 | 19429 | 19825 | 20162 | 20367 | 19009 | 17564 | 19940 | 20479 | 21633 | 21571 | 20238
2080 | 2080 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 16 | 16004 | 16919 | 15849 | 15880 | 17864 | 18329 | 18734 | 19209 | 17603 | 19531 | 20271 | 20188 | 20305 | 18918 | 17681 | 19921 | 20902 | 21484 | 21376 | 20104
2081 | 2081 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 17 | 16176 | 17120 | 16257 | 16131 | 18194 | 18661 | 18921 | 19462 | 18072 | 19838 | 20591 | 20554 | 20579 | 19423 | 18040 | 20303 | 21016 | 21772 | 21639 | 20626
2082 | 2082 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 18 | 16016 | 17063 | 16116 | 16139 | 18098 | 18319 | 18750 | 19488 | 18098 | 19792 | 20432 | 20337 | 20621 | 19655 | 18761 | 20826 | 21445 | 21937 | 22396 | 20948
2083 | 2083 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 19 | 16249 | 17238 | 16243 | 16593 | 18234 | 18559 | 18890 | 19684 | 18352 | 20091 | 20832 | 20887 | 21193 | 20200 | 19916 | 21689 | 22483 | 22734 | 23448 | 21656
2084 | 2084 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 20 | 16483 | 17498 | 16599 | 17043 | 18716 | 18904 | 19346 | 20139 | 18767 | 20680 | 21564 | 21583 | 22233 | 21145 | 21145 | 22990 | 23917 | 24058 | 24736 | 22814
2085 | 2085 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 21 | 16030 | 17150 | 16349 | 16759 | 18264 | 18687 | 19180 | 20049 | 18875 | 20503 | 21673 | 21951 | 22694 | 21783 | 21621 | 23287 | 24534 | 24852 | 25536 | 23733
2086 | 2086 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 22 | 15036 | 16260 | 15580 | 16089 | 17221 | 17854 | 18331 | 19323 | 18314 | 19617 | 21091 | 21487 | 22233 | 21559 | 21408 | 22683 | 24247 | 24571 | 25364 | 23651
2087 | 2087 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 23 | 13941 | 15312 | 14836 | 15294 | 16159 | 16829 | 17344 | 18431 | 17642 | 18617 | 20156 | 20661 | 21465 | 21074 | 20840 | 21837 | 23443 | 23925 | 24738 | 23251
2088 | 2088 | 87 | 3 | 28 | Winter | 3 | 27 | Winter | 24 | 13079 | 14521 | 14169 | 14785 | 15412 | 15962 | 16556 | 17701 | 17069 | 17926 | 19551 | 19937 | 20787 | 20601 | 20411 | 21136 | 22850 | 23312 | 24224 | 22830
2089 | 2089 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 1 | 12588 | 13863 | 14006 | 14167 | 15246 | 15557 | 16187 | 16977 | 16584 | 18102 | 19452 | 19700 | 20408 | 19263 | 19696 | 21468 | 22676 | 22924 | 23179 | 21205
2090 | 2090 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 2 | 12295 | 13514 | 13708 | 13986 | 14997 | 15174 | 15869 | 16570 | 16280 | 17805 | 19094 | 19204 | 19996 | 19040 | 19590 | 21269 | 22445 | 22441 | 22625 | 20939
2091 | 2091 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 3 | 12182 | 13342 | 13536 | 14039 | 14976 | 15041 | 15751 | 16415 | 16162 | 17719 | 19023 | 18958 | 19893 | 18637 | 19392 | 20908 | 22114 | 22244 | 22317 | 20479
2092 | 2092 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 4 | 12233 | 13358 | 13580 | 14345 | 15129 | 15122 | 15832 | 16433 | 16182 | 17793 | 18957 | 18758 | 19604 | 18047 | 18918 | 20262 | 21337 | 21726 | 21777 | 19744
2093 | 2093 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 5 | 12767 | 13608 | 13871 | 14851 | 15680 | 15643 | 16308 | 16567 | 16371 | 18119 | 19189 | 18834 | 19591 | 17720 | 18802 | 20053 | 21032 | 21429 | 21274 | 19243
2094 | 2094 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 6 | 13945 | 14211 | 14346 | 15652 | 16865 | 16691 | 17222 | 16831 | 16614 | 18938 | 19946 | 19341 | 19963 | 17518 | 19365 | 20497 | 21394 | 21535 | 20848 | 18861
2095 | 2095 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 7 | 15233 | 14734 | 14528 | 16537 | 17966 | 17851 | 18371 | 17093 | 16647 | 19758 | 20843 | 20164 | 20541 | 17134 | 20147 | 20880 | 21950 | 21917 | 20580 | 18358
2096 | 2096 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 8 | 15604 | 14828 | 14431 | 17141 | 18277 | 18255 | 18934 | 17134 | 16397 | 19931 | 20990 | 20419 | 20794 | 16777 | 20268 | 20714 | 21827 | 22077 | 20281 | 17938
2097 | 2097 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 9 | 15914 | 15479 | 15004 | 17727 | 18523 | 18564 | 19259 | 17779 | 16817 | 20076 | 20895 | 20630 | 20977 | 17167 | 20398 | 20806 | 21611 | 22212 | 20626 | 18285
2098 | 2098 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 10 | 15930 | 15678 | 15202 | 17713 | 18388 | 18505 | 19111 | 17859 | 16890 | 20030 | 20649 | 20565 | 20656 | 17364 | 20481 | 21005 | 21599 | 21931 | 20709 | 18531
2099 | 2099 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 11 | 15796 | 15655 | 15247 | 17607 | 18222 | 18377 | 19033 | 17840 | 16875 | 20007 | 20498 | 20496 | 20509 | 17360 | 20339 | 21080 | 21531 | 21827 | 20709 | 18564
2100 | 2100 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 12 | 15590 | 15457 | 15193 | 17416 | 17944 | 18116 | 18846 | 17637 | 16798 | 19747 | 20309 | 20244 | 20367 | 17274 | 20099 | 20774 | 21301 | 21707 | 20523 | 18481
2101 | 2101 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 13 | 15689 | 15305 | 15211 | 17436 | 17926 | 18106 | 18823 | 17459 | 16931 | 19642 | 20323 | 20211 | 20283 | 17228 | 19944 | 20594 | 21254 | 21621 | 20428 | 18423
2102 | 2102 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 14 | 15643 | 15057 | 15120 | 17351 | 17739 | 17956 | 18678 | 17150 | 16857 | 19347 | 20223 | 19990 | 20072 | 17075 | 19691 | 20209 | 21096 | 21384 | 20098 | 18244
2103 | 2103 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 15 | 15579 | 14862 | 15088 | 17268 | 17625 | 17831 | 18500 | 16917 | 16812 | 19140 | 20189 | 19781 | 19853 | 17019 | 19438 | 19954 | 21033 | 21128 | 19810 | 18172
2104 | 2104 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 16 | 15781 | 15016 | 15413 | 17594 | 18106 | 17983 | 18595 | 17011 | 17093 | 19671 | 20460 | 19805 | 19805 | 17218 | 19493 | 20452 | 21207 | 21008 | 19748 | 18341
2105 | 2105 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 17 | 16176 | 15560 | 15803 | 18116 | 18576 | 18318 | 18989 | 17621 | 17653 | 20133 | 20966 | 20250 | 20228 | 17744 | 20048 | 20735 | 21611 | 21441 | 20438 | 18887
2106 | 2106 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 18 | 15984 | 15474 | 15855 | 18118 | 18511 | 18246 | 19093 | 17712 | 17679 | 20049 | 20812 | 20285 | 20903 | 18499 | 20606 | 21200 | 21992 | 22243 | 20793 | 19707
2107 | 2107 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 19 | 16047 | 15640 | 16349 | 17796 | 18800 | 18424 | 19311 | 17974 | 18240 | 20435 | 21345 | 20797 | 21733 | 19644 | 21454 | 22225 | 23019 | 23307 | 21526 | 20975
2108 | 2108 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 20 | 16453 | 16041 | 16845 | 18136 | 19160 | 18951 | 19816 | 18427 | 18777 | 21172 | 22185 | 21751 | 22713 | 20823 | 22713 | 23621 | 24572 | 24587 | 22690 | 22323
2109 | 2109 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 21 | 16082 | 15751 | 16531 | 17918 | 18787 | 18735 | 19643 | 18438 | 18733 | 21167 | 22374 | 22108 | 23165 | 21233 | 22952 | 24180 | 25317 | 25367 | 23592 | 22944
2110 | 2110 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 22 | 15126 | 14992 | 15855 | 16996 | 17924 | 17862 | 18882 | 17837 | 18218 | 20528 | 21797 | 21589 | 22808 | 20995 | 22334 | 23880 | 25076 | 25199 | 23523 | 22829
2111 | 2111 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 23 | 14071 | 14191 | 15011 | 15961 | 16817 | 16823 | 17931 | 17110 | 17466 | 19518 | 20851 | 20764 | 22057 | 20366 | 21448 | 23048 | 24294 | 24532 | 23073 | 22270
2112 | 2112 | 88 | 3 | 29 | Winter | 3 | 28 | Winter | 24 | 13262 | 13539 | 14499 | 15325 | 16115 | 16040 | 17197 | 16527 | 17007 | 18913 | 20206 | 20086 | 21465 | 19945 | 20759 | 22461 | 23657 | 24020 | 22677 | 21889
2113 | 2113 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 1 | 13176 | 13596 | 14243 | 15110 | 15965 | 15803 | 16659 | 16282 | 16494 | 18974 | 19774 | 22845 | 20752 | 19436 | 21254 | 22479 | 23135 | 23185 | 21276 | 21169
2114 | 2114 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 2 | 12783 | 13316 | 14093 | 14868 | 15703 | 15409 | 16284 | 15991 | 16306 | 18679 | 19439 | 22340 | 20276 | 19351 | 21065 | 22257 | 22810 | 22633 | 21005 | 20900
2115 | 2115 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 3 | 12656 | 13174 | 14116 | 14859 | 15667 | 15381 | 16221 | 15930 | 16322 | 18759 | 19418 | 22203 | 20012 | 19129 | 20679 | 21899 | 22410 | 22283 | 20503 | 20911
2116 | 2116 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 4 | 12793 | 13217 | 14307 | 15050 | 15820 | 15539 | 16287 | 16024 | 16642 | 18790 | 19370 | 22028 | 19742 | 18723 | 20101 | 21194 | 21667 | 21787 | 19811 | 20823
2117 | 2117 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 5 | 13034 | 13460 | 14861 | 15523 | 16340 | 15662 | 16394 | 16134 | 17093 | 19019 | 19521 | 21883 | 19523 | 18654 | 19929 | 20916 | 21343 | 21310 | 19314 | 20731
2118 | 2118 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 6 | 13382 | 13938 | 16033 | 16679 | 17538 | 15908 | 16717 | 16375 | 17678 | 19841 | 20188 | 22154 | 19369 | 19237 | 20405 | 21303 | 21562 | 20894 | 18925 | 20838
2119 | 2119 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 7 | 13608 | 14172 | 17391 | 17818 | 18893 | 16023 | 17044 | 16451 | 18363 | 20800 | 21020 | 22976 | 19367 | 20100 | 20875 | 21957 | 22033 | 20689 | 18470 | 21091
2120 | 2120 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 8 | 13881 | 13998 | 17647 | 18080 | 19100 | 16231 | 16986 | 16162 | 18773 | 20849 | 21027 | 23326 | 19079 | 20147 | 20640 | 21777 | 21892 | 20298 | 17957 | 21261
2121 | 2121 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 9 | 14156 | 14190 | 17481 | 17973 | 18733 | 16346 | 17261 | 16263 | 18905 | 20385 | 20674 | 23023 | 19107 | 19927 | 20379 | 21204 | 21538 | 20280 | 17941 | 21183
2122 | 2122 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 10 | 14080 | 14262 | 17194 | 17670 | 18404 | 16016 | 17092 | 16129 | 18821 | 19836 | 20086 | 22289 | 19070 | 19931 | 20497 | 21110 | 21379 | 20283 | 18109 | 20907
2123 | 2123 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 11 | 14080 | 14311 | 16994 | 17504 | 18235 | 15886 | 17002 | 16099 | 18817 | 19582 | 19835 | 21893 | 19063 | 19848 | 20627 | 21077 | 21297 | 20333 | 18199 | 20786
2124 | 2124 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 12 | 13951 | 14307 | 16796 | 17295 | 18057 | 15761 | 16848 | 16087 | 18678 | 19443 | 19595 | 21592 | 18906 | 19630 | 20354 | 20901 | 21067 | 20181 | 18151 | 20678
2125 | 2125 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 13 | 13732 | 14212 | 16592 | 17074 | 17959 | 15513 | 16530 | 15961 | 18616 | 19309 | 19348 | 21288 | 18727 | 19382 | 20080 | 20759 | 20792 | 19990 | 17994 | 20556
2126 | 2126 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 14 | 13544 | 14114 | 16477 | 16854 | 17880 | 15329 | 16211 | 15830 | 18487 | 19197 | 19106 | 21010 | 18407 | 19123 | 19692 | 20596 | 20430 | 19654 | 17812 | 20352
2127 | 2127 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 15 | 13386 | 14127 | 16369 | 16801 | 17937 | 15142 | 16053 | 15833 | 18413 | 19241 | 19028 | 20789 | 18197 | 18919 | 19479 | 20578 | 20290 | 19410 | 17779 | 20241
2128 | 2128 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 16 | 13732 | 14477 | 16633 | 17317 | 18335 | 15417 | 16192 | 16173 | 18752 | 19561 | 19177 | 20757 | 18245 | 19027 | 20028 | 20812 | 20295 | 19389 | 17990 | 20449
2129 | 2129 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 17 | 14360 | 14994 | 17234 | 17913 | 18927 | 16124 | 16955 | 16860 | 19340 | 20238 | 19736 | 21482 | 19032 | 19680 | 20422 | 21313 | 20767 | 20180 | 18636 | 21166
2130 | 2130 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 18 | 14358 | 15354 | 17534 | 18282 | 18879 | 16452 | 17472 | 17375 | 19578 | 20563 | 20325 | 22344 | 19476 | 20410 | 21059 | 21859 | 21675 | 20728 | 19645 | 22005
2131 | 2131 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 19 | 14582 | 16021 | 17890 | 18780 | 19302 | 16709 | 17937 | 18171 | 19515 | 21270 | 21013 | 23300 | 20123 | 21356 | 22172 | 22977 | 22797 | 21589 | 21046 | 22483
2132 | 2132 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 20 | 14961 | 16490 | 18416 | 19167 | 19871 | 17251 | 18317 | 18720 | 19980 | 21959 | 21848 | 24162 | 21015 | 22587 | 23524 | 24488 | 24322 | 22755 | 22412 | 23400
2133 | 2133 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 21 | 14765 | 16168 | 17925 | 18766 | 19564 | 17212 | 18267 | 18616 | 20019 | 22054 | 22120 | 24513 | 21580 | 22779 | 24037 | 25192 | 25134 | 23656 | 23046 | 24087
2134 | 2134 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 22 | 14078 | 15441 | 16858 | 17853 | 18654 | 16655 | 17607 | 18041 | 19211 | 21387 | 21513 | 24097 | 21309 | 22104 | 23687 | 24908 | 24839 | 23565 | 22913 | 23648
2135 | 2135 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 23 | 13245 | 14594 | 15749 | 16717 | 17528 | 15815 | 16837 | 17228 | 18173 | 20376 | 20592 | 23277 | 20734 | 21176 | 22822 | 24085 | 24084 | 23104 | 22325 | 22786
2136 | 2136 | 89 | 3 | 30 | Winter | 3 | 29 | Winter | 24 | 12640 | 14055 | 15003 | 16018 | 16755 | 15230 | 16233 | 16757 | 17557 | 19719 | 19991 | 22464 | 20255 | 20457 | 22206 | 23434 | 23518 | 22682 | 21940 | 22283
2137 | 2137 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 1 | 13298 | 13490 | 14639 | 15513 | 15847 | 16018 | 15751 | 16234 | 17538 | 18984 | 19696 | 19949 | 18911 | 20590 | 21890 | 22588 | 22618 | 20981 | 21083 | 22716
2138 | 2138 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 2 | 12997 | 13363 | 14425 | 15285 | 15603 | 15654 | 15471 | 16099 | 17306 | 18679 | 19408 | 19506 | 18716 | 20442 | 21701 | 22284 | 22063 | 20729 | 20971 | 22513
2139 | 2139 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 3 | 12858 | 13340 | 14360 | 15278 | 15621 | 15508 | 15327 | 16127 | 17352 | 18603 | 19315 | 19276 | 18289 | 20091 | 21381 | 21912 | 21847 | 20243 | 20719 | 22097
2140 | 2140 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 4 | 12894 | 13505 | 14522 | 15400 | 15782 | 15564 | 15415 | 16328 | 17487 | 18609 | 19258 | 19060 | 17767 | 19554 | 20707 | 21195 | 21433 | 19547 | 20171 | 21395
2141 | 2141 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 5 | 13109 | 14092 | 15049 | 15936 | 16313 | 15783 | 15648 | 16944 | 17781 | 18958 | 19567 | 18913 | 17487 | 19435 | 20468 | 20908 | 20822 | 19053 | 19934 | 21077
2142 | 2142 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 6 | 13709 | 15347 | 16251 | 17217 | 17456 | 16210 | 16010 | 18043 | 18662 | 19796 | 20358 | 18849 | 17325 | 19965 | 20903 | 21164 | 20222 | 18668 | 20364 | 21387
2143 | 2143 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 7 | 14264 | 16752 | 17471 | 18609 | 18575 | 16631 | 16204 | 19273 | 19537 | 20790 | 21216 | 18913 | 17020 | 20469 | 21591 | 21647 | 19633 | 18211 | 21110 | 21726
2144 | 2144 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 8 | 14180 | 16934 | 17677 | 18720 | 18615 | 16500 | 15856 | 19382 | 19517 | 20752 | 21181 | 18584 | 16500 | 20189 | 21360 | 21449 | 19409 | 17627 | 21002 | 21326
2145 | 2145 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 9 | 14289 | 16598 | 17412 | 18182 | 18202 | 16601 | 15801 | 18983 | 19119 | 20229 | 20586 | 18479 | 16370 | 19772 | 20637 | 20946 | 19121 | 17450 | 20565 | 20851
2146 | 2146 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 10 | 14260 | 16308 | 17122 | 17735 | 17646 | 16480 | 15721 | 18608 | 18694 | 19692 | 20062 | 18339 | 16399 | 19784 | 20442 | 20682 | 18654 | 17515 | 20511 | 20927
2147 | 2147 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 11 | 14276 | 16188 | 17025 | 17567 | 17435 | 16483 | 15787 | 18458 | 18613 | 19522 | 19803 | 18367 | 16486 | 19924 | 20434 | 20636 | 18586 | 17632 | 20504 | 21133
2148 | 2148 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 12 | 14142 | 16035 | 16843 | 17421 | 17202 | 16342 | 15783 | 18257 | 18422 | 19293 | 19560 | 18235 | 16456 | 19678 | 20276 | 20426 | 18520 | 17610 | 20324 | 20904
2149 | 2149 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 13 | 13898 | 15923 | 16736 | 17420 | 16994 | 16180 | 15822 | 18202 | 18195 | 19246 | 19377 | 18089 | 16338 | 19430 | 20157 | 20190 | 18270 | 17476 | 20087 | 20644
2150 | 2150 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 14 | 13645 | 15812 | 16550 | 17372 | 16811 | 15903 | 15735 | 18096 | 17890 | 19067 | 19136 | 17775 | 16181 | 19040 | 19981 | 19832 | 17976 | 17284 | 19796 | 20217
2151 | 2151 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 15 | 13537 | 15732 | 16529 | 17469 | 16826 | 15774 | 15763 | 17979 | 17798 | 19015 | 19001 | 17594 | 16202 | 18860 | 19991 | 19713 | 17730 | 17276 | 19597 | 20006
2152 | 2152 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 16 | 13784 | 16062 | 17044 | 17905 | 17144 | 15978 | 16164 | 18265 | 18410 | 19244 | 19095 | 17706 | 16497 | 19480 | 20291 | 19790 | 17819 | 17542 | 19730 | 20573
2153 | 2153 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 17 | 14489 | 16669 | 17660 | 18552 | 17624 | 16753 | 16854 | 18882 | 19085 | 19806 | 19629 | 18532 | 17167 | 19931 | 20844 | 20297 | 18659 | 18240 | 20456 | 21039
2154 | 2154 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 18 | 14801 | 16879 | 17965 | 18606 | 18158 | 17089 | 17133 | 19147 | 19594 | 20090 | 20226 | 19041 | 18191 | 20662 | 21503 | 21299 | 19549 | 19364 | 21363 | 21851
2155 | 2155 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 19 | 15165 | 17195 | 18410 | 19028 | 18596 | 17451 | 17804 | 19573 | 20202 | 20581 | 20849 | 19641 | 19455 | 21758 | 22595 | 22415 | 20499 | 20801 | 22471 | 23117
2156 | 2156 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 20 | 15545 | 17700 | 18775 | 19529 | 19119 | 17798 | 18307 | 20112 | 20841 | 21286 | 21780 | 20468 | 20603 | 23056 | 24055 | 23898 | 21843 | 22164 | 23871 | 24630
2157 | 2157 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 21 | 15232 | 17171 | 18325 | 19146 | 18872 | 17673 | 18130 | 19777 | 20746 | 21416 | 22043 | 20911 | 20935 | 23475 | 24672 | 24639 | 22815 | 22769 | 24253 | 25316
2158 | 2158 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 22 | 14449 | 16101 | 17378 | 18191 | 17961 | 16972 | 17514 | 18786 | 20020 | 20718 | 21547 | 20557 | 20640 | 23069 | 24333 | 24307 | 22874 | 22626 | 23669 | 25055
2159 | 2159 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 23 | 13636 | 14992 | 16246 | 17077 | 16898 | 16206 | 16702 | 17697 | 18971 | 19771 | 20668 | 19963 | 19988 | 22190 | 23514 | 23557 | 22333 | 22057 | 22816 | 24248
2160 | 2160 | 90 | 3 | 31 | Winter | 3 | 30 | Winter | 24 | 12972 | 14212 | 15523 | 16294 | 16185 | 15577 | 16202 | 16971 | 18336 | 19135 | 20068 | 19451 | 19531 | 21558 | 22859 | 22973 | 21950 | 21659 | 22136 | 23670
2161 | 2161 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 1 | 12801 | 13726 | 14882 | 15220 | 15822 | 14965 | 15466 | 16645 | 18105 | 18596 | 18216 | 18249 | 18766 | 21265 | 22043 | 22539 | 21767 | 20844 | 22478 | 23484
2162 | 2162 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 2 | 12518 | 13579 | 14726 | 15053 | 15592 | 14792 | 15459 | 16567 | 17813 | 18516 | 18005 | 18056 | 18685 | 21069 | 21735 | 22318 | 21435 | 20709 | 22260 | 23237
2163 | 2163 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 3 | 12377 | 13443 | 14655 | 14928 | 15594 | 14539 | 15364 | 16395 | 17844 | 18308 | 17724 | 17688 | 18521 | 20801 | 21414 | 21951 | 21011 | 20484 | 21880 | 22900
2164 | 2164 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 4 | 12390 | 13438 | 14578 | 14859 | 15762 | 14352 | 15278 | 16225 | 17892 | 17963 | 17461 | 17209 | 18142 | 20164 | 20727 | 21204 | 20420 | 19935 | 21168 | 22084
2165 | 2165 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 5 | 12671 | 13871 | 15008 | 15347 | 16336 | 14456 | 15755 | 16516 | 18290 | 18172 | 17461 | 16987 | 18109 | 19979 | 20483 | 20893 | 20060 | 19703 | 20853 | 21684
2166 | 2166 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 6 | 13205 | 15085 | 16262 | 16544 | 17543 | 14812 | 16875 | 17509 | 19288 | 19023 | 17809 | 16909 | 18773 | 20489 | 20805 | 21219 | 20031 | 20160 | 21196 | 21967
2167 | 2167 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 7 | 13474 | 16291 | 17585 | 17682 | 18771 | 14939 | 18072 | 18443 | 20373 | 19861 | 17909 | 16653 | 19647 | 21212 | 21310 | 21730 | 19757 | 20900 | 21512 | 22491
2168 | 2168 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 8 | 13398 | 16644 | 17849 | 17879 | 19087 | 14754 | 18346 | 18622 | 20520 | 20019 | 17635 | 16329 | 19777 | 21163 | 21275 | 21700 | 19271 | 20958 | 21265 | 22306
2169 | 2169 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 9 | 13319 | 16278 | 17251 | 17380 | 18521 | 14638 | 17888 | 18167 | 19801 | 19362 | 17394 | 16112 | 19302 | 20351 | 20673 | 21023 | 18941 | 20419 | 20685 | 21406
2170 | 2170 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 10 | 13320 | 15995 | 16838 | 16961 | 17964 | 14595 | 17549 | 17926 | 19254 | 18863 | 17270 | 16057 | 19136 | 20079 | 20333 | 20737 | 18871 | 20288 | 20685 | 21185
2171 | 2171 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 11 | 13473 | 15949 | 16721 | 16850 | 17698 | 14700 | 17434 | 17938 | 19136 | 18617 | 17189 | 16169 | 19111 | 20100 | 20321 | 20661 | 18856 | 20299 | 20926 | 21249
2172 | 2172 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 12 | 13480 | 15770 | 16554 | 16583 | 17410 | 14659 | 17189 | 17684 | 18986 | 18323 | 17005 | 16122 | 18905 | 19917 | 20088 | 20378 | 18692 | 20094 | 20675 | 21088
2173 | 2173 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 13 | 13497 | 15596 | 16465 | 16391 | 17188 | 14571 | 16997 | 17472 | 19055 | 17983 | 16784 | 16015 | 18696 | 19808 | 19853 | 20021 | 18453 | 19866 | 20424 | 20973
2174 | 2174 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 14 | 13439 | 15430 | 16420 | 16246 | 17010 | 14479 | 16886 | 17209 | 19026 | 17734 | 16406 | 15889 | 18464 | 19670 | 19534 | 19692 | 18021 | 19611 | 20030 | 20812
2175 | 2175 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 15 | 13428 | 15409 | 16502 | 16243 | 16891 | 14500 | 16762 | 17107 | 19055 | 17602 | 16293 | 15882 | 18247 | 19661 | 19396 | 19469 | 17849 | 19386 | 19799 | 20783
2176 | 2176 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 16 | 13874 | 15927 | 16977 | 16614 | 17153 | 14936 | 17083 | 17716 | 19489 | 17740 | 16587 | 16249 | 18469 | 20019 | 19533 | 19513 | 18059 | 19565 | 20415 | 21103
2177 | 2177 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 17 | 14425 | 16530 | 17590 | 17062 | 17740 | 15577 | 17667 | 18303 | 20176 | 18237 | 17403 | 16933 | 19185 | 20576 | 20054 | 19994 | 18845 | 20301 | 20889 | 21686
2178 | 2178 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 18 | 14668 | 16963 | 17875 | 17565 | 18166 | 16176 | 18233 | 18831 | 20184 | 19200 | 18625 | 17858 | 19951 | 21154 | 20987 | 21106 | 20270 | 21153 | 21627 | 22360
2179 | 2179 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 19 | 15295 | 17525 | 18448 | 18066 | 18459 | 17059 | 18881 | 19535 | 20722 | 20026 | 19351 | 19071 | 20888 | 22206 | 22062 | 22276 | 21399 | 22263 | 22891 | 23595
2180 | 2180 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 20 | 15719 | 18055 | 19093 | 18743 | 19055 | 17786 | 19666 | 20377 | 21301 | 21177 | 20260 | 20146 | 22085 | 23603 | 23472 | 23886 | 22722 | 23667 | 24402 | 25209
2181 | 2181 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 21 | 15312 | 17522 | 18643 | 18406 | 18759 | 17534 | 19235 | 20142 | 21220 | 21286 | 20662 | 20350 | 22135 | 24092 | 24115 | 24609 | 23650 | 23979 | 25030 | 25997
2182 | 2182 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 22 | 14593 | 16593 | 17709 | 17519 | 17986 | 16948 | 18268 | 19407 | 20520 | 20753 | 20334 | 20047 | 21463 | 23749 | 23793 | 24453 | 23631 | 23446 | 24814 | 25826
2183 | 2183 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 23 | 13770 | 15465 | 16581 | 16464 | 16984 | 16134 | 17171 | 18335 | 19497 | 19843 | 19721 | 19365 | 20526 | 22894 | 23017 | 23759 | 23170 | 22591 | 24016 | 25068
2184 | 2184 | 91 | 4 | 1 | Winter | 3 | 31 | Winter | 24 | 13220 | 14734 | 15777 | 15723 | 16284 | 15598 | 16397 | 17622 | 18825 | 19171 | 19280 | 18913 | 19817 | 22237 | 22448 | 23183 | 22828 | 21922 | 23455 | 24457
2185 | 2185 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 1 | 12695 | 14370 | 14978 | 14689 | 14798 | 14882 | 16278 | 17359 | 18023 | 17635 | 18400 | 18515 | 20125 | 21612 | 22204 | 21500 | 21436 | 22438 | 23448 | 23896
2186 | 2186 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 2 | 12583 | 14222 | 14806 | 14475 | 14578 | 14828 | 16165 | 17228 | 17910 | 17431 | 18225 | 18336 | 19977 | 21328 | 21997 | 21192 | 21044 | 22224 | 23222 | 23555
2187 | 2187 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 3 | 12553 | 14122 | 14695 | 14289 | 14387 | 14810 | 16030 | 17134 | 17691 | 17211 | 18034 | 18115 | 19657 | 21005 | 21623 | 20759 | 20678 | 21824 | 22862 | 23153
2188 | 2188 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 4 | 12716 | 14119 | 14679 | 14202 | 14465 | 14900 | 15938 | 16940 | 17425 | 17061 | 17794 | 17756 | 19185 | 20395 | 20945 | 20228 | 20149 | 21148 | 22077 | 22348
2189 | 2189 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 5 | 13146 | 14514 | 15139 | 14560 | 14811 | 15216 | 16184 | 17129 | 17680 | 17029 | 17627 | 17682 | 19133 | 20225 | 20698 | 19922 | 19653 | 20858 | 21697 | 21955
2190 | 2190 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 6 | 14024 | 15763 | 16353 | 15581 | 15571 | 15971 | 17214 | 18117 | 18552 | 17434 | 17775 | 18262 | 19725 | 20602 | 21069 | 19920 | 19443 | 21216 | 21981 | 22116
2191 | 2191 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 7 | 14955 | 17103 | 17508 | 16748 | 15999 | 16723 | 18202 | 19171 | 19489 | 17589 | 17599 | 19107 | 20251 | 21143 | 21614 | 19662 | 19025 | 21543 | 22502 | 22501
2192 | 2192 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 8 | 15466 | 17323 | 17650 | 17170 | 15853 | 17156 | 18372 | 19290 | 19578 | 17301 | 17104 | 19268 | 20102 | 21068 | 21540 | 19130 | 18425 | 21243 | 22261 | 22343
2193 | 2193 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 9 | 15485 | 16823 | 17242 | 16958 | 15831 | 17175 | 18044 | 18724 | 19031 | 17208 | 16926 | 18916 | 19631 | 20507 | 20906 | 18834 | 18111 | 20703 | 21401 | 21739
2194 | 2194 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 10 | 15422 | 16596 | 17023 | 16839 | 15808 | 17193 | 18025 | 18535 | 18635 | 17346 | 17047 | 18841 | 19659 | 20262 | 20713 | 18858 | 18237 | 20794 | 21280 | 21520
2195 | 2195 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 11 | 15460 | 16527 | 16971 | 16863 | 15736 | 17241 | 18090 | 18487 | 18505 | 17342 | 17196 | 18880 | 19837 | 20244 | 20631 | 18845 | 18482 | 21029 | 21350 | 21554
2196 | 2196 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 12 | 15378 | 16459 | 16812 | 16803 | 15638 | 17188 | 17948 | 18418 | 18309 | 17271 | 17179 | 18793 | 19650 | 20088 | 20423 | 18752 | 18471 | 20848 | 21265 | 21423
2197 | 2197 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 13 | 15297 | 16357 | 16621 | 16673 | 15440 | 17108 | 17733 | 18316 | 18102 | 17049 | 17087 | 18664 | 19410 | 19853 | 20072 | 18506 | 18375 | 20593 | 21147 | 21187
2198 | 2198 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 14 | 15302 | 16364 | 16530 | 16598 | 15184 | 17054 | 17507 | 18263 | 17992 | 16680 | 16932 | 18532 | 19139 | 19623 | 19833 | 18159 | 18259 | 20286 | 21067 | 20927
2199 | 2199 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 15 | 15338 | 16503 | 16581 | 16567 | 15185 | 17065 | 17451 | 18364 | 18013 | 16606 | 16994 | 18486 | 19012 | 19563 | 19683 | 18080 | 18318 | 20127 | 21109 | 20837
2200 | 2200 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 16 | 15725 | 16921 | 16917 | 16781 | 15521 | 17443 | 17990 | 18736 | 18245 | 16858 | 17398 | 18654 | 19643 | 19680 | 19706 | 18256 | 18651 | 20708 | 21391 | 20886
2201 | 2201 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 17 | 16415 | 17587 | 17412 | 17366 | 16341 | 18116 | 18641 | 19428 | 18784 | 17745 | 18262 | 19397 | 20132 | 20242 | 20218 | 19078 | 19502 | 21219 | 22011 | 21446
2202 | 2202 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 18 | 16667 | 17721 | 17702 | 17802 | 17160 | 18510 | 18992 | 19682 | 19332 | 18749 | 18922 | 20112 | 20663 | 21029 | 21195 | 20356 | 20358 | 21835 | 22555 | 22311
2203 | 2203 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 19 | 16500 | 18104 | 18013 | 18162 | 17471 | 18446 | 19473 | 20241 | 19912 | 19191 | 19462 | 20774 | 21574 | 21920 | 22180 | 21300 | 21203 | 22961 | 23644 | 23378
2204 | 2204 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 20 | 16909 | 18642 | 18601 | 18718 | 17885 | 18950 | 20202 | 21030 | 20826 | 19947 | 20205 | 21728 | 22765 | 23221 | 23676 | 22556 | 22393 | 24396 | 25200 | 24912
2205 | 2205 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 21 | 16604 | 18203 | 18281 | 18439 | 17848 | 18818 | 19950 | 20917 | 20863 | 20280 | 20330 | 21982 | 23113 | 23818 | 24383 | 23473 | 22951 | 25059 | 26023 | 25789
2206 | 2206 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 22 | 15616 | 17215 | 17335 | 17599 | 17196 | 17921 | 19136 | 20132 | 20116 | 19848 | 19774 | 21343 | 22666 | 23413 | 24152 | 23396 | 22646 | 24803 | 25807 | 25532
2207 | 2207 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 23 | 14577 | 16076 | 16254 | 16613 | 16432 | 16853 | 18026 | 19059 | 19119 | 19183 | 19001 | 20403 | 21736 | 22598 | 23409 | 22900 | 21997 | 23984 | 25031 | 24788
2208 | 2208 | 92 | 4 | 2 | Winter | 4 | 1 | Winter | 24 | 13897 | 15250 | 15495 | 15801 | 15902 | 16152 | 17289 | 18280 | 18412 | 18708 | 18533 | 19520 | 21111 | 21999 | 22823 | 22529 | 21599 | 23406 | 24408 | 24239
2209 | 2209 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 1 | 12858 | 14044 | 14067 | 14204 | 15089 | 15517 | 16593 | 17153 | 17017 | 17576 | 17643 | 19184 | 20535 | 20893 | 20733 | 20772 | 20303 | 22943 | 23414 | 23320
2210 | 2210 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 2 | 12713 | 13874 | 13756 | 13958 | 14895 | 15404 | 16469 | 17025 | 16842 | 17450 | 17544 | 19047 | 20358 | 20360 | 20429 | 20380 | 20018 | 22704 | 23061 | 22822
2211 | 2211 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 3 | 12605 | 13762 | 13590 | 13806 | 14798 | 15261 | 16368 | 16858 | 16633 | 17263 | 17372 | 18776 | 20108 | 20249 | 20040 | 20046 | 20083 | 22369 | 22689 | 22619
2212 | 2212 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 4 | 12615 | 13737 | 13536 | 13887 | 14784 | 15174 | 16189 | 16637 | 16308 | 17052 | 17209 | 18349 | 19532 | 19967 | 19530 | 19527 | 20011 | 21579 | 21882 | 22080
2213 | 2213 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 5 | 13045 | 14276 | 13672 | 14270 | 14956 | 15570 | 16555 | 16976 | 16449 | 17101 | 17478 | 18395 | 19448 | 19539 | 19281 | 19091 | 19972 | 21239 | 21519 | 21757
2214 | 2214 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 6 | 14273 | 15528 | 14037 | 15085 | 15520 | 16673 | 17636 | 17949 | 17205 | 17351 | 18396 | 19087 | 20040 | 19109 | 19339 | 18933 | 20137 | 21552 | 21683 | 21812
2215 | 2215 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 7 | 15483 | 16708 | 14211 | 15567 | 15702 | 17744 | 18783 | 18997 | 18107 | 17281 | 19334 | 19690 | 20804 | 18617 | 19123 | 18544 | 20366 | 22096 | 22079 | 22182
2216 | 2216 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 8 | 15917 | 17007 | 14571 | 15547 | 15462 | 18078 | 19071 | 19251 | 18565 | 16945 | 19492 | 19714 | 20864 | 18691 | 18751 | 18077 | 20699 | 22014 | 22056 | 22381
2217 | 2217 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 9 | 15827 | 16832 | 14780 | 15802 | 15575 | 17967 | 18740 | 19024 | 18534 | 16994 | 19211 | 19496 | 20340 | 18585 | 18701 | 18002 | 20630 | 21402 | 21690 | 22131
2218 | 2218 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 10 | 15716 | 16663 | 14741 | 15894 | 15664 | 17921 | 18532 | 18780 | 18479 | 17099 | 19062 | 19546 | 20189 | 18146 | 18753 | 18160 | 20300 | 21305 | 21510 | 21764
2219 | 2219 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 11 | 15618 | 16532 | 14747 | 15810 | 15706 | 17909 | 18425 | 18659 | 18486 | 17190 | 18856 | 19637 | 20142 | 18016 | 18664 | 18329 | 20165 | 21305 | 21462 | 21752
2220 | 2220 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 12 | 15627 | 16444 | 14744 | 15783 | 15745 | 17804 | 18380 | 18522 | 18511 | 17191 | 18797 | 19524 | 20107 | 18070 | 18653 | 18388 | 20211 | 21287 | 21403 | 21835
2221 | 2221 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 13 | 15613 | 16428 | 14683 | 15744 | 15814 | 17751 | 18437 | 18471 | 18529 | 17257 | 18872 | 19446 | 20153 | 17992 | 18568 | 18454 | 20269 | 21329 | 21323 | 21836
2222 | 2222 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 14 | 15781 | 16627 | 14859 | 15740 | 15973 | 17834 | 18685 | 18601 | 18648 | 17408 | 18960 | 19445 | 20357 | 18075 | 18482 | 18598 | 20433 | 21502 | 21329 | 21935
2223 | 2223 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 15 | 15945 | 16781 | 14874 | 15842 | 16191 | 17911 | 18914 | 18715 | 18675 | 17593 | 18966 | 19446 | 20544 | 17998 | 18525 | 18779 | 20518 | 21665 | 21357 | 21897
2224 | 2224 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 16 | 16329 | 17056 | 15160 | 16120 | 16584 | 18409 | 19251 | 18915 | 18705 | 17979 | 19157 | 19983 | 20791 | 18072 | 18624 | 19031 | 20710 | 21856 | 21325 | 21781
2225 | 2225 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 17 | 16610 | 17139 | 15454 | 16506 | 17026 | 18588 | 19456 | 18989 | 18885 | 18326 | 19288 | 20090 | 21005 | 18565 | 19046 | 19500 | 21138 | 22084 | 21501 | 22046
2226 | 2226 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 18 | 16550 | 17063 | 15285 | 16926 | 17054 | 18602 | 19363 | 19103 | 19193 | 18624 | 19338 | 20249 | 21080 | 18890 | 19962 | 19993 | 21546 | 22271 | 22013 | 22647
2227 | 2227 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 19 | 16810 | 17212 | 15308 | 17027 | 17218 | 18897 | 19723 | 19409 | 19672 | 18929 | 19843 | 20944 | 21788 | 19444 | 20730 | 20657 | 21774 | 23209 | 22932 | 23642
2228 | 2228 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 20 | 17236 | 17689 | 15862 | 17331 | 17668 | 19518 | 20383 | 20142 | 20463 | 19500 | 20678 | 22016 | 23033 | 20527 | 21903 | 21773 | 22601 | 24730 | 24425 | 24908
2229 | 2229 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 21 | 16723 | 17332 | 15701 | 17239 | 17405 | 19200 | 20187 | 20079 | 20488 | 19525 | 20707 | 22248 | 23477 | 21293 | 22751 | 22271 | 23241 | 25525 | 25294 | 25732
2230 | 2230 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 22 | 15740 | 16397 | 15099 | 16583 | 16624 | 18371 | 19369 | 19290 | 19846 | 18923 | 19919 | 21762 | 23051 | 21260 | 22641 | 21965 | 22806 | 25316 | 25053 | 25598
2231 | 2231 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 23 | 14589 | 15306 | 14253 | 15812 | 15742 | 17244 | 18272 | 18261 | 18923 | 18118 | 18809 | 20800 | 22161 | 20661 | 22129 | 21300 | 21935 | 24542 | 24311 | 24918
2232 | 2232 | 93 | 4 | 3 | Winter | 4 | 2 | Winter | 24 | 13850 | 14549 | 13617 | 15284 | 15207 | 16508 | 17484 | 17530 | 18169 | 17640 | 17997 | 20146 | 21481 | 20266 | 21758 | 20900 | 21432 | 23917 | 23767 | 24401
2233 | 2233 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 1 | 13484 | 14263 | 13952 | 14944 | 14779 | 16146 | 16694 | 17227 | 16792 | 17141 | 18369 | 19957 | 20805 | 20263 | 20462 | 20329 | 21734 | 23296 | 23070 | 22476
2234 | 2234 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 2 | 13383 | 14134 | 13731 | 14782 | 14672 | 16030 | 16580 | 17166 | 16638 | 17093 | 18143 | 19828 | 20559 | 19999 | 20114 | 20002 | 21371 | 22974 | 22511 | 22157
2235 | 2235 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 3 | 13266 | 14024 | 13571 | 14637 | 14568 | 15917 | 16409 | 17001 | 16405 | 16930 | 18015 | 19588 | 20268 | 19622 | 19772 | 19694 | 21024 | 22588 | 22312 | 21704
2236 | 2236 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 4 | 13274 | 14038 | 13686 | 14648 | 14669 | 15785 | 16252 | 16810 | 16302 | 16836 | 17841 | 19094 | 19714 | 19175 | 19300 | 19302 | 20491 | 21802 | 21850 | 21078
2237 | 2237 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 5 | 13707 | 14521 | 14054 | 14876 | 15202 | 16152 | 16609 | 17156 | 16456 | 17140 | 18117 | 19055 | 19608 | 18967 | 18873 | 19138 | 20237 | 21426 | 21179 | 20649
2238 | 2238 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 6 | 14965 | 15786 | 14902 | 15472 | 16465 | 17287 | 17663 | 18187 | 16963 | 18136 | 19062 | 19725 | 20061 | 19087 | 18760 | 19713 | 20756 | 21616 | 20530 | 20551
2239 | 2239 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 7 | 16352 | 17077 | 15446 | 15733 | 17680 | 18510 | 18797 | 19228 | 17248 | 19159 | 19941 | 20582 | 20678 | 18937 | 18419 | 20358 | 21315 | 22040 | 19896 | 20240
2240 | 2240 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 8 | 16824 | 17607 | 15573 | 15614 | 18074 | 18952 | 19198 | 19663 | 17232 | 19470 | 20122 | 20795 | 20884 | 18699 | 18080 | 20549 | 21305 | 22144 | 20008 | 19915
2241 | 2241 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 9 | 16913 | 17733 | 16197 | 16070 | 18239 | 18987 | 19337 | 19729 | 17724 | 19553 | 19992 | 20646 | 20926 | 19003 | 18360 | 20579 | 21166 | 22131 | 20208 | 20169
2242 | 2242 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 10 | 16940 | 17717 | 16538 | 16372 | 18261 | 18998 | 19325 | 19706 | 18075 | 19633 | 19996 | 20716 | 20935 | 19275 | 18737 | 20702 | 21287 | 22177 | 20029 | 20496
2243 | 2243 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 11 | 16911 | 17546 | 16552 | 16521 | 18110 | 18970 | 19288 | 19551 | 18115 | 19515 | 20054 | 20748 | 20941 | 19263 | 18994 | 20654 | 21467 | 22215 | 20032 | 20528
2244 | 2244 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 12 | 16746 | 17259 | 16393 | 16387 | 17894 | 18782 | 19007 | 19254 | 17913 | 19312 | 19829 | 20567 | 20701 | 19102 | 18905 | 20515 | 21245 | 22006 | 19965 | 20370
2245 | 2245 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 13 | 16594 | 16915 | 16166 | 16267 | 17769 | 18648 | 18765 | 18876 | 17648 | 19195 | 19631 | 20421 | 20423 | 18826 | 18775 | 20401 | 21025 | 21729 | 19700 | 20093
2246 | 2246 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 14 | 16582 | 16767 | 15893 | 16173 | 17611 | 18627 | 18628 | 18682 | 17306 | 19014 | 19478 | 20355 | 20168 | 18473 | 18643 | 20205 | 20860 | 21449 | 19482 | 19711
2247 | 2247 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 15 | 16696 | 16689 | 15847 | 16247 | 17514 | 18712 | 18603 | 18565 | 17209 | 18874 | 19464 | 20394 | 20087 | 18365 | 18677 | 20052 | 20814 | 21327 | 19215 | 19580
2248 | 2248 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 16 | 16939 | 16764 | 16034 | 16577 | 17659 | 18964 | 18727 | 18562 | 17341 | 18981 | 19924 | 20568 | 20032 | 18393 | 18845 | 20037 | 21234 | 21210 | 19131 | 19566
2249 | 2249 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 17 | 17138 | 16889 | 16372 | 16901 | 17709 | 19133 | 18763 | 18581 | 17674 | 19063 | 20173 | 20728 | 20160 | 18782 | 19273 | 20244 | 21561 | 21344 | 19600 | 19959
2250 | 2250 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 18 | 16989 | 17018 | 16757 | 16948 | 17637 | 19061 | 18859 | 18978 | 18369 | 19108 | 20138 | 20819 | 20620 | 19704 | 19787 | 20541 | 21632 | 21899 | 20045 | 20973
2251 | 2251 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 19 | 17293 | 17189 | 16893 | 17153 | 18010 | 19460 | 19192 | 19397 | 18666 | 19616 | 20692 | 21532 | 21389 | 20495 | 20493 | 21464 | 22571 | 22877 | 20845 | 21925
2252 | 2252 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 20 | 17781 | 17808 | 17186 | 17580 | 18576 | 20100 | 19898 | 20260 | 19278 | 20396 | 21734 | 22716 | 22611 | 21628 | 21598 | 22664 | 24070 | 24373 | 22195 | 23267
2253 | 2253 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 21 | 17299 | 17469 | 17050 | 17269 | 18216 | 19832 | 19751 | 20203 | 19493 | 20328 | 21908 | 23034 | 23101 | 22382 | 22022 | 23063 | 24731 | 25212 | 23223 | 24312
2254 | 2254 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 22 | 16311 | 16606 | 16377 | 16478 | 17212 | 18978 | 18922 | 19532 | 19018 | 19488 | 21245 | 22551 | 22669 | 22234 | 21682 | 22497 | 24358 | 24968 | 23341 | 24297
2255 | 2255 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 23 | 15183 | 15568 | 15602 | 15603 | 15998 | 17871 | 17878 | 18532 | 18336 | 18346 | 20251 | 21627 | 21841 | 21702 | 21008 | 21504 | 23531 | 24232 | 22803 | 23835
2256 | 2256 | 94 | 4 | 4 | Winter | 4 | 3 | Winter | 24 | 14347 | 14805 | 15062 | 15064 | 15144 | 17070 | 17122 | 17803 | 17840 | 17513 | 19460 | 20921 | 21231 | 21302 | 20599 | 20754 | 22820 | 23679 | 22453 | 23486
2257 | 2257 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 1 | 13652 | 13552 | 14893 | 14448 | 15250 | 16360 | 16911 | 16415 | 17290 | 17926 | 19934 | 20336 | 21055 | 20208 | 20170 | 21562 | 23527 | 23532 | 22514 | 22116
2258 | 2258 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 2 | 13524 | 13299 | 14699 | 14366 | 15127 | 16205 | 16801 | 16216 | 17185 | 17821 | 19789 | 20110 | 20893 | 19867 | 19846 | 21202 | 23149 | 23294 | 22200 | 21730
2259 | 2259 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 3 | 13392 | 13183 | 14581 | 14291 | 15031 | 16075 | 16688 | 16044 | 16999 | 17700 | 19621 | 19842 | 20573 | 19547 | 19551 | 20864 | 22779 | 22886 | 21748 | 21352
2260 | 2260 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 4 | 13385 | 13289 | 14610 | 14277 | 15103 | 15966 | 16560 | 16007 | 16847 | 17554 | 19400 | 19352 | 20003 | 19111 | 19187 | 20358 | 22212 | 22085 | 21123 | 20768
2261 | 2261 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 5 | 13913 | 13675 | 14866 | 14804 | 15663 | 16382 | 16984 | 16241 | 16930 | 17922 | 19529 | 19340 | 19896 | 18744 | 19075 | 20146 | 21861 | 21698 | 20723 | 20230
2262 | 2262 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 6 | 15170 | 14529 | 15494 | 15993 | 16946 | 17490 | 18101 | 16859 | 17250 | 18945 | 20248 | 19893 | 20412 | 18673 | 19675 | 20700 | 22179 | 21935 | 20618 | 19987
2263 | 2263 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 7 | 16360 | 15054 | 15752 | 17226 | 18261 | 18605 | 19153 | 17177 | 17252 | 19861 | 20994 | 20555 | 21075 | 18342 | 20321 | 21261 | 22557 | 22386 | 20290 | 19531
2264 | 2264 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 8 | 16502 | 14909 | 15375 | 17399 | 18488 | 18726 | 19328 | 16928 | 16787 | 19832 | 21070 | 20524 | 21025 | 17742 | 20249 | 21008 | 22393 | 22219 | 19690 | 18860
2265 | 2265 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 9 | 16287 | 15161 | 15467 | 17216 | 18176 | 18478 | 19018 | 17045 | 16825 | 19402 | 20705 | 20208 | 20621 | 17661 | 19919 | 20505 | 21936 | 21770 | 19577 | 18732
2266 | 2266 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 10 | 16120 | 15277 | 15524 | 17063 | 17896 | 18201 | 18721 | 17123 | 16914 | 19170 | 20453 | 19957 | 20424 | 17785 | 19791 | 20372 | 21770 | 21618 | 19654 | 18907
2267 | 2267 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 11 | 15972 | 15186 | 15565 | 16916 | 17767 | 18040 | 18428 | 17012 | 16985 | 19098 | 20278 | 19844 | 20233 | 17930 | 19634 | 20425 | 21698 | 21490 | 19580 | 19097
2268 | 2268 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 12 | 15922 | 15218 | 15626 | 16887 | 17687 | 17956 | 18333 | 17033 | 17012 | 19045 | 20165 | 19775 | 20119 | 18005 | 19659 | 20380 | 21608 | 21379 | 19588 | 19185
2269 | 2269 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 13 | 16013 | 15277 | 15790 | 16952 | 17811 | 17996 | 18233 | 17062 | 17181 | 19132 | 20113 | 19795 | 20020 | 18163 | 19824 | 20455 | 21561 | 21282 | 19583 | 19335
2270 | 2270 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 14 | 16218 | 15290 | 15949 | 17147 | 18017 | 18104 | 18281 | 16970 | 17336 | 19233 | 20117 | 19825 | 20047 | 18304 | 19915 | 20573 | 21599 | 21264 | 19472 | 19460
2271 | 2271 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 15 | 16413 | 15442 | 16230 | 17259 | 18237 | 18303 | 18384 | 17089 | 17577 | 19418 | 20250 | 19956 | 20074 | 18546 | 19969 | 20729 | 21704 | 21263 | 19546 | 19685
2272 | 2272 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 16 | 16785 | 15778 | 16711 | 17560 | 18859 | 18584 | 18540 | 17384 | 18056 | 20060 | 20540 | 20105 | 20139 | 18894 | 20132 | 21337 | 21905 | 21234 | 19700 | 20003
2273 | 2273 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 17 | 16888 | 16202 | 17125 | 17800 | 19141 | 18753 | 18689 | 17848 | 18410 | 20353 | 20728 | 20289 | 20271 | 19378 | 20398 | 21717 | 22066 | 21384 | 20156 | 20500
2274 | 2274 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 18 | 16797 | 16510 | 17057 | 17792 | 18968 | 18770 | 18978 | 18404 | 18668 | 20242 | 20750 | 20646 | 20843 | 19847 | 20639 | 21734 | 22272 | 22076 | 21129 | 21030
2275 | 2275 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 19 | 16910 | 16541 | 17145 | 18035 | 19054 | 18988 | 19267 | 18554 | 18902 | 20593 | 21315 | 21232 | 21542 | 20407 | 21422 | 22537 | 23317 | 23015 | 21987 | 21719
2276 | 2276 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 20 | 17364 | 16802 | 17557 | 18683 | 19670 | 19685 | 20106 | 19128 | 19420 | 21532 | 22335 | 22351 | 22874 | 21435 | 22569 | 23990 | 24816 | 24647 | 23314 | 22924
2277 | 2277 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 21 | 16970 | 16645 | 17225 | 18218 | 19373 | 19486 | 19978 | 19260 | 19351 | 21599 | 22618 | 22737 | 23391 | 21813 | 22921 | 24606 | 25637 | 25520 | 24352 | 23520
2278 | 2278 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 22 | 16005 | 15917 | 16383 | 17184 | 18389 | 18598 | 19230 | 18694 | 18684 | 20837 | 22112 | 22215 | 23050 | 21413 | 22297 | 24168 | 25450 | 25378 | 24308 | 23224
2279 | 2279 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 23 | 14903 | 15132 | 15489 | 16078 | 17231 | 17542 | 18204 | 17963 | 17845 | 19779 | 21175 | 21338 | 22241 | 20717 | 21284 | 23292 | 24660 | 24680 | 23841 | 22580
2280 | 2280 | 95 | 4 | 5 | Winter | 4 | 4 | Winter | 24 | 14148 | 14611 | 14957 | 15318 | 16391 | 16800 | 17480 | 17467 | 17354 | 19002 | 20451 | 20721 | 21634 | 20315 | 20550 | 22595 | 24009 | 24134 | 23514 | 22204
2281 | 2281 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 1 | 12887 | 14139 | 13840 | 14796 | 16196 | 15534 | 15767 | 16656 | 16420 | 19101 | 19572 | 20184 | 19764 | 19241 | 20948 | 22916 | 23247 | 22137 | 21789 | 21259
2282 | 2282 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 2 | 12666 | 13953 | 13778 | 14669 | 16047 | 15385 | 15595 | 16548 | 16430 | 19031 | 19352 | 20059 | 19522 | 19026 | 20613 | 22552 | 22749 | 21821 | 21418 | 21143
2283 | 2283 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 3 | 12486 | 13820 | 13735 | 14575 | 15960 | 15149 | 15387 | 16371 | 16330 | 18842 | 19087 | 19762 | 19154 | 19104 | 20279 | 22191 | 22318 | 21367 | 21035 | 20890
2284 | 2284 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 4 | 12453 | 13838 | 13846 | 14663 | 16049 | 14973 | 15378 | 16263 | 16188 | 18671 | 18776 | 19258 | 18767 | 19143 | 19808 | 21664 | 21668 | 20765 | 20452 | 20323
2285 | 2285 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 5 | 12887 | 14096 | 14270 | 15238 | 16506 | 15364 | 15647 | 16393 | 16543 | 18874 | 18870 | 19225 | 18634 | 19198 | 19644 | 21345 | 21230 | 20376 | 19924 | 20072
2286 | 2286 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 6 | 14004 | 14739 | 15124 | 16562 | 17631 | 16358 | 16332 | 16793 | 17506 | 19668 | 19515 | 19843 | 18823 | 19467 | 20259 | 21708 | 21415 | 20296 | 19687 | 20498
2287 | 2287 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 7 | 15263 | 15041 | 15986 | 17905 | 18724 | 17479 | 16752 | 16856 | 18586 | 20531 | 20412 | 20577 | 18700 | 19781 | 20867 | 22107 | 21959 | 19987 | 19240 | 21217
2288 | 2288 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 8 | 15803 | 14844 | 16575 | 18323 | 19178 | 18016 | 16714 | 16598 | 18884 | 20825 | 20684 | 20742 | 18376 | 20160 | 20802 | 22134 | 22064 | 19572 | 18743 | 21346
2289 | 2289 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 9 | 16055 | 15258 | 17107 | 18312 | 19283 | 18288 | 17173 | 16963 | 18935 | 20807 | 20495 | 20655 | 18615 | 20392 | 20599 | 21992 | 21763 | 19755 | 18910 | 21333
2290 | 2290 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 10 | 16019 | 15436 | 17160 | 18090 | 19052 | 18237 | 17339 | 17120 | 18865 | 20651 | 20110 | 20510 | 18701 | 20095 | 20526 | 21888 | 21438 | 19890 | 19152 | 21410
2291 | 2291 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 11 | 15965 | 15472 | 17134 | 17974 | 18816 | 18216 | 17254 | 17192 | 18732 | 20495 | 19858 | 20313 | 18573 | 19944 | 20584 | 21817 | 21267 | 19814 | 19336 | 21371
2292 | 2292 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 12 | 15667 | 15196 | 16792 | 17550 | 18334 | 17862 | 16883 | 16871 | 18342 | 19981 | 19483 | 19846 | 18222 | 19656 | 20187 | 21378 | 20960 | 19464 | 19075 | 21004
2293 | 2293 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 13 | 15426 | 15001 | 16578 | 17288 | 17910 | 17592 | 16536 | 16648 | 17994 | 19554 | 19200 | 19357 | 17847 | 19425 | 19881 | 20939 | 20658 | 19082 | 18840 | 20635
2294 | 2294 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 14 | 15347 | 14890 | 16543 | 17229 | 17712 | 17499 | 16221 | 16533 | 17856 | 19340 | 19039 | 19118 | 17505 | 19313 | 19733 | 20705 | 20471 | 18703 | 18694 | 20423
2295 | 2295 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 15 | 15320 | 14976 | 16565 | 17279 | 17713 | 17431 | 16158 | 16600 | 17759 | 19286 | 18951 | 18978 | 17432 | 19278 | 19711 | 20637 | 20358 | 18595 | 18734 | 20250
2296 | 2296 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 16 | 15597 | 15502 | 17005 | 17893 | 18119 | 17660 | 16522 | 17108 | 18035 | 19658 | 19196 | 19083 | 17668 | 19599 | 20363 | 20856 | 20435 | 18781 | 19084 | 20408
2297 | 2297 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 17 | 15964 | 16055 | 17423 | 18372 | 18482 | 17919 | 17089 | 17648 | 18543 | 19936 | 19608 | 19399 | 18286 | 20195 | 20913 | 21203 | 20962 | 19412 | 19749 | 20988
2298 | 2298 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 18 | 16182 | 16255 | 17672 | 18494 | 18657 | 18395 | 17905 | 18144 | 18952 | 20243 | 20158 | 20209 | 19433 | 20858 | 21200 | 21685 | 21702 | 20667 | 20564 | 21674
2299 | 2299 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 19 | 16485 | 16499 | 17592 | 18748 | 19151 | 18883 | 18194 | 18520 | 19524 | 20891 | 20677 | 21030 | 20247 | 21158 | 22157 | 22903 | 22601 | 21709 | 21452 | 22691
2300 | 2300 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 20 | 16937 | 16885 | 18010 | 19347 | 19719 | 19489 | 18686 | 18994 | 20384 | 21775 | 21640 | 22290 | 21317 | 21894 | 23570 | 24389 | 24135 | 23046 | 22670 | 24069
2301 | 2301 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 21 | 16594 | 16527 | 17788 | 19014 | 19483 | 19290 | 18749 | 18863 | 20148 | 21958 | 22049 | 22706 | 21996 | 22375 | 24128 | 25162 | 25087 | 24069 | 23264 | 24479
2302 | 2302 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 22 | 15705 | 15680 | 16839 | 18002 | 18648 | 18492 | 18142 | 18146 | 19225 | 21371 | 21411 | 22290 | 21766 | 21840 | 23654 | 24935 | 24763 | 24022 | 22971 | 23909
2303 | 2303 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 23 | 14710 | 14790 | 15782 | 16861 | 17572 | 17507 | 17400 | 17302 | 18173 | 20401 | 20331 | 21489 | 21210 | 20946 | 22776 | 24147 | 23856 | 23562 | 22342 | 23069
2304 | 2304 | 96 | 4 | 6 | Winter | 4 | 5 | Winter | 24 | 13905 | 14233 | 15087 | 16010 | 16763 | 16688 | 16864 | 16785 | 17399 | 19632 | 19488 | 20825 | 20804 | 20410 | 22048 | 23470 | 23118 | 23208 | 21944 | 22380
2305 | 2305 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 1 | 12891 | 13880 | 14659 | 16073 | 16026 | 15445 | 16432 | 16382 | 17299 | 19069 | 18865 | 19252 | 19730 | 20587 | 22618 | 22969 | 23241 | 21793 | 21097 | 22684
2306 | 2306 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 2 | 12692 | 13758 | 14532 | 15933 | 15825 | 15264 | 16314 | 16337 | 17251 | 18883 | 18607 | 19039 | 19418 | 20276 | 22282 | 22485 | 23028 | 21421 | 20848 | 22323
2307 | 2307 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 3 | 12570 | 13661 | 14442 | 15821 | 15688 | 15061 | 16141 | 16193 | 17095 | 18652 | 18254 | 18696 | 19106 | 19967 | 21934 | 22060 | 22608 | 21034 | 20873 | 21934
2308 | 2308 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 4 | 12678 | 13812 | 14571 | 15932 | 15734 | 15111 | 16096 | 16217 | 17006 | 18441 | 17825 | 18385 | 18722 | 19566 | 21459 | 21459 | 21837 | 20487 | 20791 | 21362
2309 | 2309 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 5 | 13089 | 14413 | 15185 | 16435 | 16213 | 15450 | 16303 | 16677 | 17447 | 18669 | 17566 | 18356 | 18428 | 19482 | 21218 | 21093 | 21501 | 19981 | 20704 | 21075
2310 | 2310 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 6 | 13933 | 15770 | 16503 | 17573 | 17330 | 16169 | 16753 | 17802 | 18523 | 19408 | 17415 | 18619 | 18401 | 20132 | 21612 | 21299 | 21755 | 19736 | 20793 | 21509
2311 | 2311 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 7 | 14497 | 17054 | 17886 | 18719 | 18605 | 16610 | 16853 | 18908 | 19564 | 20359 | 17125 | 18598 | 18132 | 20790 | 22071 | 21896 | 22234 | 19308 | 21006 | 22004
2312 | 2312 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 8 | 14646 | 17477 | 18435 | 19294 | 19075 | 16676 | 16708 | 19252 | 19866 | 20752 | 17343 | 18420 | 17832 | 20858 | 22231 | 22125 | 22367 | 18924 | 21435 | 21962
2313 | 2313 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 9 | 15220 | 17589 | 18432 | 19420 | 18939 | 17116 | 17058 | 19256 | 19795 | 20525 | 17627 | 18698 | 18071 | 20683 | 22116 | 21850 | 22231 | 19112 | 21632 | 21724
2314 | 2314 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 10 | 15734 | 17734 | 18468 | 19452 | 18835 | 17492 | 17415 | 19346 | 19956 | 20304 | 17838 | 19081 | 18557 | 20908 | 22312 | 21828 | 22436 | 19653 | 21693 | 22009
2315 | 2315 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 11 | 15865 | 17684 | 18503 | 19404 | 18731 | 17541 | 17614 | 19244 | 20096 | 20139 | 18003 | 19151 | 18894 | 21142 | 22436 | 21858 | 22504 | 20033 | 21774 | 22296
2316 | 2316 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 12 | 15875 | 17663 | 18440 | 19245 | 18694 | 17523 | 17640 | 19207 | 19986 | 20120 | 18033 | 19140 | 18961 | 21096 | 22323 | 21894 | 22385 | 20106 | 21837 | 22259
2317 | 2317 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 13 | 15723 | 17585 | 18351 | 18998 | 18599 | 17344 | 17583 | 19164 | 19868 | 20006 | 17841 | 18940 | 18904 | 20959 | 22053 | 21763 | 22063 | 20044 | 21771 | 22113
2318 | 2318 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 14 | 15348 | 17295 | 18160 | 18687 | 18358 | 16903 | 17341 | 18859 | 19604 | 19731 | 17544 | 18450 | 18631 | 20667 | 21672 | 21427 | 21637 | 19748 | 21489 | 21791
2319 | 2319 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 15 | 15276 | 17200 | 18190 | 18657 | 18299 | 16832 | 17398 | 18744 | 19565 | 19642 | 17341 | 18338 | 18651 | 20612 | 21567 | 21269 | 21420 | 19747 | 21397 | 21712
2320 | 2320 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 16 | 15514 | 17409 | 18585 | 18934 | 18525 | 17041 | 17747 | 18902 | 20137 | 19741 | 17434 | 18455 | 18905 | 21134 | 21662 | 21217 | 21294 | 19953 | 21542 | 22196
2321 | 2321 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 17 | 15763 | 17403 | 18788 | 18976 | 18652 | 17357 | 18041 | 18977 | 20205 | 19920 | 17677 | 18753 | 19245 | 21364 | 21686 | 21419 | 21309 | 20293 | 21848 | 22447
2322 | 2322 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 18 | 16025 | 17082 | 18576 | 18840 | 18562 | 17827 | 18172 | 18869 | 20058 | 20114 | 17833 | 19516 | 19654 | 21300 | 21816 | 21813 | 21946 | 20779 | 22227 | 22450
2323 | 2323 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 19 | 16054 | 17351 | 18673 | 19162 | 18618 | 17964 | 18406 | 19274 | 20362 | 20457 | 18346 | 20095 | 20200 | 22031 | 22809 | 22521 | 22886 | 21487 | 22477 | 23347
2324 | 2324 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 20 | 16274 | 17851 | 19253 | 19671 | 19232 | 18450 | 18883 | 19977 | 21177 | 21359 | 19476 | 21061 | 21180 | 23376 | 24225 | 24002 | 24502 | 22684 | 23364 | 24901
2325 | 2325 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 21 | 16057 | 17371 | 18855 | 19347 | 19098 | 18418 | 18658 | 19717 | 21112 | 21610 | 19884 | 21601 | 21450 | 23811 | 24882 | 24859 | 25309 | 23228 | 24015 | 25602
2326 | 2326 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 22 | 15316 | 16270 | 17815 | 18478 | 18161 | 17781 | 17898 | 18750 | 20284 | 20895 | 19632 | 21306 | 21006 | 23300 | 24619 | 24509 | 25153 | 22945 | 23578 | 25226
2327 | 2327 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 23 | 14538 | 15047 | 16654 | 17391 | 16939 | 17021 | 17033 | 17561 | 19192 | 19762 | 18926 | 20703 | 20299 | 22390 | 23788 | 23572 | 24466 | 22306 | 22716 | 24401
2328 | 2328 | 97 | 4 | 7 | Winter | 4 | 6 | Winter | 24 | 13991 | 14201 | 15812 | 16586 | 15989 | 16489 | 16515 | 16703 | 18370 | 18906 | 18357 | 20268 | 19850 | 21651 | 23109 | 22818 | 23878 | 21910 | 22215 | 23707
2329 | 2329 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 1 | 13564 | 13896 | 15544 | 15540 | 15063 | 15805 | 15788 | 16614 | 18440 | 18025 | 18562 | 19002 | 19080 | 21902 | 22316 | 22207 | 22080 | 21090 | 22325 | 24106
2330 | 2330 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 2 | 13376 | 13690 | 15317 | 15228 | 14849 | 15548 | 15584 | 16409 | 18367 | 17682 | 18182 | 18694 | 18781 | 21564 | 21836 | 21659 | 21574 | 20729 | 21959 | 23724
2331 | 2331 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 3 | 13235 | 13601 | 15201 | 15086 | 14681 | 15364 | 15438 | 16251 | 18190 | 17413 | 17838 | 18398 | 18506 | 21238 | 21434 | 21463 | 21085 | 20383 | 21584 | 23321
2332 | 2332 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 4 | 13265 | 13724 | 15312 | 15156 | 14724 | 15329 | 15480 | 16215 | 18096 | 17183 | 17503 | 18065 | 18232 | 20799 | 20860 | 21088 | 20417 | 19933 | 21005 | 22697
2333 | 2333 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 5 | 13572 | 14306 | 15767 | 15610 | 15204 | 15475 | 15879 | 16627 | 18422 | 17232 | 17375 | 17844 | 18248 | 20624 | 20549 | 20537 | 19992 | 19743 | 20734 | 22303
2334 | 2334 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 6 | 14228 | 15651 | 16916 | 16780 | 16219 | 15965 | 17066 | 17776 | 19303 | 17861 | 17482 | 17912 | 18954 | 21095 | 20830 | 19972 | 19703 | 20254 | 21194 | 22547
2335 | 2335 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 7 | 14559 | 17080 | 18085 | 18069 | 17344 | 16104 | 18237 | 18869 | 20217 | 18720 | 17441 | 17719 | 19691 | 21606 | 21472 | 19400 | 19362 | 20855 | 21704 | 22868
2336 | 2336 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 8 | 14262 | 17462 | 18476 | 18325 | 17667 | 15780 | 18417 | 19013 | 20427 | 18939 | 17271 | 17238 | 19726 | 21590 | 21513 | 19331 | 19018 | 20809 | 21462 | 22719
2337 | 2337 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 9 | 14070 | 16893 | 18043 | 17576 | 17194 | 15577 | 17884 | 18365 | 19778 | 18414 | 17048 | 16883 | 19120 | 20882 | 20637 | 18879 | 18643 | 20142 | 20615 | 21933
2338 | 2338 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 10 | 14085 | 16529 | 17694 | 17030 | 16812 | 15563 | 17619 | 18067 | 19363 | 18104 | 17032 | 16914 | 18914 | 20616 | 20153 | 18377 | 18632 | 19965 | 20439 | 21718
2339 | 2339 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 11 | 14181 | 16487 | 17596 | 16835 | 16602 | 15734 | 17489 | 18124 | 19210 | 18010 | 17043 | 17136 | 18839 | 20632 | 20064 | 18365 | 18689 | 19930 | 20620 | 21770
2340 | 2340 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 12 | 14200 | 16386 | 17401 | 16774 | 16436 | 15722 | 17421 | 17996 | 18986 | 17898 | 16934 | 17142 | 18784 | 20460 | 20043 | 18373 | 18585 | 19895 | 20512 | 21615
2341 | 2341 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 13 | 14167 | 16305 | 17145 | 16670 | 16237 | 15651 | 17361 | 17866 | 18710 | 17706 | 16689 | 17068 | 18725 | 20180 | 19896 | 18135 | 18321 | 19838 | 20363 | 21329
2342 | 2342 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 14 | 13942 | 16137 | 16869 | 16480 | 16014 | 15444 | 17095 | 17658 | 18410 | 17441 | 16369 | 16832 | 18424 | 19837 | 19599 | 17800 | 17968 | 19511 | 20072 | 20963
2343 | 2343 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 15 | 14015 | 16193 | 16869 | 16472 | 15981 | 15528 | 17001 | 17678 | 18377 | 17363 | 16198 | 16887 | 18286 | 19765 | 19475 | 17565 | 17760 | 19359 | 20026 | 20874
2344 | 2344 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 16 | 14489 | 16654 | 17245 | 16778 | 16218 | 15971 | 17257 | 18260 | 18694 | 17481 | 16419 | 17253 | 18460 | 19975 | 19546 | 17667 | 17911 | 19489 | 20609 | 21045
2345 | 2345 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 17 | 15213 | 17314 | 17752 | 17424 | 16839 | 16733 | 17797 | 18872 | 19204 | 18174 | 17142 | 18049 | 19041 | 20450 | 20210 | 18517 | 18664 | 20075 | 21311 | 21547
2346 | 2346 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 18 | 15549 | 17593 | 18096 | 17787 | 17361 | 17324 | 18125 | 19194 | 19659 | 18861 | 18144 | 18899 | 19698 | 21055 | 21077 | 19343 | 19799 | 20830 | 21810 | 22241
2347 | 2347 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 19 | 15889 | 17939 | 18678 | 18139 | 17481 | 17832 | 18794 | 19799 | 20417 | 19277 | 18647 | 19657 | 20695 | 22268 | 22020 | 20273 | 20644 | 21988 | 22985 | 23643
2348 | 2348 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 20 | 16286 | 18508 | 19169 | 18779 | 18047 | 18318 | 19479 | 20641 | 21287 | 20191 | 19734 | 20585 | 21752 | 23628 | 23465 | 21549 | 22162 | 23256 | 24551 | 25235
2349 | 2349 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 21 | 15912 | 18133 | 18861 | 18651 | 17926 | 18098 | 19226 | 20540 | 21362 | 20467 | 20205 | 20828 | 21991 | 24256 | 24298 | 22489 | 23157 | 23756 | 25291 | 26166
2350 | 2350 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 22 | 15036 | 17050 | 17949 | 17670 | 17031 | 17301 | 18207 | 19632 | 20682 | 19811 | 19762 | 20311 | 21272 | 23926 | 23891 | 22521 | 23024 | 23183 | 24890 | 25989
2351 | 2351 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 23 | 14134 | 15899 | 16862 | 16454 | 16035 | 16439 | 17006 | 18520 | 19684 | 18925 | 18992 | 19578 | 20217 | 23087 | 22937 | 21969 | 22421 | 22196 | 24066 | 25221
2352 | 2352 | 98 | 4 | 8 | Winter | 4 | 7 | Winter | 24 | 13579 | 15057 | 16058 | 15519 | 15218 | 15923 | 16142 | 17691 | 18921 | 18159 | 18392 | 19124 | 19455 | 22390 | 22184 | 21591 | 21914 | 21470 | 23373 | 24577
2353 | 2353 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 1 | 12803 | 15037 | 15294 | 14842 | 15134 | 15232 | 16260 | 17969 | 18248 | 17995 | 17454 | 18624 | 19969 | 21835 | 21610 | 21750 | 20318 | 22229 | 24018 | 24108
2354 | 2354 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 2 | 12684 | 14817 | 15011 | 14544 | 14827 | 15122 | 16071 | 17769 | 17919 | 17667 | 17168 | 18361 | 19683 | 21384 | 21133 | 21272 | 19809 | 21877 | 23651 | 23602
2355 | 2355 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 3 | 12571 | 14718 | 14887 | 14386 | 14600 | 14990 | 15930 | 17607 | 17701 | 17357 | 16924 | 18111 | 19389 | 21010 | 20719 | 20805 | 19538 | 21507 | 23255 | 23150
2356 | 2356 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 4 | 12595 | 14840 | 14992 | 14463 | 14591 | 14945 | 15952 | 17582 | 17552 | 17109 | 16619 | 17901 | 19038 | 20501 | 20152 | 20183 | 19022 | 20952 | 22654 | 22442
2357 | 2357 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 5 | 13104 | 15332 | 15473 | 14897 | 14819 | 15355 | 16428 | 17857 | 17736 | 17078 | 16448 | 17983 | 19023 | 20257 | 19904 | 19809 | 18699 | 20701 | 22269 | 21965
2358 | 2358 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 6 | 14384 | 16498 | 16693 | 15954 | 15341 | 16484 | 17658 | 18807 | 18557 | 17294 | 16408 | 18772 | 19751 | 20614 | 20083 | 19573 | 18390 | 21187 | 22540 | 22095
2359 | 2359 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 7 | 15693 | 17678 | 17990 | 17091 | 15722 | 17708 | 18797 | 19759 | 19570 | 17300 | 16213 | 19549 | 20473 | 21275 | 20569 | 19241 | 17932 | 21686 | 22844 | 22609
2360 | 2360 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 8 | 15930 | 18072 | 18224 | 17403 | 15759 | 17936 | 18956 | 19993 | 19795 | 17134 | 16025 | 19589 | 20355 | 21314 | 20614 | 18888 | 17591 | 21455 | 22693 | 22589
2361 | 2361 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 9 | 15649 | 17811 | 17668 | 17154 | 15847 | 17650 | 18511 | 19614 | 19230 | 17115 | 16033 | 19181 | 19780 | 20628 | 20224 | 18691 | 17423 | 20800 | 22089 | 21866
2362 | 2362 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 10 | 15644 | 17682 | 17342 | 17043 | 15973 | 17647 | 18400 | 19502 | 18874 | 17293 | 16373 | 19158 | 19737 | 20341 | 20200 | 18862 | 17754 | 20821 | 22077 | 21615
2363 | 2363 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 11 | 15815 | 17770 | 17333 | 17073 | 16098 | 17820 | 18614 | 19619 | 18873 | 17478 | 16682 | 19254 | 20029 | 20419 | 20330 | 19096 | 18114 | 21172 | 22304 | 21737
2364 | 2364 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 12 | 15875 | 17696 | 17380 | 17041 | 16075 | 17813 | 18596 | 19531 | 18939 | 17468 | 16848 | 19319 | 20027 | 20507 | 20297 | 19104 | 18317 | 21176 | 22253 | 21851
2365 | 2365 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 13 | 15702 | 17461 | 17285 | 16846 | 15834 | 17635 | 18468 | 19260 | 18812 | 17223 | 16840 | 19254 | 19871 | 20363 | 20077 | 18841 | 18293 | 21015 | 21963 | 21704
2366 | 2366 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 14 | 15539 | 17162 | 17102 | 16626 | 15561 | 17459 | 18267 | 18959 | 18586 | 16905 | 16713 | 18957 | 19623 | 20075 | 19770 | 18488 | 18144 | 20728 | 21605 | 21386
2367 | 2367 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 15 | 15477 | 17134 | 17094 | 16590 | 15436 | 17365 | 18285 | 18921 | 18527 | 16737 | 16767 | 18829 | 19606 | 19955 | 19653 | 18291 | 18191 | 20680 | 21512 | 21235
2368 | 2368 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 16 | 15825 | 17546 | 17461 | 16877 | 15785 | 17672 | 18892 | 19282 | 18762 | 17023 | 17161 | 19064 | 20264 | 20090 | 19721 | 18491 | 18524 | 21299 | 21723 | 21304
2369 | 2369 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 17 | 16147 | 17884 | 17907 | 17303 | 16340 | 18112 | 19309 | 19601 | 19212 | 17549 | 17759 | 19444 | 20762 | 20558 | 20110 | 19058 | 19057 | 21816 | 22032 | 21764
2370 | 2370 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 18 | 16147 | 17891 | 17886 | 17459 | 16758 | 18266 | 19299 | 19706 | 19525 | 18193 | 18295 | 19738 | 20847 | 21093 | 20749 | 19861 | 19736 | 21996 | 22411 | 22384
2371 | 2371 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 19 | 16535 | 18295 | 18070 | 17430 | 16748 | 18774 | 19727 | 20287 | 19966 | 18481 | 18641 | 20546 | 21671 | 21846 | 21400 | 20542 | 20413 | 23026 | 23679 | 23312
2372 | 2372 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 20 | 17127 | 18754 | 18658 | 17947 | 17410 | 19512 | 20498 | 21081 | 20805 | 19448 | 19618 | 21526 | 22943 | 23213 | 22713 | 22010 | 21745 | 24569 | 25251 | 24893
2373 | 2373 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 21 | 16557 | 18354 | 18450 | 17735 | 17334 | 19075 | 20283 | 21013 | 20946 | 19756 | 19865 | 21632 | 23297 | 23911 | 23477 | 22902 | 22414 | 25248 | 26121 | 25893
2374 | 2374 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 22 | 15503 | 17445 | 17468 | 16840 | 16628 | 18057 | 19355 | 20309 | 20171 | 19261 | 19355 | 20889 | 22739 | 23495 | 23189 | 22768 | 22163 | 24867 | 25966 | 25604
2375 | 2375 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 23 | 14364 | 16347 | 16232 | 15828 | 15729 | 16957 | 18218 | 19268 | 19006 | 18449 | 18600 | 19809 | 21796 | 22505 | 22473 | 22140 | 21531 | 24053 | 25186 | 24699
2376 | 2376 | 99 | 4 | 9 | Winter | 4 | 8 | Winter | 24 | 13535 | 15521 | 15279 | 14984 | 15035 | 16147 | 17356 | 18457 | 18110 | 17809 | 18052 | 19000 | 21023 | 21716 | 21796 | 21590 | 21055 | 23323 | 24511 | 23947
2377 | 2377 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 1 | 13277 | 14577 | 15070 | 14763 | 14434 | 15696 | 17372 | 17606 | 17330 | 16799 | 17386 | 19267 | 21326 | 21600 | 21202 | 19873 | 20864 | 23751 | 23847 | 23227
2378 | 2378 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 2 | 13074 | 14288 | 14877 | 14442 | 14152 | 15483 | 17159 | 17274 | 17002 | 16523 | 17200 | 18982 | 21020 | 21415 | 20736 | 19363 | 20508 | 23365 | 23327 | 22694
2379 | 2379 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 3 | 13023 | 14201 | 14762 | 14244 | 14019 | 15374 | 17026 | 17099 | 16789 | 16325 | 17051 | 18737 | 20729 | 21069 | 20298 | 19122 | 20187 | 22978 | 22896 | 22253
2380 | 2380 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 4 | 13145 | 14302 | 14750 | 14248 | 13956 | 15417 | 17036 | 17006 | 16624 | 16070 | 16871 | 18437 | 20341 | 20425 | 19706 | 18624 | 19746 | 22380 | 22186 | 21528
2381 | 2381 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 5 | 13739 | 14822 | 15261 | 14531 | 14106 | 15953 | 17391 | 17297 | 16773 | 15987 | 16903 | 18518 | 20246 | 20276 | 19391 | 18356 | 19586 | 22037 | 21741 | 21136
2382 | 2382 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 6 | 15106 | 16052 | 16505 | 15084 | 14437 | 17214 | 18390 | 18208 | 17515 | 16000 | 17268 | 19321 | 20812 | 20697 | 19182 | 18068 | 20133 | 22298 | 21856 | 21128
2383 | 2383 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 7 | 16523 | 17368 | 17689 | 15490 | 14538 | 18418 | 19413 | 19293 | 18417 | 15878 | 17717 | 20102 | 21357 | 21292 | 18898 | 17621 | 20722 | 22623 | 22377 | 21514
2384 | 2384 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 8 | 16919 | 17630 | 17952 | 15554 | 14523 | 18641 | 19718 | 19569 | 18661 | 15754 | 18103 | 20057 | 21377 | 21289 | 18596 | 17315 | 20687 | 22529 | 22388 | 21544
2385 | 2385 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 9 | 16475 | 17019 | 17523 | 15582 | 14613 | 18149 | 19305 | 18959 | 18276 | 15725 | 18084 | 19439 | 20814 | 20694 | 18362 | 17087 | 20152 | 21883 | 21607 | 21064
2386 | 2386 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 10 | 16243 | 16651 | 17314 | 15641 | 14821 | 17944 | 19103 | 18526 | 18086 | 15983 | 18192 | 19316 | 20670 | 20566 | 18451 | 17342 | 20097 | 21784 | 21278 | 20987
2387 | 2387 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 11 | 16121 | 16386 | 17082 | 15530 | 14823 | 17891 | 18969 | 18283 | 17913 | 16039 | 18280 | 19361 | 20613 | 20429 | 18433 | 17463 | 19991 | 21773 | 21154 | 20910
2388 | 2388 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 12 | 16093 | 16397 | 16982 | 15472 | 14924 | 17834 | 18837 | 18301 | 17866 | 16166 | 18339 | 19308 | 20499 | 20313 | 18397 | 17627 | 20016 | 21679 | 21217 | 20861
2389 | 2389 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 13 | 16073 | 16370 | 16705 | 15286 | 14965 | 17755 | 18615 | 18229 | 17724 | 16206 | 18323 | 19208 | 20269 | 20016 | 18184 | 17658 | 20011 | 21437 | 21123 | 20703
2390 | 2390 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 14 | 15975 | 16271 | 16517 | 15081 | 14932 | 17642 | 18392 | 18077 | 17536 | 16160 | 18216 | 19041 | 19994 | 19713 | 17909 | 17580 | 19753 | 21152 | 20882 | 20459
2391 | 2391 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 15 | 16077 | 16311 | 16496 | 14994 | 15055 | 17704 | 18402 | 18058 | 17500 | 16258 | 18223 | 19063 | 19969 | 19576 | 17757 | 17664 | 19642 | 21095 | 20774 | 20360
2392 | 2392 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 16 | 16356 | 16443 | 16521 | 15135 | 15289 | 18087 | 18547 | 18104 | 17467 | 16438 | 18336 | 19499 | 20009 | 19415 | 17742 | 17784 | 19595 | 21082 | 20620 | 20154
2393 | 2393 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 17 | 16893 | 16978 | 16871 | 15758 | 15924 | 18577 | 18936 | 18623 | 18031 | 17102 | 18904 | 20067 | 20364 | 19760 | 18384 | 18387 | 20066 | 21461 | 21160 | 20621
2394 | 2394 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 18 | 17073 | 17129 | 17364 | 16348 | 16431 | 18769 | 19227 | 19080 | 18573 | 17805 | 19550 | 20345 | 20827 | 20730 | 19386 | 19280 | 20693 | 22031 | 21982 | 21528
2395 | 2395 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 19 | 17378 | 17388 | 17840 | 16415 | 16683 | 19274 | 19873 | 19562 | 18893 | 18190 | 19894 | 21208 | 21960 | 21773 | 20132 | 20033 | 21822 | 23381 | 23006 | 22411
2396 | 2396 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 20 | 17939 | 17987 | 18588 | 17082 | 17321 | 20030 | 20644 | 20357 | 19740 | 19121 | 20719 | 22421 | 23266 | 23246 | 21580 | 21370 | 23114 | 24987 | 24625 | 23912
2397 | 2397 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 21 | 17495 | 17729 | 18244 | 16961 | 17168 | 19755 | 20490 | 20402 | 19861 | 19260 | 20916 | 22682 | 23757 | 23843 | 22384 | 21998 | 23549 | 25824 | 25604 | 24887
2398 | 2398 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 22 | 16405 | 16692 | 17373 | 16209 | 16399 | 18780 | 19711 | 19547 | 19140 | 18672 | 20223 | 22050 | 23380 | 23561 | 22193 | 21709 | 22973 | 25639 | 25294 | 24673
2399 | 2399 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 23 | 15252 | 15478 | 16342 | 15327 | 15543 | 17638 | 18664 | 18362 | 18220 | 17895 | 19275 | 21094 | 22517 | 22815 | 21561 | 21072 | 22010 | 24873 | 24400 | 24021
2400 | 2400 | 100 | 4 | 10 | Winter | 4 | 9 | Winter | 24 | 14395 | 14536 | 15559 | 14636 | 14935 | 16770 | 17833 | 17442 | 17413 | 17328 | 18597 | 20299 | 21790 | 22179 | 20999 | 20587 | 21248 | 24190 | 23647 | 23371
2401 | 2401 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 1 | 14253 | 13783 | 14422 | 14164 | 14606 | 16815 | 17042 | 16644 | 17181 | 17004 | 18729 | 20631 | 21114 | 20613 | 19440 | 20185 | 21997 | 23599 | 23659 | 22812
2402 | 2402 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 2 | 14033 | 13483 | 14111 | 13890 | 14500 | 16604 | 16719 | 16271 | 16856 | 16886 | 18481 | 20345 | 20685 | 20162 | 18951 | 19929 | 21505 | 23086 | 23424 | 22302
2403 | 2403 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 3 | 13953 | 13350 | 13922 | 13755 | 14444 | 16482 | 16556 | 16011 | 16591 | 16773 | 18254 | 20076 | 20356 | 19749 | 18713 | 19985 | 21223 | 22656 | 23011 | 21821
2404 | 2404 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 4 | 14081 | 13451 | 13959 | 13731 | 14522 | 16541 | 16531 | 15791 | 16417 | 16662 | 18057 | 19775 | 19918 | 19222 | 18265 | 19957 | 20796 | 21977 | 22188 | 21111
2405 | 2405 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 5 | 14579 | 13928 | 14239 | 13887 | 15001 | 16913 | 16860 | 15662 | 16467 | 16899 | 18187 | 19740 | 19748 | 18939 | 18018 | 19935 | 20718 | 21523 | 21794 | 20614
2406 | 2406 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 6 | 15715 | 15033 | 14834 | 14225 | 15884 | 17974 | 17854 | 15789 | 16740 | 17474 | 18950 | 20362 | 20151 | 18794 | 17776 | 20099 | 21105 | 21660 | 21997 | 20246
2407 | 2407 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 7 | 16920 | 16250 | 15295 | 14375 | 16939 | 19057 | 19012 | 15731 | 16835 | 18231 | 19637 | 20988 | 20882 | 18563 | 17365 | 20352 | 21427 | 22197 | 22445 | 19852
2408 | 2408 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 8 | 17537 | 16801 | 15568 | 14556 | 17452 | 19569 | 19489 | 16065 | 16912 | 18672 | 19709 | 21237 | 21154 | 18462 | 17252 | 20780 | 21316 | 22392 | 22552 | 19664
2409 | 2409 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 9 | 17266 | 16570 | 15664 | 14704 | 17195 | 19217 | 18944 | 16037 | 16908 | 18369 | 19289 | 20748 | 20473 | 18288 | 17079 | 20564 | 20724 | 21663 | 21961 | 19435
2410 | 2410 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 10 | 16940 | 16296 | 15625 | 14794 | 16911 | 18887 | 18394 | 15902 | 16887 | 18127 | 19086 | 20475 | 19981 | 18251 | 17208 | 20159 | 20523 | 21216 | 21752 | 19458
2411 | 2411 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 11 | 16647 | 15944 | 15371 | 14648 | 16605 | 18596 | 17996 | 15816 | 16671 | 17865 | 18937 | 20260 | 19662 | 18073 | 17174 | 19897 | 20454 | 20941 | 21513 | 19327
2412 | 2412 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 12 | 16407 | 15732 | 15170 | 14598 | 16514 | 18313 | 17859 | 15731 | 16490 | 17771 | 18754 | 19999 | 19558 | 17889 | 17184 | 19813 | 20332 | 20851 | 21273 | 19156
2413 | 2413 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 13 | 16168 | 15534 | 14920 | 14571 | 16490 | 18026 | 17723 | 15512 | 16234 | 17738 | 18649 | 19702 | 19406 | 17614 | 17153 | 19715 | 20222 | 20685 | 20911 | 18870
2414 | 2414 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 14 | 15839 | 15316 | 14627 | 14451 | 16341 | 17717 | 17485 | 15253 | 15904 | 17567 | 18412 | 19351 | 19102 | 17255 | 16981 | 19457 | 19932 | 20352 | 20488 | 18485
2415 | 2415 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 15 | 15744 | 15202 | 14426 | 14466 | 16275 | 17620 | 17363 | 15012 | 15666 | 17471 | 18325 | 19219 | 18918 | 16995 | 16960 | 19321 | 19810 | 20135 | 20212 | 18200
2416 | 2416 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 16 | 16069 | 15418 | 14717 | 14848 | 16582 | 17924 | 17575 | 15224 | 15886 | 17724 | 18862 | 19425 | 18986 | 17143 | 17231 | 19546 | 20325 | 20133 | 20135 | 18306
2417 | 2417 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 17 | 16636 | 16037 | 15465 | 15622 | 17270 | 18451 | 18231 | 15937 | 16618 | 18436 | 19577 | 19920 | 19665 | 17922 | 17976 | 20321 | 21032 | 20817 | 20628 | 19100
2418 | 2418 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 18 | 16959 | 16400 | 16100 | 16208 | 17797 | 18845 | 18755 | 16425 | 17546 | 19220 | 20065 | 20475 | 20498 | 19024 | 18970 | 21195 | 21698 | 21749 | 21791 | 20285
2419 | 2419 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 19 | 17512 | 16481 | 16194 | 16492 | 18042 | 19516 | 19250 | 17057 | 17935 | 19659 | 20576 | 21596 | 21361 | 19783 | 19766 | 21724 | 22541 | 22841 | 23089 | 21208
2420 | 2420 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 20 | 17976 | 16949 | 16793 | 17080 | 18652 | 20217 | 19967 | 17946 | 18841 | 20455 | 21626 | 22803 | 22681 | 21150 | 21056 | 22583 | 23960 | 24426 | 24780 | 22779
2421 | 2421 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 21 | 17551 | 16692 | 16675 | 16912 | 18497 | 20036 | 19969 | 18058 | 19068 | 20599 | 21881 | 23209 | 23317 | 21918 | 21645 | 23190 | 24714 | 25413 | 25679 | 23821
2422 | 2422 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 22 | 16593 | 15707 | 15888 | 16111 | 17502 | 19205 | 19056 | 17570 | 18482 | 19768 | 21223 | 22747 | 22797 | 21663 | 21305 | 22707 | 24362 | 25087 | 25529 | 23706
2423 | 2423 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 23 | 15494 | 14682 | 14988 | 15247 | 16476 | 18133 | 17842 | 16761 | 17634 | 18817 | 20238 | 21835 | 21788 | 20990 | 20645 | 21829 | 23538 | 24182 | 24854 | 23105
2424 | 2424 | 101 | 4 | 11 | Winter | 4 | 10 | Winter | 24 | 14677 | 13845 | 14303 | 14653 | 15675 | 17308 | 16913 | 16120 | 16981 | 18063 | 19476 | 21094 | 20976 | 20422 | 20153 | 21301 | 22870 | 23425 | 24272 | 22584
2425 | 2425 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 1 | 13743 | 13657 | 13781 | 14236 | 15246 | 16378 | 16061 | 16502 | 16066 | 17955 | 19191 | 20304 | 20408 | 18838 | 19526 | 21471 | 22584 | 22678 | 22519 | 20714
2426 | 2426 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 2 | 13500 | 13381 | 13532 | 14142 | 15062 | 16078 | 15766 | 16201 | 15830 | 17755 | 18952 | 19918 | 19935 | 18387 | 19222 | 21011 | 22110 | 22172 | 22030 | 20214
2427 | 2427 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 3 | 13399 | 13195 | 13382 | 14067 | 14919 | 15901 | 15563 | 15934 | 15624 | 17536 | 18728 | 19586 | 19801 | 18149 | 19068 | 20733 | 21839 | 21704 | 21522 | 19918
2428 | 2428 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 4 | 13525 | 13232 | 13376 | 14156 | 15014 | 15921 | 15539 | 15815 | 15442 | 17409 | 18455 | 19213 | 19598 | 17745 | 18764 | 20330 | 21300 | 21021 | 20822 | 19363
2429 | 2429 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 5 | 14020 | 13522 | 13549 | 14643 | 15533 | 16297 | 15810 | 15925 | 15396 | 17619 | 18536 | 19115 | 19229 | 17539 | 18839 | 20277 | 21101 | 20627 | 20331 | 18989
2430 | 2430 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 6 | 15285 | 14180 | 13955 | 15605 | 16726 | 17379 | 16741 | 16338 | 15508 | 18500 | 19212 | 19660 | 18881 | 17380 | 19166 | 20751 | 21400 | 20682 | 20006 | 18653
2431 | 2431 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 7 | 16563 | 14632 | 14112 | 16659 | 17758 | 18534 | 17778 | 16486 | 15411 | 19228 | 19894 | 20431 | 18408 | 16967 | 19669 | 21072 | 21787 | 21048 | 19578 | 18120
2432 | 2432 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 8 | 16796 | 14726 | 14113 | 16973 | 17893 | 18806 | 18072 | 16401 | 15294 | 19135 | 19917 | 20538 | 18398 | 16663 | 19779 | 20770 | 21613 | 21056 | 19184 | 17751
2433 | 2433 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 9 | 16057 | 14659 | 14115 | 16552 | 17419 | 18099 | 17616 | 16257 | 15163 | 18569 | 19198 | 19705 | 17975 | 16331 | 19075 | 20015 | 20664 | 20460 | 18790 | 17375
2434 | 2434 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 10 | 15610 | 14674 | 14243 | 16300 | 17146 | 17576 | 17331 | 16262 | 15322 | 18382 | 18905 | 19226 | 17480 | 16476 | 18835 | 19833 | 20369 | 20291 | 18833 | 17578
2435 | 2435 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 11 | 15408 | 14626 | 14295 | 16184 | 17096 | 17369 | 17183 | 16229 | 15432 | 18414 | 18835 | 19086 | 17416 | 16627 | 18809 | 19950 | 20384 | 20252 | 18892 | 17772
2436 | 2436 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 12 | 15301 | 14462 | 14283 | 16118 | 16932 | 17261 | 17016 | 16068 | 15438 | 18267 | 18668 | 18999 | 17372 | 16671 | 18783 | 19838 | 20263 | 20086 | 18758 | 17831
2437 | 2437 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 13 | 15244 | 14237 | 14277 | 16112 | 16850 | 17148 | 16825 | 15829 | 15432 | 18184 | 18538 | 18867 | 17144 | 16663 | 18765 | 19744 | 20127 | 19883 | 18494 | 17817
2438 | 2438 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 14 | 15109 | 13989 | 14214 | 16027 | 16730 | 16971 | 16621 | 15566 | 15355 | 18011 | 18352 | 18631 | 16877 | 16552 | 18618 | 19521 | 19908 | 19598 | 18166 | 17686
2439 | 2439 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 15 | 15113 | 13850 | 14273 | 16014 | 16759 | 16909 | 16534 | 15384 | 15408 | 17978 | 18280 | 18509 | 16644 | 16583 | 18551 | 19453 | 19827 | 19440 | 17930 | 17702
2440 | 2440 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 16 | 15449 | 14182 | 14703 | 16383 | 17309 | 17186 | 16736 | 15672 | 15797 | 18564 | 18512 | 18651 | 16822 | 16913 | 18796 | 20034 | 19998 | 19437 | 18085 | 18002
2441 | 2441 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 17 | 16109 | 14881 | 15429 | 17034 | 17928 | 17813 | 17398 | 16363 | 16568 | 19242 | 19095 | 19296 | 17653 | 17623 | 19471 | 20703 | 20632 | 20010 | 18843 | 18729
2442 | 2442 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 18 | 16311 | 15414 | 15890 | 17473 | 18298 | 18254 | 17878 | 17171 | 17303 | 19644 | 19731 | 20024 | 18374 | 18546 | 20376 | 21304 | 21352 | 20977 | 19970 | 19720
2443 | 2443 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 19 | 16623 | 15487 | 16148 | 17700 | 18501 | 18718 | 18141 | 17505 | 17706 | 20080 | 20347 | 20824 | 19194 | 19307 | 21050 | 22116 | 22321 | 21913 | 20890 | 20605
2444 | 2444 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 20 | 17183 | 16067 | 16701 | 18273 | 19128 | 19397 | 18820 | 18326 | 18553 | 21033 | 21557 | 22049 | 20276 | 20543 | 22255 | 23495 | 23975 | 23380 | 22453 | 22003
2445 | 2445 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 21 | 16905 | 15890 | 16485 | 18063 | 18884 | 19321 | 18770 | 18444 | 18615 | 21157 | 21896 | 22559 | 20932 | 21056 | 22805 | 24178 | 24846 | 24332 | 23465 | 22737
2446 | 2446 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 22 | 15856 | 15108 | 15678 | 17063 | 17957 | 18394 | 17943 | 17815 | 17978 | 20448 | 21338 | 21992 | 20822 | 20697 | 22254 | 23808 | 24614 | 24121 | 23365 | 22489
2447 | 2447 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 23 | 14657 | 14247 | 14827 | 16063 | 16827 | 17196 | 16983 | 16960 | 17184 | 19447 | 20342 | 20969 | 20209 | 20035 | 21446 | 23012 | 23779 | 23474 | 22790 | 21888
2448 | 2448 | 102 | 4 | 12 | Winter | 4 | 11 | Winter | 24 | 13769 | 13579 | 14250 | 15294 | 16034 | 16279 | 16167 | 16312 | 16636 | 18691 | 19583 | 20158 | 19797 | 19555 | 20771 | 22357 | 23100 | 22845 | 22297 | 21445
2449 | 2449 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 1 | 13181 | 13331 | 14362 | 15057 | 15874 | 15631 | 16098 | 15702 | 16463 | 18611 | 19055 | 19597 | 20080 | 19616 | 21148 | 22289 | 22594 | 22432 | 20683 | 21034
2450 | 2450 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 2 | 12895 | 13064 | 14164 | 14854 | 15667 | 15320 | 15780 | 15448 | 16362 | 18385 | 18756 | 19179 | 19652 | 19309 | 20684 | 21811 | 22064 | 21928 | 20164 | 20699
2451 | 2451 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 3 | 12765 | 12942 | 14053 | 14736 | 15580 | 15146 | 15545 | 15280 | 16258 | 18212 | 18517 | 18851 | 19252 | 19018 | 20441 | 21560 | 21766 | 21441 | 19892 | 20530
2452 | 2452 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 4 | 12864 | 12952 | 14193 | 14856 | 15621 | 15169 | 15481 | 15150 | 16192 | 18018 | 18175 | 18482 | 18775 | 18710 | 20087 | 21062 | 21126 | 20763 | 19350 | 20132
2453 | 2453 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 5 | 13361 | 13203 | 14747 | 15480 | 16067 | 15582 | 15756 | 15279 | 16498 | 18318 | 18268 | 18460 | 18566 | 18668 | 20098 | 20923 | 20860 | 20307 | 19005 | 20108
2454 | 2454 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 6 | 14503 | 13605 | 16068 | 16709 | 17119 | 16554 | 16240 | 15476 | 17163 | 19076 | 18776 | 18870 | 18515 | 19318 | 20597 | 21253 | 21013 | 19978 | 18650 | 20298
2455 | 2455 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 7 | 15715 | 13811 | 17347 | 17836 | 18225 | 17682 | 16514 | 15516 | 17953 | 19896 | 19385 | 19534 | 18320 | 19980 | 20972 | 21688 | 21219 | 19576 | 18133 | 20736
2456 | 2456 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 8 | 16078 | 13875 | 17562 | 18025 | 18506 | 18022 | 16500 | 15467 | 18228 | 19997 | 19512 | 19708 | 18055 | 19997 | 20724 | 21562 | 21115 | 19220 | 17794 | 20837
2457 | 2457 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 9 | 15684 | 13901 | 17077 | 17560 | 17917 | 17583 | 16384 | 15368 | 17777 | 19303 | 18904 | 19195 | 17733 | 19381 | 19990 | 20635 | 20320 | 18841 | 17428 | 20097
2458 | 2458 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 10 | 15452 | 14022 | 16846 | 17292 | 17554 | 17312 | 16393 | 15543 | 17566 | 19019 | 18582 | 18975 | 17721 | 19219 | 19806 | 20341 | 20009 | 18881 | 17633 | 19901
2459 | 2459 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 11 | 15296 | 14073 | 16672 | 17204 | 17401 | 17139 | 16330 | 15609 | 17497 | 18911 | 18525 | 18871 | 17728 | 19144 | 19912 | 20338 | 20062 | 18934 | 17821 | 19911
2460 | 2460 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 12 | 15195 | 14129 | 16608 | 17102 | 17275 | 17011 | 16207 | 15656 | 17510 | 18774 | 18418 | 18756 | 17652 | 19130 | 19878 | 20305 | 20056 | 18877 | 17963 | 19974
2461 | 2461 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 13 | 15020 | 14126 | 16550 | 17023 | 17137 | 16817 | 15968 | 15650 | 17494 | 18644 | 18271 | 18557 | 17394 | 19065 | 19785 | 20169 | 19901 | 18613 | 17947 | 19953
2462 | 2462 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 14 | 14812 | 14011 | 16267 | 16846 | 16930 | 16558 | 15649 | 15514 | 17327 | 18403 | 18031 | 18250 | 17043 | 18727 | 19506 | 19888 | 19624 | 18227 | 17760 | 19726
2463 | 2463 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 15 | 14740 | 14064 | 16176 | 16883 | 16885 | 16493 | 15489 | 15572 | 17279 | 18355 | 17933 | 18135 | 16830 | 18565 | 19445 | 19798 | 19467 | 17994 | 17775 | 19649
2464 | 2464 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 16 | 15005 | 14492 | 16484 | 17410 | 17209 | 16716 | 15795 | 15974 | 17587 | 18611 | 18100 | 18228 | 17037 | 18731 | 20031 | 19966 | 19529 | 18146 | 18074 | 19868
2465 | 2465 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 17 | 15569 | 15136 | 16930 | 17945 | 17814 | 17274 | 16361 | 16605 | 18248 | 19044 | 18566 | 18769 | 17762 | 19285 | 20680 | 20567 | 20037 | 18882 | 18775 | 20541
2466 | 2466 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 18 | 15855 | 15570 | 17073 | 18306 | 18322 | 17726 | 17117 | 17275 | 18948 | 19649 | 19531 | 19577 | 18782 | 19951 | 21269 | 21278 | 21199 | 20010 | 19772 | 21501
2467 | 2467 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 19 | 15915 | 15801 | 17695 | 18468 | 18550 | 17945 | 17400 | 17617 | 19329 | 20181 | 20050 | 20206 | 19481 | 21049 | 22042 | 22206 | 22127 | 20917 | 20655 | 22252
2468 | 2468 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 20 | 16359 | 16307 | 18286 | 19050 | 19321 | 18577 | 18165 | 18399 | 20057 | 21289 | 21204 | 21305 | 20776 | 22199 | 23358 | 23820 | 23718 | 22476 | 22037 | 23576
2469 | 2469 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 21 | 16066 | 16087 | 17868 | 18769 | 19165 | 18474 | 18216 | 18396 | 20104 | 21517 | 21753 | 21798 | 21447 | 22476 | 23983 | 24642 | 24818 | 23470 | 22773 | 24270
2470 | 2470 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 22 | 15072 | 15250 | 16779 | 17813 | 18290 | 17617 | 17547 | 17709 | 19235 | 20883 | 21165 | 21308 | 21141 | 21817 | 23574 | 24372 | 24545 | 23371 | 22519 | 23789
2471 | 2471 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 23 | 14044 | 14367 | 15560 | 16657 | 17142 | 16622 | 16646 | 16866 | 18258 | 19827 | 20225 | 20496 | 20441 | 20783 | 22731 | 23501 | 23757 | 22763 | 21895 | 23000
2472 | 2472 | 103 | 4 | 13 | Winter | 4 | 12 | Winter | 24 | 13211 | 13767 | 14689 | 15842 | 16285 | 15773 | 15962 | 16277 | 17490 | 19026 | 19528 | 19765 | 19862 | 20004 | 22042 | 22787 | 23165 | 22243 | 21435 | 22308
2473 | 2473 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 1 | 13175 | 13521 | 14780 | 15567 | 15511 | 15630 | 15334 | 15790 | 17424 | 18400 | 18863 | 19404 | 18518 | 20658 | 21861 | 22155 | 22296 | 20553 | 21362 | 22751
2474 | 2474 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 2 | 12907 | 13430 | 14594 | 15367 | 15256 | 15322 | 15086 | 15663 | 17229 | 18136 | 18486 | 19009 | 18068 | 20220 | 21406 | 21636 | 21848 | 20042 | 21029 | 22260
2475 | 2475 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 3 | 12767 | 13384 | 14498 | 15304 | 15160 | 15112 | 14943 | 15580 | 17068 | 17949 | 18201 | 18653 | 17886 | 20011 | 21187 | 21380 | 21454 | 19786 | 20704 | 21986
2476 | 2476 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 4 | 12800 | 13502 | 14614 | 15370 | 15149 | 15067 | 14836 | 15569 | 16996 | 17666 | 17891 | 18243 | 17525 | 19686 | 20715 | 20781 | 20767 | 19241 | 20239 | 21492
2477 | 2477 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 5 | 13160 | 14083 | 15254 | 15926 | 15602 | 15388 | 15015 | 15897 | 17413 | 17864 | 17976 | 18127 | 17399 | 19756 | 20629 | 20569 | 20505 | 18902 | 20036 | 21357
2478 | 2478 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 6 | 13813 | 15104 | 16489 | 17018 | 16550 | 15919 | 15274 | 16522 | 18364 | 18475 | 18487 | 18154 | 17270 | 20303 | 21003 | 20744 | 20608 | 18553 | 20520 | 21699
2479 | 2479 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 7 | 14314 | 16258 | 17637 | 18165 | 17488 | 16203 | 15338 | 17153 | 19224 | 19127 | 19187 | 18033 | 16916 | 20718 | 21478 | 20976 | 21028 | 18035 | 21063 | 21941
2480 | 2480 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 8 | 14508 | 16658 | 17881 | 18501 | 17803 | 16226 | 15333 | 17649 | 19257 | 19310 | 19413 | 17846 | 16705 | 20525 | 21400 | 20929 | 21050 | 17730 | 21055 | 21639
2481 | 2481 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 9 | 14666 | 16458 | 17624 | 18103 | 17548 | 16294 | 15424 | 17737 | 18929 | 18873 | 19071 | 17762 | 16608 | 20017 | 20702 | 20360 | 20615 | 17583 | 20602 | 21066
2482 | 2482 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 10 | 14713 | 16227 | 17329 | 17707 | 17188 | 16242 | 15534 | 17691 | 18757 | 18462 | 18762 | 17741 | 16760 | 19830 | 20407 | 20045 | 20521 | 17786 | 20493 | 20938
2483 | 2483 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 11 | 14635 | 16118 | 17230 | 17523 | 17029 | 16163 | 15584 | 17776 | 18722 | 18378 | 18640 | 17721 | 16868 | 19910 | 20382 | 20072 | 20545 | 17954 | 20440 | 21074
2484 | 2484 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 12 | 14493 | 16105 | 17110 | 17358 | 16852 | 16031 | 15622 | 17743 | 18563 | 18273 | 18520 | 17607 | 16948 | 19832 | 20305 | 20034 | 20498 | 18050 | 20400 | 21016
2485 | 2485 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 13 | 14268 | 16102 | 17037 | 17230 | 16696 | 15797 | 15620 | 17687 | 18482 | 18132 | 18328 | 17363 | 16941 | 19746 | 20174 | 19888 | 20314 | 18040 | 20337 | 20924
2486 | 2486 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 14 | 14058 | 16078 | 16993 | 17142 | 16605 | 15609 | 15613 | 17620 | 18358 | 18031 | 18153 | 17135 | 16879 | 19595 | 20018 | 19734 | 20059 | 17975 | 20101 | 20745
2487 | 2487 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 15 | 14015 | 16177 | 17120 | 17205 | 16636 | 15540 | 15760 | 17683 | 18436 | 18025 | 18137 | 17027 | 16997 | 19628 | 20020 | 19675 | 19939 | 18077 | 20009 | 20752
2488 | 2488 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 16 | 14371 | 16561 | 17622 | 17567 | 16958 | 15888 | 16200 | 18061 | 19058 | 18247 | 18283 | 17280 | 17365 | 20255 | 20227 | 19777 | 19965 | 18402 | 20169 | 21340
2489 | 2489 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 17 | 14805 | 16961 | 18009 | 17954 | 17261 | 16328 | 16707 | 18475 | 19398 | 18599 | 18717 | 17801 | 17850 | 20704 | 20635 | 20091 | 20226 | 18903 | 20545 | 21808
2490 | 2490 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 18 | 15188 | 17167 | 18242 | 18327 | 17830 | 16938 | 17209 | 18929 | 19648 | 19400 | 19358 | 18647 | 18629 | 21163 | 21200 | 21111 | 21016 | 19774 | 21155 | 22333
2491 | 2491 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 19 | 15118 | 17198 | 18252 | 18405 | 17943 | 17064 | 17391 | 19044 | 19898 | 19714 | 19784 | 19153 | 19222 | 21747 | 21952 | 21878 | 21939 | 20529 | 22245 | 23092
2492 | 2492 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 20 | 15678 | 17678 | 18792 | 19125 | 18604 | 17782 | 18121 | 19639 | 20766 | 20753 | 20780 | 20360 | 20398 | 23006 | 23505 | 23418 | 23370 | 21907 | 23547 | 24561
2493 | 2493 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 21 | 15457 | 17396 | 18459 | 18900 | 18621 | 17760 | 18043 | 19585 | 20775 | 21167 | 21137 | 20900 | 20823 | 23535 | 24238 | 24441 | 24251 | 22612 | 24013 | 25354
2494 | 2494 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 22 | 14682 | 16390 | 17497 | 18028 | 17752 | 17084 | 17345 | 18760 | 20025 | 20526 | 20595 | 20564 | 20438 | 23103 | 23950 | 24167 | 24056 | 22385 | 23481 | 25063
2495 | 2495 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 23 | 13791 | 15303 | 16311 | 16856 | 16655 | 16155 | 16467 | 17706 | 18952 | 19521 | 19724 | 19807 | 19714 | 22193 | 23051 | 23335 | 23279 | 21731 | 22482 | 24254
2496 | 2496 | 104 | 4 | 14 | Winter | 4 | 13 | Winter | 24 | 13127 | 14533 | 15516 | 16027 | 15895 | 15490 | 15891 | 17020 | 18182 | 18829 | 19000 | 19224 | 19226 | 21514 | 22343 | 22742 | 22667 | 21285 | 21747 | 23610
2497 | 2497 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 1 | 12510 | 13869 | 14919 | 14896 | 14774 | 14565 | 15229 | 16553 | 17674 | 17698 | 17951 | 17682 | 18604 | 21021 | 21399 | 21817 | 21452 | 20472 | 22297 | 23184
2498 | 2498 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 2 | 12271 | 13660 | 14692 | 14591 | 14425 | 14245 | 15051 | 16282 | 17483 | 17190 | 17486 | 17265 | 18413 | 20602 | 20907 | 21337 | 20852 | 20150 | 21825 | 22708
2499 | 2499 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 3 | 12171 | 13624 | 14684 | 14553 | 14207 | 14175 | 15064 | 16217 | 17354 | 16969 | 17218 | 17106 | 18525 | 20417 | 20677 | 20920 | 20440 | 19999 | 21550 | 22444
2500 | 2500 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 4 | 12178 | 13762 | 14792 | 14595 | 14109 | 14138 | 15127 | 16251 | 17220 | 16657 | 16860 | 16788 | 18619 | 19990 | 20110 | 20285 | 19753 | 19592 | 21057 | 21832
2501 | 2501 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 5 | 12435 | 14391 | 15346 | 15065 | 14200 | 14339 | 15645 | 16734 | 17598 | 16499 | 16742 | 16704 | 18748 | 19947 | 19933 | 19962 | 19243 | 19568 | 20914 | 21571
2502 | 2502 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 6 | 12871 | 15696 | 16497 | 16113 | 14534 | 14694 | 16522 | 17831 | 18476 | 16490 | 16766 | 16696 | 19083 | 20430 | 20207 | 20106 | 18794 | 19810 | 21309 | 21821
2503 | 2503 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 7 | 13098 | 16902 | 17676 | 17088 | 14603 | 14811 | 17475 | 18760 | 19343 | 16233 | 16644 | 16421 | 19428 | 20965 | 20497 | 20538 | 18296 | 20266 | 21575 | 22170
2504 | 2504 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 8 | 13354 | 17331 | 18176 | 17542 | 14974 | 14975 | 18005 | 18978 | 19646 | 16518 | 16798 | 16378 | 19907 | 21071 | 20613 | 20770 | 18316 | 20543 | 21412 | 22147
2505 | 2505 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 9 | 13730 | 17209 | 17930 | 17387 | 15159 | 15196 | 17885 | 18741 | 19284 | 16574 | 16986 | 16448 | 19932 | 20540 | 20201 | 20560 | 18438 | 20177 | 20993 | 21533
2506 | 2506 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 10 | 13886 | 16977 | 17611 | 17046 | 15085 | 15364 | 17681 | 18555 | 18982 | 16490 | 17237 | 16648 | 19600 | 20296 | 19938 | 20456 | 18760 | 20039 | 20920 | 21347
2507 | 2507 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 11 | 13829 | 16791 | 17337 | 16808 | 15051 | 15313 | 17475 | 18450 | 18761 | 16511 | 17332 | 16660 | 19394 | 20159 | 19852 | 20293 | 18929 | 19920 | 20965 | 21261
2508 | 2508 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 12 | 13725 | 16581 | 17073 | 16559 | 14876 | 15250 | 17352 | 18239 | 18487 | 16414 | 17233 | 16628 | 19242 | 19964 | 19698 | 20049 | 18832 | 19828 | 20787 | 21089
2509 | 2509 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 13 | 13695 | 16460 | 16900 | 16364 | 14642 | 15203 | 17303 | 18118 | 18328 | 16175 | 17001 | 16581 | 19134 | 19789 | 19507 | 19804 | 18602 | 19766 | 20651 | 20912
2510 | 2510 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 14 | 13782 | 16479 | 16876 | 16362 | 14595 | 15261 | 17328 | 18083 | 18300 | 16076 | 16838 | 16609 | 19087 | 19703 | 19423 | 19646 | 18416 | 19731 | 20535 | 20805
2511 | 2511 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 15 | 13899 | 16602 | 16935 | 16390 | 14515 | 15402 | 17389 | 18162 | 18326 | 15962 | 16780 | 16728 | 19082 | 19702 | 19363 | 19581 | 18312 | 19732 | 20540 | 20788
2512 | 2512 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 16 | 14222 | 16960 | 17181 | 16595 | 14732 | 15725 | 17633 | 18622 | 18497 | 16084 | 16887 | 16983 | 19279 | 19795 | 19352 | 19480 | 18329 | 19853 | 20998 | 20843
2513 | 2513 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 17 | 14813 | 17459 | 17694 | 17078 | 15302 | 16358 | 18175 | 19174 | 18946 | 16656 | 17260 | 17589 | 19918 | 20324 | 19792 | 19961 | 18721 | 20443 | 21589 | 21396
2514 | 2514 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 18 | 14986 | 17563 | 17939 | 17491 | 15394 | 16717 | 18518 | 19281 | 19284 | 17024 | 17696 | 18205 | 20451 | 20754 | 20671 | 20669 | 19407 | 21161 | 21991 | 21914
2515 | 2515 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 19 | 15012 | 17474 | 17924 | 17496 | 15728 | 16811 | 18629 | 19401 | 19561 | 17623 | 18214 | 18668 | 20673 | 21395 | 21324 | 21363 | 20260 | 21717 | 22683 | 22734
2516 | 2516 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 20 | 15483 | 17984 | 18619 | 18127 | 16488 | 17524 | 19256 | 20206 | 20571 | 18667 | 19301 | 19778 | 21396 | 22882 | 22831 | 22777 | 21698 | 23042 | 24162 | 24460
2517 | 2517 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 21 | 15239 | 17646 | 18378 | 18114 | 16407 | 17419 | 19169 | 20147 | 20689 | 18980 | 19738 | 20138 | 21791 | 23560 | 23800 | 23642 | 22660 | 23725 | 24956 | 25416
2518 | 2518 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 22 | 14385 | 16636 | 17458 | 17201 | 15846 | 16677 | 18228 | 19319 | 20002 | 18651 | 19437 | 19682 | 21216 | 23201 | 23476 | 23379 | 22668 | 23241 | 24641 | 25216
2519 | 2519 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 23 | 13519 | 15463 | 16317 | 16136 | 15035 | 15834 | 17234 | 18251 | 18931 | 17927 | 18794 | 18964 | 20309 | 22317 | 22676 | 22700 | 22183 | 22466 | 23859 | 24416
2520 | 2520 | 105 | 4 | 15 | Winter | 4 | 14 | Winter | 24 | 12935 | 14648 | 15473 | 15362 | 14378 | 15242 | 16453 | 17445 | 18127 | 17345 | 18251 | 18440 | 19769 | 21586 | 22056 | 22043 | 21752 | 21794 | 23218 | 23733
2521 | 2521 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 1 | 12709 | 14414 | 14680 | 14488 | 14582 | 14914 | 16196 | 17175 | 17421 | 17374 | 17008 | 18011 | 19918 | 20947 | 21134 | 21143 | 19962 | 22208 | 23110 | 23175
2522 | 2522 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 2 | 12583 | 14180 | 14381 | 14168 | 14205 | 14725 | 15917 | 16875 | 17063 | 16927 | 16702 | 17743 | 19503 | 20458 | 20606 | 20545 | 19557 | 21721 | 22623 | 22636
2523 | 2523 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 3 | 12559 | 14163 | 14343 | 14057 | 14008 | 14733 | 15855 | 16844 | 16978 | 16687 | 16527 | 17676 | 19299 | 20239 | 20293 | 20139 | 19251 | 21445 | 22368 | 22330
2524 | 2524 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 4 | 12742 | 14331 | 14452 | 14151 | 13993 | 14869 | 15981 | 16870 | 16867 | 16457 | 16237 | 17547 | 19063 | 19780 | 19743 | 19539 | 18671 | 21018 | 21828 | 21675
2525 | 2525 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 5 | 13314 | 14898 | 14927 | 14589 | 14245 | 15401 | 16502 | 17315 | 17144 | 16423 | 16217 | 17778 | 19179 | 19660 | 19369 | 19057 | 18297 | 20887 | 21571 | 21334
2526 | 2526 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 6 | 14388 | 16024 | 15983 | 15539 | 14679 | 16286 | 17638 | 18278 | 17889 | 16517 | 16134 | 18268 | 19814 | 19974 | 19307 | 18642 | 17861 | 21275 | 21806 | 21425
2527 | 2527 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 7 | 15600 | 17229 | 16990 | 16663 | 14910 | 17263 | 18634 | 19206 | 18634 | 16464 | 15880 | 18925 | 20305 | 20300 | 19545 | 18163 | 17384 | 21547 | 22154 | 21598
2528 | 2528 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 8 | 16175 | 17744 | 17479 | 17193 | 15267 | 17822 | 18918 | 19571 | 19021 | 16675 | 15855 | 19334 | 20315 | 20467 | 19606 | 18220 | 17232 | 21429 | 22146 | 21685
2529 | 2529 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 9 | 16314 | 17732 | 17550 | 17311 | 15838 | 17916 | 18910 | 19396 | 18915 | 17084 | 16090 | 19246 | 20185 | 20261 | 19562 | 18537 | 17401 | 21217 | 21736 | 21439
2530 | 2530 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 10 | 16240 | 17515 | 17307 | 17219 | 16126 | 17788 | 18795 | 19182 | 18646 | 17407 | 16409 | 19140 | 20129 | 20067 | 19701 | 18933 | 17787 | 21214 | 21626 | 21286
2531 | 2531 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 11 | 15996 | 17189 | 17031 | 16964 | 16107 | 17532 | 18632 | 18921 | 18421 | 17454 | 16559 | 18937 | 20058 | 19928 | 19766 | 19057 | 18000 | 21200 | 21496 | 21201
2532 | 2532 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 12 | 15967 | 17004 | 16843 | 16843 | 16043 | 17469 | 18478 | 18747 | 18299 | 17410 | 16707 | 18892 | 19940 | 19820 | 19832 | 19037 | 18183 | 21081 | 21385 | 21139
2533 | 2533 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 13 | 15865 | 16788 | 16603 | 16644 | 15764 | 17375 | 18313 | 18533 | 18064 | 17137 | 16667 | 18793 | 19758 | 19586 | 19693 | 18753 | 18129 | 20901 | 21164 | 20912
2534 | 2534 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 14 | 15754 | 16634 | 16468 | 16487 | 15480 | 17271 | 18152 | 18356 | 17878 | 16841 | 16503 | 18654 | 19522 | 19373 | 19499 | 18424 | 17916 | 20652 | 20923 | 20671
2535 | 2535 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 15 | 15842 | 16695 | 16497 | 16492 | 15454 | 17332 | 18233 | 18390 | 17868 | 16789 | 16617 | 18682 | 19555 | 19317 | 19441 | 18334 | 18001 | 20656 | 20903 | 20587
2536 | 2536 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 16 | 16141 | 16968 | 16748 | 16690 | 15681 | 17623 | 18706 | 18616 | 18025 | 16947 | 16903 | 18897 | 20097 | 19358 | 19372 | 18395 | 18222 | 21151 | 20994 | 20566
2537 | 2537 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 17 | 16540 | 17351 | 17110 | 16998 | 15864 | 18051 | 19141 | 18950 | 18385 | 17201 | 17318 | 19349 | 20550 | 19682 | 19511 | 18671 | 18706 | 21623 | 21428 | 20897
2538 | 2538 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 18 | 16571 | 17559 | 17412 | 17099 | 16065 | 18339 | 19198 | 19229 | 18988 | 17556 | 17842 | 19894 | 20832 | 20517 | 20004 | 19300 | 19345 | 21998 | 21908 | 21807
2539 | 2539 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 19 | 16494 | 17505 | 17362 | 17076 | 16239 | 18405 | 19256 | 19427 | 19151 | 17972 | 18199 | 20213 | 21286 | 21110 | 20647 | 20100 | 19977 | 22658 | 22707 | 22580
2540 | 2540 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 20 | 16935 | 18140 | 17948 | 17554 | 16926 | 18995 | 19997 | 20369 | 20113 | 18959 | 19262 | 21256 | 22484 | 22546 | 21980 | 21519 | 21390 | 24117 | 24414 | 24225
2541 | 2541 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 21 | 16634 | 17862 | 17881 | 17389 | 16857 | 18851 | 19849 | 20381 | 20422 | 19262 | 19605 | 21570 | 22928 | 23415 | 22826 | 22409 | 22161 | 24881 | 25340 | 25377
2542 | 2542 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 22 | 15592 | 16888 | 16925 | 16491 | 16256 | 17874 | 18962 | 19608 | 19686 | 18870 | 19165 | 20866 | 22420 | 23017 | 22600 | 22370 | 21982 | 24549 | 25123 | 25133
2543 | 2543 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 23 | 14502 | 15730 | 15826 | 15446 | 15445 | 16853 | 17851 | 18485 | 18660 | 18168 | 18467 | 19965 | 21503 | 22159 | 21900 | 21856 | 21424 | 23746 | 24304 | 24359
2544 | 2544 | 106 | 4 | 16 | Winter | 4 | 15 | Winter | 24 | 13731 | 14895 | 15061 | 14648 | 14849 | 16088 | 17047 | 17669 | 17948 | 17618 | 17956 | 19255 | 20808 | 21539 | 21344 | 21421 | 20963 | 23105 | 23635 | 23793
2545 | 2545 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 1 | 13334 | 14058 | 14371 | 14317 | 14107 | 15729 | 16698 | 16886 | 16953 | 16451 | 17409 | 19293 | 20553 | 20655 | 20673 | 19611 | 20050 | 22912 | 22998 | 22662
2546 | 2546 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 2 | 13115 | 13781 | 14111 | 13951 | 13877 | 15459 | 16418 | 16547 | 16586 | 16176 | 17167 | 18898 | 20138 | 20254 | 20095 | 19223 | 19703 | 22430 | 22460 | 22100
2547 | 2547 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 3 | 13111 | 13750 | 14006 | 13780 | 13776 | 15416 | 16403 | 16504 | 16443 | 16043 | 17135 | 18748 | 19988 | 19928 | 19721 | 18952 | 19463 | 22186 | 22167 | 21690
2548 | 2548 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 4 | 13261 | 13850 | 14039 | 13760 | 13689 | 15533 | 16438 | 16427 | 16305 | 15780 | 17028 | 18548 | 19639 | 19380 | 19116 | 18373 | 19122 | 21613 | 21482 | 20986
2549 | 2549 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 5 | 13881 | 14338 | 14529 | 14025 | 13896 | 16085 | 16936 | 16767 | 16496 | 15836 | 17329 | 18730 | 19659 | 19241 | 18683 | 18025 | 19062 | 21372 | 21148 | 20621
2550 | 2550 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 6 | 15172 | 15403 | 15583 | 14503 | 14136 | 17276 | 17975 | 17610 | 17170 | 15841 | 17900 | 19450 | 20197 | 19524 | 18327 | 17628 | 19492 | 21637 | 21251 | 20618
2551 | 2551 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 7 | 16364 | 16414 | 16722 | 14735 | 14204 | 18300 | 18938 | 18404 | 18023 | 15623 | 18588 | 19986 | 20759 | 20042 | 17867 | 17140 | 20069 | 21983 | 21403 | 20967
2552 | 2552 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 8 | 16749 | 16830 | 17158 | 15025 | 14286 | 18535 | 19255 | 18752 | 18385 | 15542 | 18936 | 19975 | 20839 | 20199 | 17868 | 16928 | 20324 | 21930 | 21419 | 21087
2553 | 2553 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 9 | 16646 | 16765 | 17103 | 15449 | 14499 | 18389 | 18952 | 18515 | 18250 | 15639 | 18709 | 19704 | 20358 | 19977 | 18052 | 16937 | 20024 | 21375 | 21018 | 20885
2554 | 2554 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 10 | 16429 | 16482 | 16965 | 15685 | 14719 | 18203 | 18669 | 18186 | 18108 | 15892 | 18533 | 19579 | 20124 | 19943 | 18385 | 17259 | 19987 | 21200 | 20809 | 20895
2555 | 2555 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 11 | 16312 | 16317 | 16807 | 15770 | 14920 | 18125 | 18508 | 18061 | 18016 | 16143 | 18429 | 19599 | 20058 | 19916 | 18608 | 17573 | 19998 | 21175 | 20827 | 20920
2556 | 2556 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 12 | 16131 | 16080 | 16619 | 15639 | 14991 | 17920 | 18273 | 17866 | 17880 | 16238 | 18332 | 19415 | 19868 | 19764 | 18536 | 17690 | 19865 | 20996 | 20712 | 20807
2557 | 2557 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 13 | 15983 | 15889 | 16403 | 15394 | 14965 | 17781 | 18085 | 17662 | 17705 | 16223 | 18258 | 19270 | 19670 | 19526 | 18282 | 17672 | 19732 | 20803 | 20511 | 20619
2558 | 2558 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 14 | 15883 | 15750 | 16234 | 15129 | 14832 | 17628 | 17906 | 17499 | 17520 | 16060 | 18122 | 19064 | 19455 | 19238 | 17948 | 17478 | 19528 | 20558 | 20271 | 20333
2559 | 2559 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 15 | 15976 | 15741 | 16195 | 15060 | 14934 | 17670 | 17903 | 17451 | 17445 | 16134 | 18113 | 19060 | 19426 | 19085 | 17821 | 17525 | 19439 | 20501 | 20148 | 20174
2560 | 2560 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 16 | 16344 | 15957 | 16372 | 15277 | 15252 | 18135 | 18125 | 17613 | 17522 | 16423 | 18333 | 19576 | 19534 | 19049 | 17879 | 17733 | 19476 | 20574 | 20117 | 20082
2561 | 2561 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 17 | 16782 | 16361 | 16661 | 15498 | 15760 | 18611 | 18500 | 18010 | 17891 | 16872 | 18820 | 20063 | 19997 | 19351 | 18191 | 18256 | 19942 | 21043 | 20485 | 20425
2562 | 2562 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 18 | 16971 | 16719 | 16868 | 15771 | 16163 | 18771 | 18870 | 18656 | 18309 | 17467 | 19438 | 20429 | 20484 | 20050 | 18919 | 18993 | 20649 | 21633 | 21513 | 21151
2563 | 2563 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 19 | 16919 | 16734 | 17044 | 16007 | 16295 | 18882 | 19108 | 18838 | 18594 | 17844 | 19785 | 20909 | 21133 | 20841 | 19770 | 19691 | 21514 | 22504 | 22356 | 22000
2564 | 2564 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 20 | 17389 | 17288 | 17556 | 16655 | 17036 | 19568 | 19990 | 19714 | 19356 | 18819 | 20749 | 22019 | 22561 | 22116 | 21131 | 21074 | 22595 | 24199 | 23991 | 23401
2565 | 2565 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 21 | 17033 | 17188 | 17338 | 16547 | 16999 | 19377 | 19937 | 19933 | 19534 | 19075 | 20982 | 22374 | 23135 | 22811 | 21965 | 21812 | 23213 | 25112 | 25147 | 24408
2566 | 2566 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 22 | 16008 | 16242 | 16463 | 15934 | 16346 | 18481 | 19138 | 19150 | 18852 | 18594 | 20244 | 21819 | 22722 | 22485 | 21907 | 21623 | 22664 | 24913 | 24925 | 24217
2567 | 2567 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 23 | 14803 | 15147 | 15403 | 15127 | 15568 | 17356 | 17996 | 18094 | 17889 | 17868 | 19320 | 20865 | 21793 | 21662 | 21371 | 21049 | 21644 | 24082 | 24150 | 23491
2568 | 2568 | 107 | 4 | 17 | Winter | 4 | 16 | Winter | 24 | 13971 | 14364 | 14610 | 14520 | 14971 | 16533 | 17149 | 17344 | 17093 | 17327 | 18583 | 20135 | 21027 | 20996 | 20908 | 20567 | 20842 | 23390 | 23570 | 22860
2569 | 2569 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 1 | 13869 | 13693 | 14128 | 14004 | 14449 | 16326 | 16501 | 16714 | 16824 | 16751 | 18368 | 20013 | 20465 | 20241 | 19329 | 20109 | 21658 | 22904 | 22820 | 22420
2570 | 2570 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 2 | 13659 | 13291 | 13781 | 13790 | 14229 | 16054 | 16173 | 16294 | 16402 | 16496 | 17991 | 19625 | 20002 | 19678 | 18955 | 19781 | 21181 | 22367 | 22362 | 21802
2571 | 2571 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 3 | 13629 | 13124 | 13593 | 13654 | 14209 | 16015 | 16110 | 16163 | 16172 | 16453 | 17777 | 19470 | 19790 | 19302 | 18669 | 19623 | 20830 | 22066 | 21936 | 21354
2572 | 2572 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 4 | 13766 | 13104 | 13588 | 13579 | 14333 | 16082 | 16080 | 16136 | 15972 | 16408 | 17612 | 19186 | 19356 | 18748 | 18125 | 19274 | 20347 | 21397 | 21200 | 20612
2573 | 2573 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 5 | 14350 | 13271 | 13889 | 13820 | 14732 | 16636 | 16489 | 16477 | 16024 | 16638 | 17830 | 19305 | 19318 | 18395 | 17841 | 19311 | 20052 | 21100 | 20870 | 20043
2574 | 2574 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 6 | 15475 | 13672 | 14393 | 14083 | 15499 | 17722 | 17402 | 17321 | 16202 | 17150 | 18487 | 19919 | 19703 | 18094 | 17482 | 19581 | 20291 | 21216 | 20935 | 19520
2575 | 2575 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 7 | 16675 | 13796 | 14664 | 14182 | 16228 | 18729 | 18256 | 18238 | 16200 | 17651 | 19116 | 20551 | 20071 | 17671 | 17013 | 20031 | 20629 | 21368 | 21281 | 18934
2576 | 2576 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 8 | 17026 | 14064 | 14891 | 14177 | 16760 | 18983 | 18539 | 18582 | 16273 | 18087 | 19193 | 20582 | 20108 | 17601 | 16722 | 20182 | 20535 | 21296 | 21274 | 18778
2577 | 2577 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 9 | 16556 | 14020 | 15023 | 14096 | 16739 | 18380 | 18008 | 18133 | 16241 | 17902 | 18688 | 19813 | 19445 | 17474 | 16415 | 19551 | 19955 | 20576 | 20693 | 18589
2578 | 2578 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 10 | 16179 | 13928 | 15173 | 14221 | 16649 | 17986 | 17580 | 17794 | 16399 | 17850 | 18449 | 19470 | 19083 | 17697 | 16626 | 19323 | 19858 | 20265 | 20595 | 18875
2579 | 2579 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 11 | 15967 | 13995 | 15263 | 14417 | 16676 | 17816 | 17450 | 17622 | 16547 | 17939 | 18384 | 19386 | 19043 | 17912 | 16944 | 19268 | 19883 | 20284 | 20620 | 19139
2580 | 2580 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 12 | 15880 | 14032 | 15282 | 14618 | 16691 | 17720 | 17390 | 17563 | 16598 | 17987 | 18282 | 19326 | 19025 | 17987 | 17202 | 19329 | 19806 | 20296 | 20648 | 19233
2581 | 2581 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 13 | 15870 | 13963 | 15223 | 14782 | 16749 | 17713 | 17366 | 17496 | 16528 | 18050 | 18215 | 19319 | 18999 | 17915 | 17368 | 19434 | 19732 | 20274 | 20594 | 19157
2582 | 2582 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 14 | 15744 | 13792 | 15000 | 14673 | 16654 | 17572 | 17243 | 17304 | 16272 | 17928 | 18098 | 19141 | 18826 | 17625 | 17209 | 19302 | 19572 | 20071 | 20316 | 18847
2583 | 2583 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 15 | 15720 | 13615 | 14868 | 14710 | 16617 | 17511 | 17141 | 17193 | 16121 | 17861 | 18078 | 19050 | 18679 | 17440 | 17202 | 19204 | 19508 | 19889 | 20076 | 18641
2584 | 2584 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 16 | 16022 | 13912 | 15113 | 15073 | 16961 | 17769 | 17344 | 17331 | 16323 | 18141 | 18687 | 19219 | 18761 | 17539 | 17439 | 19381 | 20083 | 19887 | 20005 | 18699
2585 | 2585 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 17 | 16538 | 14483 | 15425 | 15670 | 17517 | 18247 | 17841 | 17907 | 16699 | 18717 | 19363 | 19767 | 19208 | 17951 | 18067 | 19990 | 20797 | 20357 | 20405 | 19125
2586 | 2586 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 18 | 16969 | 14604 | 15745 | 16149 | 17964 | 18718 | 18550 | 18461 | 17244 | 19350 | 19811 | 20340 | 20234 | 18775 | 18901 | 20876 | 21385 | 21482 | 21300 | 20019
2587 | 2587 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 19 | 17029 | 14986 | 15988 | 16304 | 18075 | 18966 | 18726 | 18714 | 17730 | 19579 | 20168 | 20966 | 20904 | 19620 | 19612 | 21519 | 22015 | 22374 | 22308 | 21029
2588 | 2588 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 20 | 17618 | 15591 | 16576 | 16996 | 18583 | 19781 | 19521 | 19410 | 18616 | 20366 | 21129 | 22284 | 22252 | 20906 | 20939 | 22776 | 23446 | 23988 | 23756 | 22508
2589 | 2589 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 21 | 17342 | 15427 | 16444 | 16925 | 18437 | 19677 | 19674 | 19460 | 18838 | 20505 | 21505 | 22756 | 23046 | 21669 | 21629 | 23401 | 24331 | 25127 | 24731 | 23553
2590 | 2590 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 22 | 16337 | 14758 | 15781 | 16228 | 17506 | 18816 | 18819 | 18667 | 18368 | 19741 | 20824 | 22254 | 22580 | 21539 | 21380 | 22867 | 23942 | 24872 | 24535 | 23563
2591 | 2591 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 23 | 15173 | 13928 | 14961 | 15443 | 16452 | 17660 | 17741 | 17700 | 17630 | 18750 | 19807 | 21276 | 21698 | 20967 | 20789 | 22044 | 23098 | 24085 | 23789 | 23065
2592 | 2592 | 108 | 4 | 18 | Winter | 4 | 17 | Winter | 24 | 14342 | 13272 | 14359 | 14877 | 15764 | 16815 | 16982 | 16902 | 17062 | 18079 | 19023 | 20510 | 21060 | 20502 | 20304 | 21365 | 22398 | 23508 | 23189 | 22653
2593 | 2593 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 1 | 13574 | 13558 | 13779 | 14171 | 15135 | 16007 | 16132 | 16293 | 16051 | 17736 | 18791 | 19817 | 20416 | 18891 | 19252 | 21299 | 22340 | 23106 | 22272 | 20757
2594 | 2594 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 2 | 13316 | 13225 | 13576 | 14017 | 14859 | 15685 | 15658 | 15881 | 15796 | 17381 | 18424 | 19376 | 19974 | 18528 | 18941 | 20827 | 21845 | 22542 | 21656 | 20350
2595 | 2595 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 3 | 13276 | 13048 | 13453 | 13972 | 14743 | 15635 | 15483 | 15678 | 15666 | 17211 | 18237 | 19202 | 19627 | 18272 | 18778 | 20507 | 21523 | 22333 | 21223 | 20042
2596 | 2596 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 4 | 13386 | 13058 | 13392 | 14114 | 14852 | 15643 | 15365 | 15533 | 15457 | 17117 | 18003 | 18840 | 19170 | 17775 | 18524 | 20058 | 20953 | 21881 | 20499 | 19391
2597 | 2597 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 5 | 13916 | 13368 | 13652 | 14703 | 15386 | 16098 | 15428 | 15665 | 15603 | 17427 | 18177 | 18909 | 19061 | 17553 | 18614 | 19824 | 20598 | 21253 | 19953 | 18995
2598 | 2598 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 6 | 14967 | 13854 | 13939 | 15699 | 16448 | 17049 | 15652 | 15929 | 15666 | 18159 | 18846 | 19387 | 19367 | 17238 | 19065 | 20097 | 20790 | 20602 | 19431 | 18500
2599 | 2599 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 7 | 15957 | 14150 | 14077 | 16831 | 17487 | 17941 | 15575 | 15997 | 15468 | 18864 | 19538 | 19812 | 19885 | 16799 | 19739 | 20442 | 21065 | 19893 | 18842 | 17937
2600 | 2600 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 8 | 16200 | 14321 | 14019 | 17193 | 17691 | 18159 | 15736 | 16034 | 15239 | 18911 | 19543 | 19799 | 19963 | 16439 | 19926 | 20279 | 20917 | 19749 | 18604 | 17516
2601 | 2601 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 9 | 15800 | 14480 | 13956 | 16810 | 17302 | 17638 | 15590 | 16027 | 15020 | 18419 | 18873 | 19138 | 19489 | 16129 | 19295 | 19691 | 20218 | 19362 | 18412 | 17164
2602 | 2602 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 10 | 15422 | 14641 | 14102 | 16560 | 17017 | 17220 | 15440 | 16198 | 15174 | 18182 | 18591 | 18765 | 19289 | 16336 | 19072 | 19592 | 20078 | 18929 | 18693 | 17429
2603 | 2603 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 11 | 15324 | 14804 | 14362 | 16514 | 16915 | 17144 | 15563 | 16398 | 15481 | 18166 | 18527 | 18778 | 19217 | 16706 | 19112 | 19673 | 20091 | 18940 | 19010 | 17847
2604 | 2604 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 12 | 15172 | 14760 | 14498 | 16425 | 16727 | 17009 | 15546 | 16381 | 15657 | 18001 | 18436 | 18690 | 19054 | 16901 | 19006 | 19533 | 20032 | 18944 | 19042 | 18058
2605 | 2605 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 13 | 15076 | 14598 | 14559 | 16390 | 16575 | 16879 | 15365 | 16212 | 15730 | 17834 | 18330 | 18562 | 18884 | 16962 | 18908 | 19356 | 19934 | 18735 | 18867 | 18115
2606 | 2606 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 14 | 14948 | 14375 | 14438 | 16293 | 16481 | 16743 | 15171 | 15948 | 15589 | 17709 | 18180 | 18379 | 18632 | 16792 | 18714 | 19185 | 19743 | 18434 | 18541 | 17925
2607 | 2607 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 15 | 14912 | 14270 | 14508 | 16266 | 16513 | 16689 | 15005 | 15837 | 15629 | 17734 | 18158 | 18277 | 18501 | 16825 | 18643 | 19158 | 19659 | 18166 | 18372 | 17942
2608 | 2608 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 16 | 15246 | 14605 | 14966 | 16609 | 17141 | 16998 | 15331 | 16133 | 16041 | 18434 | 18407 | 18464 | 18604 | 17169 | 18885 | 19826 | 19795 | 18297 | 18526 | 18256
2609 | 2609 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 17 | 15783 | 14944 | 15569 | 17163 | 17836 | 17516 | 15934 | 16532 | 16611 | 19120 | 18963 | 18940 | 19121 | 17812 | 19572 | 20570 | 20407 | 19081 | 18967 | 18911
2610 | 2610 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 18 | 16259 | 15254 | 16018 | 17681 | 18156 | 18233 | 16370 | 17049 | 17326 | 19574 | 19415 | 19950 | 19986 | 18670 | 20521 | 21182 | 21061 | 19911 | 19898 | 19837
2611 | 2611 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 19 | 16319 | 15502 | 16172 | 17929 | 18239 | 18400 | 16924 | 17498 | 17725 | 19885 | 19941 | 20574 | 20660 | 19370 | 21142 | 21807 | 21951 | 20907 | 20929 | 20664
2612 | 2612 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 20 | 16832 | 16055 | 16829 | 18347 | 18840 | 19152 | 17700 | 18297 | 18610 | 20747 | 21076 | 21828 | 21848 | 20644 | 22227 | 23192 | 23472 | 22280 | 22406 | 22088
2613 | 2613 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 21 | 16684 | 15882 | 16707 | 18210 | 18713 | 19222 | 17717 | 18403 | 18765 | 20988 | 21584 | 22489 | 22448 | 21249 | 22908 | 23986 | 24528 | 23281 | 23411 | 22911
2614 | 2614 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 22 | 15697 | 15171 | 15980 | 17171 | 17736 | 18330 | 17184 | 17877 | 18206 | 20227 | 20978 | 21957 | 22022 | 20955 | 22280 | 23574 | 24256 | 23350 | 23412 | 22727
2615 | 2615 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 23 | 14613 | 14359 | 15193 | 16011 | 16591 | 17257 | 16363 | 17121 | 17467 | 19191 | 19960 | 21047 | 21256 | 20355 | 21221 | 22721 | 23419 | 22835 | 22927 | 22186
2616 | 2616 | 109 | 4 | 19 | Winter | 4 | 18 | Winter | 24 | 13835 | 13761 | 14612 | 15168 | 15725 | 16485 | 15724 | 16519 | 16914 | 18385 | 19120 | 20373 | 20555 | 19856 | 20380 | 22005 | 22677 | 22476 | 22511 | 21720
2617 | 2617 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 1 | 12927 | 13135 | 13907 | 14742 | 15160 | 15425 | 15712 | 15468 | 16033 | 18017 | 18374 | 19235 | 19592 | 18923 | 20766 | 21804 | 21988 | 21979 | 20525 | 20597
2618 | 2618 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 2 | 12666 | 12945 | 13750 | 14486 | 14899 | 15102 | 15323 | 15233 | 15872 | 17694 | 17950 | 18790 | 19058 | 18626 | 20322 | 21334 | 21437 | 21380 | 20128 | 20260
2619 | 2619 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 3 | 12562 | 12835 | 13700 | 14380 | 14806 | 14963 | 15140 | 15123 | 15804 | 17554 | 17761 | 18509 | 18733 | 18419 | 20029 | 21028 | 21103 | 20963 | 19833 | 20056
2620 | 2620 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 4 | 12655 | 12793 | 13861 | 14506 | 14862 | 14960 | 15040 | 14957 | 15817 | 17392 | 17503 | 18132 | 18247 | 18178 | 19621 | 20494 | 20502 | 20249 | 19188 | 19690
2621 | 2621 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 5 | 13179 | 13045 | 14475 | 15061 | 15390 | 15430 | 15226 | 15153 | 16238 | 17658 | 17696 | 18177 | 17975 | 18269 | 19439 | 20187 | 20114 | 19724 | 18802 | 19677
2622 | 2622 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 6 | 14216 | 13367 | 15619 | 16159 | 16488 | 16317 | 15566 | 15291 | 17013 | 18418 | 18230 | 18551 | 17755 | 18794 | 19762 | 20424 | 20182 | 19224 | 18312 | 19943
2623 | 2623 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 7 | 15380 | 13523 | 16842 | 17264 | 17530 | 17363 | 15701 | 15194 | 17912 | 19183 | 18966 | 19167 | 17389 | 19447 | 20143 | 20755 | 20627 | 18643 | 17749 | 20445
2624 | 2624 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 8 | 15782 | 13581 | 17274 | 17596 | 17842 | 17729 | 15868 | 15109 | 18304 | 19323 | 19099 | 19349 | 17358 | 19668 | 20102 | 20728 | 20606 | 18512 | 17426 | 20666
2625 | 2625 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 9 | 15836 | 13907 | 17261 | 17608 | 17737 | 17726 | 16272 | 15313 | 18263 | 19052 | 18857 | 19257 | 17632 | 19454 | 19904 | 20427 | 20370 | 18705 | 17455 | 20383
2626 | 2626 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 10 | 15910 | 14372 | 17307 | 17619 | 17703 | 17798 | 16727 | 15766 | 18358 | 19055 | 18781 | 19398 | 18136 | 19596 | 20089 | 20570 | 20435 | 19270 | 18007 | 20544
2627 | 2627 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 11 | 15979 | 14746 | 17362 | 17632 | 17700 | 17855 | 17033 | 16188 | 18494 | 19098 | 18843 | 19536 | 18525 | 19765 | 20280 | 20703 | 20591 | 19707 | 18537 | 20768
2628 | 2628 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 12 | 15826 | 14800 | 17177 | 17374 | 17510 | 17695 | 16939 | 16289 | 18352 | 18935 | 18788 | 19404 | 18470 | 19630 | 20069 | 20578 | 20567 | 19666 | 18680 | 20667
2629 | 2629 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 13 | 15617 | 14727 | 16993 | 17082 | 17280 | 17457 | 16637 | 16219 | 18184 | 18697 | 18730 | 19159 | 18164 | 19450 | 19760 | 20336 | 20506 | 19349 | 18603 | 20501
2630 | 2630 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 14 | 15524 | 14654 | 16894 | 17035 | 17205 | 17330 | 16421 | 16128 | 18090 | 18597 | 18614 | 18974 | 17901 | 19311 | 19637 | 20191 | 20332 | 19066 | 18461 | 20388
2631 | 2631 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 15 | 15492 | 14725 | 16861 | 17102 | 17222 | 17263 | 16330 | 16203 | 18042 | 18597 | 18544 | 18853 | 17765 | 19219 | 19630 | 20141 | 20189 | 18914 | 18492 | 20313
2632 | 2632 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 16 | 15789 | 15179 | 17171 | 17685 | 17546 | 17507 | 16617 | 16609 | 18304 | 18842 | 18717 | 18966 | 17959 | 19396 | 20286 | 20270 | 20235 | 19048 | 18787 | 20489
2633 | 2633 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 17 | 16030 | 15578 | 17457 | 18179 | 17852 | 17747 | 16811 | 16968 | 18681 | 19195 | 18886 | 19219 | 18187 | 19761 | 20826 | 20677 | 20511 | 19285 | 19239 | 20901
2634 | 2634 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 18 | 15926 | 15619 | 17475 | 18142 | 17882 | 17820 | 16926 | 17269 | 19046 | 19264 | 19201 | 19588 | 18678 | 20228 | 21074 | 20976 | 20980 | 19871 | 19812 | 21508
2635 | 2635 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 19 | 15775 | 15543 | 17632 | 17990 | 17857 | 17817 | 17121 | 17409 | 19251 | 19500 | 19561 | 19995 | 19290 | 20863 | 21443 | 21607 | 21682 | 20692 | 20429 | 22092
2636 | 2636 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 20 | 16147 | 16171 | 18041 | 18556 | 18544 | 18370 | 17866 | 18232 | 19830 | 20537 | 20681 | 21023 | 20500 | 21813 | 22772 | 23093 | 23216 | 22159 | 21852 | 23183
2637 | 2637 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 21 | 15863 | 15974 | 17787 | 18357 | 18493 | 18284 | 17873 | 18290 | 19904 | 20903 | 21102 | 21517 | 21109 | 22237 | 23485 | 24059 | 24162 | 23113 | 22645 | 23879
2638 | 2638 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 22 | 14919 | 15268 | 16738 | 17374 | 17581 | 17460 | 17336 | 17709 | 19018 | 20247 | 20442 | 21043 | 20940 | 21595 | 23072 | 23786 | 23821 | 23142 | 22493 | 23376
2639 | 2639 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 23 | 13866 | 14478 | 15508 | 16222 | 16399 | 16416 | 16556 | 16940 | 17896 | 19186 | 19418 | 20164 | 20348 | 20536 | 22182 | 22920 | 22982 | 22656 | 21949 | 22445
2640 | 2640 | 110 | 4 | 20 | Winter | 4 | 19 | Winter | 24 | 13068 | 13930 | 14647 | 15369 | 15502 | 15602 | 15949 | 16382 | 17064 | 18335 | 18708 | 19448 | 19867 | 19738 | 21459 | 22178 | 22347 | 22242 | 21494 | 21699
2641 | 2641 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 1 | 12748 | 13216 | 14342 | 14791 | 14649 | 15120 | 14965 | 15760 | 16912 | 17569 | 18404 | 18842 | 18232 | 20136 | 21221 | 21478 | 22105 | 20250 | 20494 | 22199
2642 | 2642 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 2 | 12445 | 13018 | 14099 | 14530 | 14318 | 14731 | 14729 | 15577 | 16586 | 17164 | 17981 | 18324 | 17889 | 19702 | 20757 | 20927 | 21555 | 19845 | 20148 | 21715
2643 | 2643 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 3 | 12283 | 13006 | 13990 | 14428 | 14208 | 14544 | 14615 | 15581 | 16441 | 17006 | 17778 | 18019 | 17661 | 19427 | 20467 | 20603 | 21198 | 19544 | 19881 | 21365
2644 | 2644 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 4 | 12316 | 13173 | 14134 | 14504 | 14264 | 14483 | 14489 | 15631 | 16417 | 16830 | 17468 | 17604 | 17221 | 19076 | 19983 | 20040 | 20531 | 18919 | 19510 | 20844
2645 | 2645 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 5 | 12621 | 13607 | 14672 | 15037 | 14736 | 14681 | 14701 | 16116 | 16777 | 17092 | 17520 | 17399 | 17039 | 18929 | 19706 | 19679 | 20065 | 18525 | 19420 | 20494
2646 | 2646 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 6 | 13121 | 14492 | 15791 | 16173 | 15690 | 15082 | 14916 | 16909 | 17600 | 17742 | 17805 | 17276 | 16794 | 19325 | 20010 | 19791 | 19902 | 18065 | 19805 | 20679
2647 | 2647 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 7 | 13512 | 15373 | 17013 | 17320 | 16879 | 15334 | 14952 | 17850 | 18447 | 18634 | 18389 | 17055 | 16473 | 19825 | 20459 | 20331 | 20094 | 17584 | 20418 | 21015
2648 | 2648 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 8 | 14057 | 16213 | 17641 | 17922 | 17441 | 15786 | 15161 | 18489 | 18891 | 19074 | 18733 | 17331 | 16492 | 20077 | 20724 | 20596 | 20221 | 17534 | 20857 | 21153
2649 | 2649 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 9 | 14804 | 16812 | 17896 | 18029 | 17521 | 16418 | 15601 | 18591 | 19004 | 19053 | 18782 | 17821 | 16775 | 20100 | 20647 | 20555 | 20244 | 17776 | 20808 | 21103
2650 | 2650 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 10 | 15310 | 17119 | 17982 | 18062 | 17512 | 16925 | 16109 | 18677 | 19107 | 19022 | 18995 | 18374 | 17317 | 20335 | 20844 | 20678 | 20598 | 18378 | 21053 | 21396
2651 | 2651 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 11 | 15415 | 17158 | 17810 | 17850 | 17338 | 17030 | 16331 | 18557 | 19018 | 18876 | 19097 | 18556 | 17612 | 20328 | 20780 | 20629 | 20806 | 18713 | 21071 | 21443
2652 | 2652 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 12 | 15261 | 16990 | 17515 | 17618 | 17212 | 16890 | 16387 | 18428 | 18739 | 18786 | 19063 | 18455 | 17696 | 20075 | 20620 | 20563 | 20801 | 18815 | 20911 | 21223
2653 | 2653 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 13 | 15137 | 16982 | 17396 | 17557 | 17327 | 16759 | 16487 | 18477 | 18608 | 18903 | 19072 | 18320 | 17791 | 19940 | 20550 | 20677 | 20799 | 18909 | 20901 | 21083
2654 | 2654 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 14 | 14994 | 16949 | 17382 | 17521 | 17300 | 16577 | 16430 | 18445 | 18563 | 18829 | 19001 | 18101 | 17703 | 19852 | 20440 | 20546 | 20679 | 18798 | 20774 | 20971
2655 | 2655 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 15 | 14765 | 16815 | 17308 | 17408 | 17147 | 16349 | 16367 | 18309 | 18471 | 18625 | 18808 | 17841 | 17615 | 19710 | 20253 | 20273 | 20423 | 18689 | 20525 | 20808
2656 | 2656 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 16 | 14850 | 16982 | 17597 | 17506 | 17223 | 16421 | 16554 | 18432 | 18922 | 18597 | 18692 | 17821 | 17725 | 20152 | 20166 | 20101 | 20178 | 18757 | 20446 | 21199
2657 | 2657 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 17 | 14916 | 17294 | 18026 | 17746 | 17372 | 16552 | 16845 | 18760 | 19332 | 18695 | 18739 | 17978 | 18089 | 20626 | 20506 | 20305 | 20208 | 19142 | 20760 | 21692
2658 | 2658 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 18 | 14791 | 17240 | 17924 | 17698 | 17363 | 16584 | 17041 | 18983 | 19354 | 18906 | 18926 | 18348 | 18514 | 20783 | 20727 | 20694 | 20589 | 19654 | 21216 | 21939
2659 | 2659 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 19 | 14757 | 17039 | 17682 | 17571 | 17268 | 16682 | 17080 | 18960 | 19339 | 19122 | 19146 | 18825 | 18901 | 21050 | 21247 | 21301 | 21230 | 20202 | 21905 | 22365
2660 | 2660 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 20 | 15255 | 17432 | 18168 | 18173 | 17930 | 17345 | 17818 | 19649 | 20082 | 20092 | 20105 | 19913 | 20080 | 22274 | 22628 | 22747 | 22628 | 21586 | 22942 | 23806
2661 | 2661 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 21 | 15055 | 17138 | 17954 | 18103 | 17880 | 17317 | 17839 | 19606 | 20218 | 20410 | 20533 | 20447 | 20612 | 22929 | 23548 | 23670 | 23609 | 22384 | 23580 | 24729
2662 | 2662 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 22 | 14330 | 16148 | 16917 | 17144 | 16913 | 16722 | 17199 | 18680 | 19410 | 19648 | 20053 | 20196 | 20288 | 22443 | 23205 | 23289 | 23462 | 22203 | 23035 | 24370
2663 | 2663 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 23 | 13523 | 15119 | 15760 | 15960 | 15776 | 15937 | 16419 | 17689 | 18343 | 18589 | 19243 | 19579 | 19671 | 21541 | 22324 | 22432 | 22821 | 21657 | 22040 | 23541
2664 | 2664 | 111 | 4 | 21 | Winter | 4 | 20 | Winter | 24 | 12948 | 14435 | 14908 | 15073 | 14986 | 15329 | 15856 | 16924 | 17532 | 17865 | 18607 | 19079 | 19175 | 20809 | 21574 | 21796 | 22287 | 21205 | 21277 | 22850
2665 | 2665 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 1 | 12297 | 13565 | 14275 | 14147 | 14585 | 14363 | 14993 | 16207 | 17053 | 17504 | 17209 | 17479 | 18427 | 20489 | 20805 | 21478 | 20746 | 20569 | 21847 | 22657
2666 | 2666 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 2 | 12108 | 13347 | 14036 | 13824 | 14264 | 14137 | 14777 | 15902 | 16746 | 17115 | 16678 | 17157 | 18145 | 20045 | 20273 | 20942 | 20188 | 20309 | 21371 | 22169
2667 | 2667 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 3 | 11995 | 13267 | 13939 | 13718 | 14152 | 14023 | 14781 | 15770 | 16620 | 16950 | 16373 | 16954 | 18054 | 19779 | 19970 | 20604 | 19697 | 20345 | 21019 | 21834
2668 | 2668 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 4 | 11953 | 13389 | 14018 | 13781 | 14150 | 13913 | 14861 | 15786 | 16515 | 16708 | 15956 | 16559 | 17821 | 19336 | 19442 | 19963 | 18877 | 20254 | 20500 | 21218
2669 | 2669 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 5 | 12207 | 13941 | 14574 | 14291 | 14575 | 14166 | 15242 | 16223 | 16855 | 16872 | 15691 | 16461 | 18019 | 19136 | 19151 | 19559 | 18063 | 20186 | 20177 | 20802
2670 | 2670 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 6 | 12554 | 15058 | 15712 | 15288 | 15304 | 14414 | 15960 | 17120 | 17703 | 17258 | 15432 | 16298 | 18427 | 19500 | 19313 | 19439 | 17320 | 20310 | 20368 | 20934
2671 | 2671 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 7 | 12785 | 16308 | 16848 | 16483 | 16209 | 14460 | 16695 | 18026 | 18588 | 17903 | 15426 | 16018 | 19021 | 19979 | 19869 | 19638 | 16990 | 20502 | 20684 | 21212
2672 | 2672 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 8 | 13065 | 16899 | 17394 | 16989 | 16648 | 14613 | 17437 | 18464 | 18975 | 18223 | 16051 | 16006 | 19452 | 20208 | 20087 | 19722 | 17481 | 20971 | 20764 | 21304
2673 | 2673 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 9 | 13493 | 17065 | 17424 | 16980 | 16773 | 14967 | 17809 | 18524 | 18835 | 18184 | 16555 | 16210 | 19329 | 20046 | 19957 | 19654 | 17988 | 21124 | 20614 | 21056
2674 | 2674 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 10 | 13797 | 16916 | 17228 | 16750 | 16746 | 15224 | 17869 | 18391 | 18666 | 18137 | 16854 | 16505 | 19208 | 19992 | 19830 | 19766 | 18523 | 20888 | 20660 | 21058
2675 | 2675 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 11 | 13875 | 16651 | 16922 | 16470 | 16676 | 15336 | 17824 | 18189 | 18408 | 18122 | 16989 | 16684 | 19023 | 19820 | 19673 | 19861 | 18785 | 20698 | 20608 | 20934
2676 | 2676 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 12 | 13784 | 16289 | 16610 | 16271 | 16503 | 15304 | 17607 | 17827 | 18107 | 18007 | 16873 | 16686 | 18815 | 19562 | 19525 | 19776 | 18697 | 20497 | 20303 | 20711
2677 | 2677 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 13 | 13766 | 16072 | 16438 | 16280 | 16394 | 15288 | 17490 | 17587 | 17924 | 17905 | 16705 | 16673 | 18738 | 19386 | 19519 | 19666 | 18511 | 20358 | 20050 | 20525
2678 | 2678 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 14 | 13698 | 16016 | 16382 | 16240 | 16345 | 15212 | 17421 | 17522 | 17838 | 17821 | 16559 | 16569 | 18656 | 19260 | 19372 | 19529 | 18256 | 20201 | 19914 | 20376
2679 | 2679 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 15 | 13693 | 16000 | 16332 | 16152 | 16276 | 15215 | 17343 | 17495 | 17773 | 17699 | 16572 | 16548 | 18555 | 19140 | 19168 | 19338 | 18202 | 20052 | 19818 | 20240
2680 | 2680 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 16 | 14175 | 16493 | 16680 | 16482 | 16530 | 15652 | 17741 | 18148 | 18056 | 17848 | 16797 | 16914 | 18858 | 19309 | 19253 | 19347 | 18326 | 20342 | 20459 | 20368
2681 | 2681 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 17 | 14687 | 17073 | 17097 | 16813 | 16761 | 16116 | 18228 | 18738 | 18525 | 18064 | 17287 | 17457 | 19392 | 19818 | 19628 | 19557 | 18873 | 20950 | 21113 | 20901
2682 | 2682 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 18 | 14759 | 17082 | 17178 | 16895 | 16798 | 16425 | 18483 | 18869 | 18631 | 18337 | 17593 | 17966 | 19976 | 20150 | 20133 | 20070 | 19318 | 21542 | 21490 | 21324
2683 | 2683 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 19 | 14699 | 16934 | 17130 | 16867 | 16829 | 16551 | 18440 | 18896 | 18833 | 18583 | 17772 | 18400 | 20360 | 20730 | 20803 | 20767 | 19723 | 21919 | 22020 | 22089
2684 | 2684 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 20 | 15286 | 17398 | 17711 | 17504 | 17314 | 17279 | 19030 | 19583 | 19756 | 19453 | 18354 | 19521 | 21453 | 22066 | 22227 | 22135 | 20785 | 22826 | 23476 | 23655
2685 | 2685 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 21 | 15085 | 17161 | 17616 | 17421 | 17236 | 17269 | 18943 | 19642 | 20045 | 19772 | 18703 | 19974 | 21869 | 22915 | 23096 | 23075 | 21647 | 23489 | 24397 | 24802
2686 | 2686 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 22 | 14322 | 16103 | 16623 | 16419 | 16434 | 16602 | 18047 | 18760 | 19282 | 19209 | 18289 | 19585 | 21203 | 22515 | 22658 | 22889 | 21538 | 23035 | 24030 | 24564
2687 | 2687 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 23 | 13517 | 14949 | 15433 | 15279 | 15487 | 15824 | 17013 | 17662 | 18185 | 18361 | 17603 | 18940 | 20335 | 21603 | 21782 | 22221 | 20998 | 22191 | 23216 | 23730
2688 | 2688 | 112 | 4 | 22 | Winter | 4 | 21 | Winter | 24 | 12974 | 14081 | 14530 | 14476 | 14766 | 15247 | 16300 | 16817 | 17322 | 17691 | 16975 | 18412 | 19638 | 20825 | 21120 | 21654 | 20482 | 21676 | 22511 | 22999
2689 | 2689 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 1 | 12253 | 13577 | 13735 | 14209 | 13655 | 14417 | 15689 | 16440 | 16581 | 16470 | 16645 | 17419 | 19324 | 20149 | 21432 | 20242 | 19628 | 21574 | 22410 | 22396
2690 | 2690 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 2 | 12094 | 13302 | 13400 | 13860 | 13211 | 14201 | 15358 | 16116 | 16172 | 15939 | 16214 | 17113 | 18885 | 19602 | 20869 | 19667 | 19081 | 21067 | 21889 | 21799
2691 | 2691 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 3 | 12114 | 13233 | 13326 | 13785 | 13020 | 14205 | 15261 | 16034 | 16069 | 15694 | 15983 | 17027 | 18657 | 19349 | 20737 | 19216 | 18731 | 20757 | 21579 | 21472
2692 | 2692 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 4 | 12287 | 13336 | 13414 | 13821 | 12914 | 14346 | 15332 | 16002 | 15960 | 15366 | 15732 | 16909 | 18363 | 18888 | 20408 | 18451 | 18203 | 20257 | 20985 | 20816
2693 | 2693 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 5 | 12899 | 13872 | 13881 | 14197 | 12990 | 14926 | 15720 | 16291 | 16319 | 15068 | 15543 | 17170 | 18304 | 18662 | 19910 | 17676 | 17687 | 19953 | 20580 | 20369
2694 | 2694 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 6 | 14008 | 15033 | 14928 | 14986 | 13222 | 15912 | 16687 | 17224 | 17084 | 14902 | 15369 | 17759 | 18790 | 18917 | 19434 | 17011 | 17129 | 20192 | 20751 | 20397
2695 | 2695 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 7 | 15249 | 16143 | 16082 | 15858 | 13583 | 16954 | 17583 | 18094 | 17961 | 14889 | 15151 | 18463 | 19260 | 19448 | 18796 | 16643 | 16593 | 20454 | 20969 | 20780
2696 | 2696 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 8 | 15687 | 16427 | 16341 | 16040 | 14113 | 17344 | 17809 | 18254 | 18115 | 15296 | 15074 | 18721 | 19226 | 19430 | 18736 | 16883 | 16442 | 20292 | 20812 | 20688
2697 | 2697 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 9 | 15523 | 16273 | 16135 | 15969 | 14489 | 17140 | 17706 | 17961 | 17751 | 15640 | 15179 | 18381 | 18908 | 19064 | 18599 | 17158 | 16487 | 19916 | 20327 | 20285
2698 | 2698 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 10 | 15334 | 16052 | 15894 | 15908 | 14688 | 16940 | 17554 | 17775 | 17418 | 15936 | 15512 | 18234 | 18832 | 18862 | 18191 | 17614 | 16890 | 19887 | 20260 | 20117
2699 | 2699 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 11 | 15286 | 15914 | 15785 | 15997 | 14905 | 16902 | 17503 | 17680 | 17319 | 16234 | 15832 | 18264 | 18873 | 18847 | 18160 | 18027 | 17272 | 19979 | 20284 | 20148
2700 | 2700 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 12 | 15166 | 15743 | 15730 | 15985 | 14882 | 16778 | 17277 | 17532 | 17284 | 16254 | 15959 | 18165 | 18672 | 18835 | 18109 | 18083 | 17415 | 19795 | 20199 | 20164
2701 | 2701 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 13 | 15039 | 15551 | 15720 | 15858 | 14699 | 16650 | 17015 | 17331 | 17272 | 16066 | 15912 | 18037 | 18409 | 18808 | 17800 | 17879 | 17367 | 19518 | 19990 | 20138
2702 | 2702 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 14 | 14914 | 15412 | 15603 | 15735 | 14490 | 16529 | 16873 | 17167 | 17095 | 15833 | 15805 | 17884 | 18210 | 18589 | 17483 | 17541 | 17220 | 19305 | 19761 | 19890
2703 | 2703 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 15 | 14907 | 15403 | 15570 | 15706 | 14597 | 16490 | 16891 | 17140 | 17022 | 15896 | 15871 | 17813 | 18198 | 18448 | 17224 | 17542 | 17266 | 19266 | 19682 | 19720
2704 | 2704 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 16 | 15211 | 15687 | 15855 | 15906 | 14851 | 16760 | 17454 | 17366 | 17203 | 16069 | 16246 | 18009 | 18829 | 18498 | 17332 | 17611 | 17568 | 19858 | 19758 | 19706
2705 | 2705 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 17 | 15712 | 16193 | 16255 | 16205 | 15389 | 17270 | 18133 | 17916 | 17536 | 16653 | 16987 | 18566 | 19536 | 18936 | 18086 | 18212 | 18325 | 20582 | 20349 | 20149
2706 | 2706 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 18 | 16018 | 16478 | 16472 | 16422 | 15587 | 17773 | 18457 | 18221 | 18048 | 17121 | 17797 | 19317 | 20021 | 19625 | 18805 | 18859 | 19358 | 21145 | 20962 | 20915
2707 | 2707 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 19 | 16174 | 16553 | 16559 | 16577 | 15588 | 18073 | 18589 | 18514 | 18446 | 17367 | 18242 | 19891 | 20479 | 20401 | 19694 | 19387 | 20084 | 21826 | 21874 | 21864
2708 | 2708 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 20 | 16494 | 17090 | 17175 | 17033 | 15843 | 18530 | 19235 | 19372 | 19364 | 17867 | 18953 | 20720 | 21682 | 21771 | 20933 | 20429 | 21089 | 23282 | 23451 | 23444
2709 | 2709 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 21 | 16294 | 16961 | 17061 | 16915 | 15706 | 18476 | 19224 | 19569 | 19608 | 18097 | 19458 | 21102 | 22275 | 22560 | 21791 | 21244 | 22022 | 24187 | 24585 | 24515
2710 | 2710 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 22 | 15211 | 15932 | 16031 | 16091 | 14993 | 17472 | 18294 | 18749 | 18773 | 17601 | 18964 | 20358 | 21723 | 22073 | 21790 | 21107 | 21799 | 23812 | 24336 | 24172
2711 | 2711 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 23 | 14073 | 14749 | 14905 | 15177 | 14204 | 16353 | 17201 | 17656 | 17705 | 16905 | 18150 | 19351 | 20817 | 21195 | 21247 | 20583 | 21116 | 23010 | 23544 | 23374
2712 | 2712 | 113 | 4 | 23 | Winter | 4 | 22 | Winter | 24 | 13234 | 13845 | 14097 | 14437 | 13489 | 15489 | 16341 | 16752 | 16946 | 16254 | 17583 | 18538 | 20054 | 20516 | 20839 | 20034 | 20632 | 22297 | 22809 | 22748
2713 | 2713 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 1 | 13222 | 13454 | 14236 | 13760 | 14054 | 15584 | 16302 | 16404 | 17103 | 16424 | 17078 | 19073 | 20203 | 20687 | 20133 | 19634 | 20005 | 22566 | 22589 | 22955
2714 | 2714 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 2 | 13005 | 13175 | 13945 | 13358 | 13724 | 15293 | 16029 | 16047 | 16723 | 16055 | 16853 | 18683 | 19777 | 20185 | 19610 | 19129 | 19667 | 22079 | 22022 | 22398
2715 | 2715 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 3 | 12959 | 13063 | 13849 | 13142 | 13533 | 15179 | 15926 | 15934 | 16596 | 15831 | 16783 | 18460 | 19540 | 19899 | 19154 | 18767 | 19485 | 21749 | 21675 | 22034
2716 | 2716 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 4 | 13087 | 13148 | 13889 | 13047 | 13505 | 15270 | 15927 | 15876 | 16436 | 15630 | 16732 | 18222 | 19169 | 19364 | 18424 | 18259 | 19172 | 21167 | 21019 | 21294
2717 | 2717 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 5 | 13588 | 13629 | 14286 | 13075 | 13644 | 15699 | 16275 | 16191 | 16557 | 15512 | 17093 | 18235 | 19037 | 19079 | 17700 | 17773 | 19179 | 20781 | 20581 | 20781
2718 | 2718 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 6 | 14680 | 14674 | 15076 | 13293 | 13787 | 16679 | 17244 | 16991 | 16992 | 15372 | 17813 | 18766 | 19460 | 19073 | 17052 | 17206 | 19560 | 20939 | 20582 | 20543
2719 | 2719 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 7 | 15842 | 15826 | 15966 | 13651 | 13840 | 17603 | 18153 | 17902 | 17584 | 15194 | 18604 | 19279 | 19887 | 19265 | 16698 | 16660 | 20105 | 21151 | 20938 | 20576
2720 | 2720 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 8 | 16100 | 16024 | 16076 | 14095 | 13847 | 17769 | 18261 | 18001 | 17592 | 15067 | 18816 | 19198 | 19802 | 19047 | 16865 | 16432 | 20213 | 20932 | 20757 | 20279
2721 | 2721 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 9 | 15869 | 15640 | 15847 | 14356 | 13925 | 17499 | 17809 | 17554 | 17217 | 15018 | 18299 | 18738 | 19246 | 18574 | 16968 | 16326 | 19623 | 20276 | 20170 | 19760
2722 | 2722 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 10 | 15681 | 15426 | 15824 | 14614 | 14200 | 17354 | 17632 | 17301 | 17168 | 15364 | 18100 | 18667 | 19117 | 18625 | 17438 | 16732 | 19466 | 20220 | 20023 | 19851
2723 | 2723 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 11 | 15556 | 15287 | 15880 | 14795 | 14436 | 17242 | 17490 | 17169 | 17293 | 15638 | 18051 | 18650 | 19077 | 18808 | 17805 | 17067 | 19494 | 20205 | 20013 | 20084
2724 | 2724 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 12 | 15422 | 15322 | 15942 | 14846 | 14606 | 17089 | 17407 | 17207 | 17400 | 15836 | 17956 | 18523 | 19031 | 18932 | 17933 | 17284 | 19425 | 20173 | 20101 | 20246
2725 | 2725 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 13 | 15289 | 15424 | 15925 | 14764 | 14665 | 16934 | 17315 | 17298 | 17380 | 15899 | 17866 | 18362 | 18931 | 18906 | 17839 | 17338 | 19330 | 20072 | 20182 | 20223
2726 | 2726 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 14 | 15184 | 15335 | 15830 | 14591 | 14629 | 16827 | 17179 | 17163 | 17258 | 15827 | 17687 | 18212 | 18763 | 18730 | 17535 | 17233 | 19131 | 19868 | 19962 | 20022
2727 | 2727 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 15 | 15214 | 15297 | 15807 | 14685 | 14714 | 16844 | 17157 | 17077 | 17174 | 15895 | 17627 | 18197 | 18700 | 18602 | 17537 | 17274 | 19038 | 19789 | 19791 | 19866
2728 | 2728 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 16 | 15677 | 15623 | 16068 | 14993 | 15204 | 17461 | 17445 | 17319 | 17325 | 16339 | 17914 | 18872 | 18870 | 18646 | 17669 | 17638 | 19241 | 19914 | 19832 | 19845
2729 | 2729 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 17 | 16372 | 16058 | 16398 | 15587 | 15892 | 18177 | 18034 | 17717 | 17673 | 17110 | 18543 | 19613 | 19479 | 18955 | 18308 | 18431 | 19945 | 20543 | 20316 | 20160
2730 | 2730 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 18 | 16640 | 16269 | 16583 | 15791 | 16567 | 18536 | 18359 | 18205 | 18166 | 17915 | 19394 | 20117 | 20038 | 19676 | 18980 | 19489 | 20913 | 21196 | 21115 | 20960
2731 | 2731 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 19 | 16619 | 16301 | 16683 | 15744 | 16734 | 18616 | 18583 | 18519 | 18479 | 18268 | 19789 | 20498 | 20695 | 20408 | 19436 | 20170 | 21587 | 22074 | 22044 | 21873
2732 | 2732 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 20 | 17069 | 16913 | 17103 | 15966 | 17132 | 19217 | 19387 | 19360 | 19274 | 18904 | 20642 | 21627 | 21990 | 21686 | 20436 | 21150 | 22764 | 23643 | 23632 | 23361
2733 | 2733 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 21 | 16803 | 16759 | 16945 | 15773 | 17241 | 19149 | 19502 | 19495 | 19485 | 19316 | 21027 | 22105 | 22744 | 22462 | 21178 | 22029 | 23561 | 24748 | 24682 | 24425
2734 | 2734 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 22 | 15726 | 15725 | 16096 | 15036 | 16516 | 18190 | 18637 | 18603 | 18860 | 18759 | 20199 | 21489 | 22292 | 22181 | 21005 | 21781 | 23006 | 24500 | 24347 | 24307
2735 | 2735 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 23 | 14555 | 14566 | 15126 | 14199 | 15541 | 17037 | 17477 | 17455 | 17963 | 17867 | 19014 | 20503 | 21335 | 21451 | 20419 | 21032 | 21960 | 23642 | 23505 | 23647
2736 | 2736 | 114 | 4 | 24 | Winter | 4 | 23 | Winter | 24 | 13686 | 13769 | 14403 | 13504 | 14921 | 16191 | 16574 | 16688 | 17268 | 17301 | 18146 | 19735 | 20534 | 20870 | 19874 | 20562 | 21121 | 22922 | 22895 | 23124
2737 | 2737 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 1 | 13063 | 13397 | 13248 | 13587 | 13997 | 15584 | 15673 | 16297 | 15965 | 16301 | 17855 | 19334 | 19727 | 19385 | 19028 | 19450 | 21188 | 22180 | 22589 | 21550
2738 | 2738 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 2 | 12845 | 13129 | 12861 | 13282 | 13842 | 15316 | 15325 | 15949 | 15496 | 16095 | 17428 | 18939 | 19244 | 18876 | 18541 | 19133 | 20659 | 21613 | 22027 | 20985
2739 | 2739 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 3 | 12734 | 13010 | 12640 | 13066 | 13805 | 15199 | 15203 | 15817 | 15231 | 16038 | 17233 | 18709 | 18972 | 18431 | 18175 | 18944 | 20216 | 21254 | 21651 | 20468
2740 | 2740 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 4 | 12838 | 13067 | 12570 | 13048 | 13976 | 15238 | 15199 | 15714 | 14964 | 16053 | 16991 | 18405 | 18568 | 17761 | 17711 | 18658 | 19615 | 20625 | 20930 | 19619
2741 | 2741 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 5 | 13362 | 13456 | 12593 | 13185 | 14575 | 15601 | 15543 | 15887 | 14721 | 16454 | 17183 | 18330 | 18390 | 17071 | 17241 | 18675 | 19612 | 20178 | 20401 | 18710
2742 | 2742 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 6 | 14509 | 14309 | 12870 | 13388 | 15628 | 16650 | 16445 | 16451 | 14626 | 17273 | 17970 | 18868 | 18706 | 16507 | 16740 | 19116 | 20082 | 20220 | 20194 | 17922
2743 | 2743 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 7 | 15673 | 15280 | 13343 | 13560 | 16845 | 17681 | 17489 | 17215 | 14722 | 18202 | 18883 | 19441 | 19328 | 16261 | 16288 | 19767 | 20596 | 20648 | 20277 | 17514
2744 | 2744 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 8 | 15987 | 15512 | 13923 | 13692 | 17339 | 17929 | 17722 | 17378 | 15191 | 18549 | 19022 | 19500 | 19370 | 16552 | 16176 | 19982 | 20511 | 20574 | 20082 | 17721
2745 | 2745 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 9 | 15832 | 15462 | 14370 | 13930 | 17099 | 17652 | 17453 | 17178 | 15540 | 18200 | 18594 | 19111 | 18995 | 16822 | 16234 | 19539 | 20021 | 20147 | 19721 | 17937
2746 | 2746 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 10 | 15577 | 15356 | 14567 | 14153 | 16786 | 17389 | 17127 | 17074 | 15799 | 17931 | 18403 | 18914 | 18753 | 17205 | 16555 | 19325 | 19980 | 19922 | 19732 | 18382
2747 | 2747 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 11 | 15341 | 15399 | 14729 | 14345 | 16595 | 17211 | 16967 | 17144 | 15975 | 17852 | 18382 | 18819 | 18620 | 17540 | 16869 | 19305 | 19927 | 19890 | 19944 | 18770
2748 | 2748 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 12 | 15145 | 15380 | 14689 | 14410 | 16374 | 17030 | 16905 | 17147 | 15971 | 17665 | 18275 | 18671 | 18581 | 17576 | 16989 | 19138 | 19802 | 19879 | 20004 | 18825
2749 | 2749 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 13 | 15020 | 15314 | 14546 | 14415 | 16235 | 16878 | 16935 | 17071 | 15844 | 17516 | 18207 | 18515 | 18617 | 17420 | 16983 | 18984 | 19728 | 19896 | 19932 | 18663
2750 | 2750 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 14 | 14932 | 15247 | 14403 | 14395 | 16117 | 16775 | 16836 | 16975 | 15681 | 17369 | 18099 | 18370 | 18462 | 17150 | 16903 | 18804 | 19596 | 19702 | 19757 | 18369
2751 | 2751 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 15 | 15027 | 15320 | 14598 | 14593 | 16195 | 16859 | 16861 | 17006 | 15845 | 17416 | 18151 | 18419 | 18429 | 17255 | 17052 | 18818 | 19612 | 19634 | 19703 | 18454
2752 | 2752 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 16 | 15320 | 15540 | 14860 | 15043 | 16514 | 17108 | 17071 | 17135 | 16040 | 17666 | 18733 | 18569 | 18501 | 17356 | 17373 | 18990 | 20165 | 19632 | 19638 | 18513
2753 | 2753 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 17 | 15888 | 15862 | 15448 | 15740 | 17184 | 17707 | 17474 | 17486 | 16663 | 18304 | 19290 | 19188 | 18981 | 18004 | 18179 | 19707 | 20683 | 20126 | 19965 | 19174
2754 | 2754 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 18 | 16160 | 15945 | 15520 | 16310 | 17760 | 17955 | 17848 | 17840 | 17081 | 19062 | 19621 | 19653 | 19622 | 18598 | 19155 | 20596 | 21146 | 20868 | 20697 | 19849
2755 | 2755 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 19 | 16142 | 15965 | 15396 | 16399 | 17801 | 18102 | 18071 | 18037 | 17193 | 19346 | 19874 | 20197 | 20272 | 18970 | 19758 | 21195 | 21784 | 21738 | 21568 | 20371
2756 | 2756 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 20 | 16635 | 16353 | 15554 | 16754 | 18310 | 18834 | 18832 | 18731 | 17588 | 20087 | 20782 | 21381 | 21564 | 19880 | 20677 | 22317 | 23109 | 23305 | 23041 | 21487
2757 | 2757 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 21 | 16427 | 16123 | 15296 | 16789 | 18269 | 18854 | 18863 | 18812 | 17675 | 20341 | 21189 | 21992 | 22219 | 20514 | 21478 | 23031 | 23979 | 24306 | 24066 | 22401
2758 | 2758 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 22 | 15390 | 15291 | 14552 | 16055 | 17244 | 17969 | 17946 | 18137 | 17136 | 19476 | 20272 | 21479 | 21688 | 20315 | 21210 | 22463 | 23374 | 23976 | 23957 | 22347
2759 | 2759 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 23 | 14157 | 14323 | 13708 | 15074 | 15986 | 16796 | 16779 | 17199 | 16361 | 18266 | 19034 | 20477 | 20739 | 19707 | 20456 | 21398 | 22275 | 23120 | 23291 | 21812
2760 | 2760 | 115 | 4 | 25 | Winter | 4 | 24 | Winter | 24 | 13282 | 13598 | 13011 | 14479 | 15079 | 15890 | 15998 | 16501 | 15711 | 17386 | 18069 | 19675 | 20059 | 19152 | 19971 | 20583 | 21392 | 22510 | 22769 | 21306
2761 | 2761 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 1 | 12749 | 12814 | 13498 | 13906 | 14757 | 15320 | 15950 | 15562 | 15805 | 17399 | 17905 | 19194 | 20074 | 18721 | 19851 | 20955 | 21353 | 22546 | 21560 | 20605
2762 | 2762 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 2 | 12490 | 12455 | 13208 | 13747 | 14417 | 14982 | 15611 | 15100 | 15458 | 16992 | 17493 | 18731 | 19593 | 18247 | 19611 | 20428 | 20845 | 21982 | 20994 | 20092
2763 | 2763 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 3 | 12376 | 12248 | 13006 | 13729 | 14313 | 14874 | 15502 | 14867 | 15246 | 16839 | 17305 | 18503 | 19333 | 17914 | 19679 | 20017 | 20406 | 21624 | 20494 | 19701
2764 | 2764 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 4 | 12467 | 12188 | 13001 | 13915 | 14356 | 14907 | 15451 | 14659 | 15100 | 16665 | 17054 | 18175 | 18867 | 17495 | 19685 | 19456 | 19796 | 20925 | 19649 | 19134
2765 | 2765 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 5 | 12932 | 12235 | 13166 | 14539 | 14931 | 15306 | 15696 | 14491 | 15024 | 16941 | 17126 | 18087 | 18639 | 17083 | 19694 | 19498 | 19605 | 20424 | 18758 | 18548
2766 | 2766 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 6 | 13992 | 12493 | 13370 | 15587 | 16104 | 16227 | 16309 | 14462 | 14960 | 17776 | 17707 | 18473 | 18716 | 16600 | 19893 | 19978 | 19808 | 20204 | 17947 | 17883
2767 | 2767 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 7 | 15246 | 13035 | 13614 | 16873 | 17414 | 17334 | 17172 | 14681 | 14946 | 18800 | 18664 | 19200 | 19063 | 16217 | 20141 | 20555 | 20442 | 20341 | 17570 | 17356
2768 | 2768 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 8 | 15783 | 13836 | 14008 | 17604 | 17988 | 17800 | 17591 | 15416 | 15189 | 19222 | 19109 | 19492 | 19208 | 16351 | 20631 | 20699 | 20676 | 20380 | 18009 | 17435
2769 | 2769 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 9 | 15736 | 14495 | 14467 | 17571 | 17930 | 17734 | 17610 | 15989 | 15509 | 19018 | 18991 | 19322 | 19094 | 16611 | 20732 | 20406 | 20316 | 20218 | 18421 | 17652
2770 | 2770 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 10 | 15611 | 14903 | 14874 | 17406 | 17834 | 17585 | 17679 | 16402 | 15935 | 18992 | 19025 | 19217 | 19213 | 17099 | 20529 | 20511 | 20474 | 20403 | 19037 | 18193
2771 | 2771 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 11 | 15397 | 14976 | 14978 | 17171 | 17660 | 17334 | 17650 | 16529 | 16117 | 18869 | 18980 | 19039 | 19295 | 17318 | 20328 | 20414 | 20565 | 20523 | 19334 | 18456
2772 | 2772 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 12 | 15352 | 14948 | 15044 | 16955 | 17528 | 17264 | 17645 | 16524 | 16224 | 18757 | 18810 | 19000 | 19330 | 17438 | 20240 | 20292 | 20438 | 20578 | 19389 | 18590
2773 | 2773 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 13 | 15326 | 14753 | 14997 | 16750 | 17389 | 17242 | 17514 | 16332 | 16160 | 18638 | 18690 | 18971 | 19171 | 17382 | 20072 | 20151 | 20297 | 20437 | 19176 | 18527
2774 | 2774 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 14 | 15192 | 14550 | 14913 | 16567 | 17247 | 17083 | 17360 | 16105 | 16049 | 18472 | 18403 | 18753 | 18960 | 17242 | 19831 | 19953 | 19976 | 20199 | 18819 | 18368
2775 | 2775 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 15 | 15222 | 14680 | 15063 | 16605 | 17287 | 17077 | 17356 | 16232 | 16185 | 18486 | 18337 | 18688 | 18898 | 17352 | 19801 | 19928 | 19877 | 20104 | 18861 | 18462
2776 | 2776 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 16 | 15630 | 15071 | 15640 | 17055 | 17931 | 17426 | 17626 | 16565 | 16705 | 19190 | 18569 | 18904 | 19033 | 17807 | 20183 | 20613 | 20022 | 20167 | 19044 | 18887
2777 | 2777 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 17 | 15942 | 15506 | 16188 | 17584 | 18346 | 17693 | 17834 | 17044 | 17343 | 19599 | 18987 | 19250 | 19210 | 18473 | 20760 | 20996 | 20464 | 20354 | 19564 | 19567
2778 | 2778 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 18 | 15853 | 15366 | 16486 | 17911 | 18360 | 17834 | 17930 | 17185 | 17840 | 19692 | 19043 | 19629 | 19625 | 19234 | 21296 | 21254 | 20676 | 20889 | 20032 | 20396
2779 | 2779 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 19 | 15658 | 15023 | 16386 | 17772 | 18211 | 17861 | 17917 | 17081 | 17941 | 19708 | 19463 | 20053 | 20102 | 19639 | 21544 | 21696 | 21396 | 21587 | 20407 | 20923
2780 | 2780 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 20 | 16210 | 15108 | 16672 | 18223 | 18644 | 18550 | 18513 | 17365 | 18460 | 20476 | 20513 | 21235 | 21253 | 20480 | 22342 | 22946 | 22947 | 23008 | 21480 | 21915
2781 | 2781 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 21 | 16057 | 14884 | 16728 | 18214 | 18615 | 18578 | 18573 | 17421 | 18814 | 20836 | 20913 | 21841 | 21966 | 21273 | 22911 | 23836 | 23872 | 24053 | 22429 | 22920
2782 | 2782 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 22 | 14983 | 14065 | 15925 | 17122 | 17335 | 17583 | 17803 | 16775 | 18175 | 19814 | 20235 | 21192 | 21599 | 20916 | 22367 | 23135 | 23520 | 23904 | 22319 | 22690
2783 | 2783 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 23 | 13847 | 13260 | 14964 | 15898 | 15947 | 16444 | 16879 | 16001 | 17278 | 18587 | 19200 | 20234 | 20852 | 20166 | 21510 | 22065 | 22626 | 23267 | 21823 | 22007
2784 | 2784 | 116 | 4 | 26 | Winter | 4 | 25 | Winter | 24 | 13058 | 12568 | 14355 | 14995 | 14912 | 15652 | 16162 | 15327 | 16697 | 17604 | 18366 | 19530 | 20254 | 19668 | 20987 | 21165 | 21869 | 22734 | 21312 | 21547
2785 | 2785 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 1 | 12587 | 12597 | 13331 | 14186 | 14127 | 15132 | 14782 | 15051 | 15590 | 16957 | 17652 | 19047 | 18679 | 18435 | 20204 | 20620 | 20964 | 21044 | 20153 | 20288
2786 | 2786 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 2 | 12327 | 12326 | 13182 | 13839 | 13823 | 14796 | 14321 | 14702 | 15393 | 16561 | 17329 | 18580 | 18179 | 18137 | 19677 | 20106 | 20516 | 20469 | 19619 | 19948
2787 | 2787 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 3 | 12240 | 12147 | 13175 | 13751 | 13737 | 14707 | 14111 | 14518 | 15380 | 16420 | 17177 | 18363 | 17786 | 18008 | 19300 | 19697 | 20118 | 19987 | 19249 | 19764
2788 | 2788 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 4 | 12289 | 12117 | 13355 | 13803 | 13779 | 14683 | 13935 | 14408 | 15436 | 16226 | 16960 | 17961 | 17168 | 17787 | 18766 | 19113 | 19545 | 19144 | 18673 | 19396
2789 | 2789 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 5 | 12699 | 12300 | 14005 | 14417 | 14251 | 14985 | 13839 | 14404 | 15916 | 16390 | 17108 | 17827 | 16564 | 17909 | 18864 | 18972 | 19470 | 18280 | 18102 | 19351
2790 | 2790 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 6 | 13569 | 12569 | 15119 | 15649 | 15319 | 15686 | 13924 | 14441 | 16800 | 17092 | 17681 | 18026 | 16079 | 18432 | 19431 | 19240 | 19639 | 17523 | 17479 | 19708
2791 | 2791 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 7 | 14546 | 12800 | 16407 | 16970 | 16634 | 16554 | 14176 | 14461 | 17790 | 18088 | 18493 | 18415 | 15896 | 19144 | 20021 | 19873 | 20092 | 17127 | 16924 | 20291
2792 | 2792 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 8 | 15138 | 13358 | 17302 | 17710 | 17321 | 17124 | 15087 | 14886 | 18521 | 18719 | 18968 | 18751 | 16567 | 19776 | 20333 | 20277 | 20437 | 17726 | 17152 | 20872
2793 | 2793 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 9 | 15418 | 13974 | 17409 | 17783 | 17409 | 17274 | 15804 | 15359 | 18518 | 18744 | 18938 | 18778 | 17172 | 19673 | 20164 | 20050 | 20446 | 18261 | 17488 | 20718
2794 | 2794 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 10 | 15634 | 14545 | 17391 | 17848 | 17519 | 17477 | 16340 | 15939 | 18559 | 18901 | 19012 | 19042 | 17867 | 19755 | 20410 | 20360 | 20690 | 19008 | 18168 | 20851
2795 | 2795 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 11 | 15676 | 14714 | 17247 | 17728 | 17476 | 17522 | 16538 | 16174 | 18470 | 18926 | 19028 | 19174 | 18185 | 19720 | 20386 | 20508 | 20815 | 19380 | 18506 | 20858
2796 | 2796 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 12 | 15693 | 14805 | 17057 | 17617 | 17309 | 17536 | 16551 | 16299 | 18309 | 18777 | 18972 | 19226 | 18249 | 19574 | 20290 | 20400 | 20789 | 19460 | 18670 | 20730
2797 | 2797 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 13 | 15637 | 14810 | 16902 | 17545 | 17246 | 17451 | 16406 | 16300 | 18164 | 18704 | 18890 | 19139 | 18099 | 19421 | 20199 | 20329 | 20674 | 19297 | 18658 | 20576
2798 | 2798 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 14 | 15571 | 14792 | 16786 | 17477 | 17056 | 17371 | 16251 | 16269 | 18020 | 18491 | 18825 | 19009 | 17834 | 19252 | 20075 | 20084 | 20496 | 19011 | 18572 | 20388
2799 | 2799 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 15 | 15528 | 14841 | 16742 | 17430 | 16942 | 17285 | 16296 | 16315 | 17948 | 18341 | 18718 | 18869 | 17817 | 19148 | 19968 | 19902 | 20332 | 18968 | 18577 | 20268
2800 | 2800 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 16 | 15570 | 15108 | 16885 | 17738 | 16958 | 17260 | 16328 | 16540 | 18020 | 18278 | 18760 | 18714 | 17742 | 19144 | 20346 | 19741 | 20230 | 18834 | 18687 | 20233
2801 | 2801 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 17 | 15597 | 15507 | 17257 | 18009 | 17214 | 17320 | 16652 | 17020 | 18362 | 18538 | 18983 | 18740 | 18096 | 19568 | 20579 | 20031 | 20493 | 19202 | 19213 | 20673
2802 | 2802 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 18 | 15344 | 15665 | 17403 | 17923 | 16978 | 17278 | 16631 | 17354 | 18770 | 18450 | 19268 | 18997 | 18347 | 20111 | 20715 | 20123 | 21041 | 19552 | 19929 | 21275
2803 | 2803 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 19 | 15218 | 15541 | 17252 | 17755 | 17106 | 17243 | 16498 | 17417 | 18874 | 18803 | 19784 | 19419 | 18537 | 20487 | 21137 | 20824 | 21873 | 19939 | 20475 | 21777
2804 | 2804 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 20 | 15550 | 15819 | 17673 | 18136 | 17793 | 17794 | 16725 | 17867 | 19518 | 19742 | 20641 | 20480 | 19340 | 21504 | 22327 | 22316 | 23034 | 21013 | 21467 | 22922
2805 | 2805 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 21 | 15294 | 15801 | 17584 | 18009 | 17615 | 17751 | 16663 | 18095 | 19704 | 19987 | 21170 | 21032 | 19893 | 22126 | 23108 | 23146 | 24056 | 21903 | 22417 | 23754
2806 | 2806 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 22 | 14442 | 15006 | 16510 | 16740 | 16633 | 16983 | 16007 | 17441 | 18773 | 19282 | 20522 | 20629 | 19626 | 21469 | 22409 | 22799 | 23691 | 21823 | 22221 | 23220
2807 | 2807 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 23 | 13509 | 14051 | 15276 | 15361 | 15426 | 16048 | 15209 | 16526 | 17566 | 18220 | 19521 | 19852 | 19019 | 20394 | 21308 | 21894 | 22785 | 21315 | 21540 | 22203
2808 | 2808 | 117 | 4 | 27 | Winter | 4 | 26 | Winter | 24 | 12798 | 13444 | 14378 | 14333 | 14510 | 15327 | 14527 | 15933 | 16674 | 17376 | 18749 | 19236 | 18446 | 19555 | 20403 | 21134 | 22105 | 20804 | 21084 | 21395
2809 | 2809 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 1 | 12011 | 12883 | 14013 | 13990 | 14479 | 14426 | 14780 | 15307 | 16608 | 17167 | 18023 | 18127 | 18067 | 19795 | 20274 | 20683 | 21327 | 20096 | 20258 | 21877
2810 | 2810 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 2 | 11677 | 12793 | 13736 | 13752 | 14276 | 14048 | 14519 | 15213 | 16220 | 16967 | 17652 | 17666 | 17610 | 19299 | 19790 | 20263 | 20750 | 19578 | 19934 | 21324
2811 | 2811 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 3 | 11480 | 12772 | 13613 | 13625 | 14187 | 13791 | 14284 | 15152 | 16085 | 16780 | 17426 | 17282 | 17294 | 18924 | 19379 | 19859 | 20316 | 19189 | 19732 | 20881
2812 | 2812 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 4 | 11426 | 12945 | 13657 | 13662 | 14250 | 13616 | 14172 | 15210 | 15966 | 16583 | 17130 | 16738 | 16917 | 18445 | 18846 | 19325 | 19709 | 18634 | 19379 | 20217
2813 | 2813 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 5 | 11496 | 13573 | 14272 | 14155 | 14782 | 13549 | 14196 | 15733 | 16332 | 16788 | 17322 | 16220 | 16572 | 18602 | 18759 | 19292 | 19666 | 18079 | 19343 | 20155
2814 | 2814 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 6 | 11764 | 14677 | 15474 | 15225 | 15715 | 13646 | 14258 | 16657 | 17239 | 17412 | 17925 | 15807 | 16147 | 19194 | 19055 | 19475 | 19883 | 17448 | 19681 | 20527
2815 | 2815 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 7 | 12276 | 16009 | 16811 | 16543 | 16819 | 13925 | 14326 | 17691 | 18278 | 18285 | 18786 | 15675 | 15760 | 19811 | 19712 | 19930 | 20468 | 16884 | 20244 | 20970
2816 | 2816 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 8 | 12917 | 16594 | 17287 | 16957 | 17130 | 14546 | 14474 | 18170 | 18572 | 18493 | 19151 | 16097 | 15752 | 19844 | 19824 | 20000 | 20710 | 16802 | 20508 | 20925
2817 | 2817 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 9 | 13570 | 16601 | 17307 | 16959 | 17081 | 15201 | 14902 | 18127 | 18389 | 18430 | 19078 | 16584 | 16018 | 19568 | 19480 | 19877 | 20581 | 17011 | 20224 | 20594
2818 | 2818 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 10 | 14060 | 16547 | 17339 | 17027 | 17048 | 15711 | 15466 | 18154 | 18419 | 18502 | 19107 | 17185 | 16568 | 19722 | 19706 | 20033 | 20697 | 17605 | 20277 | 20796
2819 | 2819 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 11 | 14239 | 16452 | 17271 | 17032 | 17018 | 15953 | 15751 | 18125 | 18393 | 18572 | 18994 | 17522 | 16881 | 19721 | 19879 | 20183 | 20647 | 17970 | 20314 | 20847
2820 | 2820 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 12 | 14207 | 16241 | 17131 | 16835 | 16893 | 15933 | 15846 | 17933 | 18269 | 18483 | 18830 | 17548 | 16993 | 19589 | 19737 | 20120 | 20495 | 18100 | 20154 | 20732
2821 | 2821 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 13 | 14033 | 16031 | 17016 | 16722 | 16765 | 15742 | 15800 | 17734 | 18166 | 18357 | 18640 | 17354 | 16960 | 19458 | 19625 | 19958 | 20276 | 18047 | 19958 | 20596
2822 | 2822 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 14 | 13898 | 15893 | 16913 | 16494 | 16726 | 15537 | 15714 | 17532 | 18071 | 18227 | 18383 | 17092 | 16895 | 19332 | 19375 | 19780 | 19970 | 17953 | 19762 | 20448
2823 | 2823 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 15 | 13888 | 15798 | 16813 | 16323 | 16623 | 15526 | 15702 | 17395 | 17956 | 18061 | 18090 | 17037 | 16874 | 19185 | 19153 | 19574 | 19638 | 17915 | 19599 | 20282
2824 | 2824 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 16 | 14053 | 16029 | 17150 | 16431 | 16868 | 15657 | 16022 | 17562 | 18442 | 18207 | 18158 | 17067 | 17115 | 19668 | 19091 | 19567 | 19565 | 18114 | 19653 | 20728
2825 | 2825 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 17 | 14481 | 16553 | 17563 | 16836 | 17176 | 16128 | 16643 | 18048 | 18847 | 18572 | 18518 | 17572 | 17775 | 20047 | 19529 | 19983 | 20025 | 18789 | 20242 | 21115
2826 | 2826 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 18 | 14449 | 16868 | 17677 | 16796 | 17505 | 16285 | 17128 | 18585 | 19039 | 19000 | 19008 | 17998 | 18631 | 20391 | 19828 | 20741 | 20712 | 19734 | 21068 | 21516
2827 | 2827 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 19 | 14196 | 16785 | 17565 | 16955 | 17845 | 16191 | 17221 | 18683 | 19105 | 19498 | 19432 | 18212 | 19114 | 20861 | 20595 | 21635 | 21502 | 20385 | 21683 | 22157
2828 | 2828 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 20 | 14311 | 17215 | 17955 | 17645 | 18401 | 16421 | 17671 | 19313 | 19835 | 20295 | 20259 | 18979 | 19949 | 22038 | 22073 | 22810 | 22703 | 21420 | 22875 | 23507
2829 | 2829 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 21 | 14014 | 17097 | 17800 | 17426 | 18453 | 16307 | 17844 | 19431 | 20055 | 20720 | 20641 | 19434 | 20625 | 22759 | 22831 | 23789 | 23595 | 22362 | 23698 | 24498
2830 | 2830 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 22 | 13219 | 16011 | 16518 | 16421 | 17508 | 15628 | 17164 | 18458 | 19014 | 20028 | 20014 | 19103 | 20262 | 22022 | 22461 | 23389 | 23251 | 22165 | 23168 | 23946
2831 | 2831 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 23 | 12405 | 14760 | 15114 | 15192 | 16338 | 14801 | 16214 | 17208 | 17746 | 18985 | 18985 | 18439 | 19477 | 20874 | 21512 | 22462 | 22334 | 21455 | 22136 | 22909
2832 | 2832 | 118 | 4 | 28 | Winter | 4 | 27 | Winter | 24 | 11704 | 13838 | 14063 | 14256 | 15489 | 14087 | 15584 | 16275 | 16730 | 18166 | 18148 | 17817 | 18949 | 19930 | 20719 | 21749 | 21568 | 20968 | 21302 | 22013
2833 | 2833 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 1 | 11833 | 13113 | 13361 | 13878 | 14374 | 14013 | 14573 | 15758 | 16150 | 17033 | 17346 | 17185 | 17802 | 19436 | 19942 | 20614 | 20570 | 19793 | 21409 | 21605
2834 | 2834 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 2 | 11613 | 12809 | 13098 | 13684 | 14076 | 13694 | 14407 | 15393 | 15855 | 16602 | 16861 | 16752 | 17520 | 18966 | 19536 | 20052 | 19962 | 19465 | 20869 | 21084
2835 | 2835 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 3 | 11420 | 12712 | 13012 | 13612 | 13966 | 13508 | 14404 | 15283 | 15686 | 16463 | 16633 | 16476 | 17404 | 18594 | 19165 | 19650 | 19490 | 19283 | 20442 | 20636
2836 | 2836 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 4 | 11374 | 12764 | 13060 | 13663 | 13970 | 13432 | 14512 | 15186 | 15502 | 16265 | 16343 | 16126 | 17230 | 18085 | 18644 | 19049 | 18883 | 18914 | 19762 | 19932
2837 | 2837 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 5 | 11565 | 13429 | 13587 | 14229 | 14504 | 13516 | 15111 | 15627 | 15731 | 16571 | 16251 | 15855 | 17418 | 18067 | 18667 | 19053 | 18607 | 18900 | 19722 | 19683
2838 | 2838 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 6 | 11834 | 14652 | 14677 | 15217 | 15487 | 13634 | 16117 | 16628 | 16487 | 17292 | 16243 | 15530 | 17979 | 18433 | 18905 | 19327 | 18287 | 19257 | 20110 | 19809
2839 | 2839 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 7 | 12098 | 16054 | 16034 | 16396 | 16726 | 13768 | 17241 | 17786 | 17567 | 18257 | 16279 | 15241 | 18742 | 19177 | 19422 | 19970 | 17957 | 19858 | 20585 | 20355
2840 | 2840 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 8 | 12515 | 16685 | 16585 | 16856 | 17400 | 14066 | 17877 | 18274 | 18080 | 18790 | 16617 | 15393 | 19236 | 19441 | 19641 | 20353 | 18141 | 20259 | 20673 | 20537
2841 | 2841 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 9 | 13062 | 16711 | 16588 | 16837 | 17389 | 14473 | 17815 | 18148 | 18088 | 18680 | 16969 | 15697 | 19038 | 19133 | 19551 | 20246 | 18442 | 20007 | 20368 | 20166
2842 | 2842 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 10 | 13538 | 16664 | 16565 | 16745 | 17281 | 14902 | 17702 | 18116 | 18195 | 18549 | 17383 | 16175 | 18982 | 19297 | 19640 | 20293 | 18987 | 19995 | 20508 | 20376
2843 | 2843 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 11 | 13858 | 16692 | 16656 | 16819 | 17197 | 15250 | 17728 | 18196 | 18384 | 18486 | 17597 | 16592 | 19077 | 19564 | 19889 | 20350 | 19215 | 20128 | 20660 | 20688
2844 | 2844 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 12 | 14060 | 16681 | 16599 | 16841 | 17146 | 15475 | 17671 | 18212 | 18352 | 18447 | 17647 | 16851 | 19042 | 19566 | 19967 | 20344 | 19238 | 20113 | 20686 | 20710
2845 | 2845 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 13 | 14115 | 16681 | 16602 | 16816 | 17050 | 15548 | 17589 | 18214 | 18328 | 18383 | 17480 | 16921 | 18943 | 19566 | 19918 | 20226 | 19027 | 20028 | 20664 | 20707
2846 | 2846 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 14 | 14092 | 16641 | 16439 | 16805 | 16898 | 15550 | 17481 | 18147 | 18083 | 18233 | 17158 | 16888 | 18807 | 19350 | 19772 | 19948 | 18677 | 19864 | 20542 | 20471
2847 | 2847 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 15 | 14170 | 16641 | 16375 | 16797 | 16767 | 15651 | 17457 | 18130 | 17963 | 18065 | 17087 | 16963 | 18750 | 19221 | 19660 | 19711 | 18574 | 19787 | 20469 | 20326
2848 | 2848 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 16 | 14545 | 16972 | 16518 | 17070 | 16968 | 16004 | 17661 | 18594 | 18020 | 18178 | 17224 | 17241 | 18868 | 19195 | 19688 | 19669 | 18633 | 19866 | 20934 | 20261
2849 | 2849 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 17 | 14950 | 17229 | 16780 | 17230 | 17227 | 16480 | 17994 | 18850 | 18279 | 18389 | 17534 | 17753 | 19291 | 19486 | 19958 | 19984 | 18906 | 20304 | 21177 | 20571
2850 | 2850 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 18 | 15026 | 17069 | 16492 | 17250 | 17203 | 16707 | 18254 | 18747 | 18081 | 18606 | 17948 | 18293 | 19761 | 19507 | 20430 | 20389 | 19499 | 20864 | 21316 | 20680
2851 | 2851 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 19 | 14826 | 16825 | 16522 | 17440 | 17145 | 16693 | 18240 | 18635 | 18279 | 18882 | 18183 | 18595 | 20068 | 20089 | 21168 | 21015 | 20086 | 21346 | 21816 | 21429
2852 | 2852 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 20 | 15089 | 17130 | 17116 | 17908 | 17561 | 17070 | 18779 | 19243 | 19115 | 19564 | 19035 | 19306 | 21019 | 21462 | 22248 | 22148 | 21321 | 22493 | 23136 | 23001
2853 | 2853 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 21 | 15074 | 16975 | 16879 | 17946 | 17490 | 17223 | 18866 | 19399 | 19280 | 19862 | 19493 | 19926 | 21599 | 22159 | 23182 | 23004 | 22231 | 23330 | 24127 | 23994
2854 | 2854 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 22 | 14242 | 15659 | 15844 | 16965 | 16538 | 16503 | 17848 | 18287 | 18506 | 19160 | 18944 | 19490 | 20887 | 21707 | 22738 | 22602 | 21958 | 22775 | 23547 | 23745
2855 | 2855 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 23 | 13265 | 14259 | 14617 | 15792 | 15375 | 15555 | 16590 | 16984 | 17403 | 18114 | 18195 | 18671 | 19779 | 20746 | 21786 | 21669 | 21339 | 21737 | 22507 | 22884
2856 | 2856 | 119 | 4 | 29 | Winter | 4 | 28 | Winter | 24 | 12628 | 13228 | 13694 | 14956 | 14489 | 14933 | 15664 | 15959 | 16526 | 17270 | 17573 | 18131 | 18913 | 19947 | 21075 | 20905 | 20789 | 20921 | 21622 | 22135
2857 | 2857 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 1 | 11938 | 12772 | 13571 | 14059 | 14109 | 14155 | 15292 | 15544 | 16175 | 16730 | 16650 | 17238 | 18954 | 19420 | 20158 | 20158 | 19363 | 21207 | 21428 | 21492
2858 | 2858 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 2 | 11795 | 12472 | 13368 | 13701 | 13687 | 13965 | 14909 | 15167 | 15881 | 16242 | 16304 | 16956 | 18452 | 19002 | 19582 | 19556 | 18939 | 20637 | 20879 | 21020
2859 | 2859 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 3 | 11829 | 12388 | 13309 | 13632 | 13540 | 13972 | 14816 | 15068 | 15782 | 16049 | 16136 | 16878 | 18121 | 18660 | 19206 | 19110 | 18560 | 20221 | 20445 | 20605
2860 | 2860 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 4 | 12011 | 12460 | 13391 | 13689 | 13540 | 14123 | 14786 | 14990 | 15692 | 15840 | 15895 | 16758 | 17691 | 18209 | 18669 | 18535 | 18056 | 19580 | 19773 | 19978
2861 | 2861 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 5 | 12641 | 13000 | 13973 | 14262 | 13808 | 14752 | 15286 | 15311 | 15998 | 15817 | 15734 | 17008 | 17918 | 18286 | 18719 | 18293 | 17738 | 19561 | 19533 | 19856
2862 | 2862 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 6 | 13792 | 14130 | 15019 | 15318 | 14231 | 15823 | 16386 | 16176 | 16753 | 15917 | 15545 | 17669 | 18608 | 18608 | 19070 | 18035 | 17254 | 19999 | 19689 | 19981
2863 | 2863 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 7 | 15140 | 15452 | 16178 | 16531 | 14546 | 16923 | 17553 | 17261 | 17680 | 15967 | 15325 | 18439 | 19268 | 19109 | 19688 | 17671 | 16807 | 20428 | 20182 | 20335
2864 | 2864 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 8 | 15801 | 15978 | 16613 | 17138 | 14975 | 17524 | 18033 | 17751 | 17998 | 16317 | 15403 | 18892 | 19412 | 19302 | 20041 | 17806 | 16732 | 20474 | 20330 | 20472
2865 | 2865 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 9 | 15759 | 15970 | 16577 | 17041 | 15453 | 17428 | 17887 | 17680 | 17855 | 16657 | 15650 | 18672 | 19137 | 19174 | 19895 | 18080 | 16778 | 20128 | 19926 | 20321
2866 | 2866 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 10 | 15671 | 16009 | 16554 | 16936 | 15864 | 17358 | 17903 | 17752 | 17828 | 17115 | 16106 | 18663 | 19273 | 19313 | 19991 | 18668 | 17355 | 20320 | 20191 | 20492
2867 | 2867 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 11 | 15549 | 15977 | 16509 | 16697 | 15900 | 17250 | 17848 | 17769 | 17830 | 17197 | 16333 | 18624 | 19251 | 19429 | 19924 | 18768 | 17686 | 20346 | 20380 | 20652
2868 | 2868 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 12 | 15312 | 15757 | 16350 | 16466 | 15751 | 17010 | 17683 | 17549 | 17697 | 17062 | 16366 | 18412 | 19084 | 19324 | 19737 | 18614 | 17751 | 20203 | 20218 | 20565
2869 | 2869 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 13 | 15143 | 15659 | 16251 | 16322 | 15518 | 16855 | 17613 | 17477 | 17623 | 16823 | 16288 | 18258 | 18996 | 19203 | 19548 | 18348 | 17670 | 20108 | 20143 | 20453
2870 | 2870 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 14 | 14960 | 15388 | 16144 | 16112 | 15121 | 16651 | 17450 | 17197 | 17494 | 16404 | 16152 | 18023 | 18798 | 18964 | 19176 | 17895 | 17507 | 19887 | 19808 | 20196
2871 | 2871 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 15 | 15079 | 15460 | 16255 | 16119 | 15195 | 16748 | 17553 | 17223 | 17564 | 16455 | 16305 | 18088 | 18861 | 18975 | 19062 | 17912 | 17633 | 19932 | 19780 | 20182
2872 | 2872 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 16 | 15356 | 15595 | 16545 | 16336 | 15414 | 16964 | 17992 | 17303 | 17754 | 16607 | 16578 | 18226 | 19368 | 19020 | 19034 | 17981 | 17847 | 20399 | 19719 | 20173
2873 | 2873 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 17 | 15866 | 15963 | 16818 | 16718 | 15827 | 17420 | 18374 | 17681 | 18099 | 17028 | 17238 | 18769 | 19725 | 19413 | 19472 | 18374 | 18528 | 20767 | 20147 | 20569
2874 | 2874 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 18 | 16042 | 15795 | 16906 | 16831 | 16132 | 17801 | 18399 | 17647 | 18405 | 17531 | 17837 | 19343 | 19915 | 20013 | 19995 | 19099 | 19290 | 21033 | 20382 | 21226
2875 | 2875 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 19 | 15902 | 15853 | 17129 | 16851 | 16208 | 17830 | 18310 | 17911 | 18845 | 17757 | 18209 | 19673 | 20279 | 20770 | 20651 | 19739 | 19860 | 21602 | 21185 | 22124
2876 | 2876 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 20 | 16303 | 16458 | 17602 | 17276 | 16717 | 18383 | 18911 | 18720 | 19564 | 18560 | 18773 | 20608 | 21390 | 21838 | 21778 | 20992 | 20786 | 22950 | 22803 | 23360
2877 | 2877 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 21 | 16174 | 16198 | 17588 | 17149 | 16698 | 18416 | 18975 | 18784 | 19901 | 18909 | 19327 | 21092 | 22032 | 22694 | 22567 | 21841 | 21711 | 23913 | 23775 | 24468
2878 | 2878 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 22 | 15074 | 15158 | 16609 | 16197 | 15870 | 17395 | 17827 | 17967 | 19152 | 18318 | 18857 | 20338 | 21237 | 22219 | 22149 | 21551 | 21470 | 23331 | 23527 | 24158
2879 | 2879 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 23 | 13853 | 13942 | 15451 | 15057 | 14989 | 16158 | 16517 | 16854 | 18112 | 17572 | 18068 | 19226 | 20099 | 21263 | 21215 | 20938 | 20785 | 22302 | 22690 | 23297
2880 | 2880 | 120 | 4 | 30 | Winter | 4 | 29 | Winter | 24 | 12949 | 13050 | 14617 | 14181 | 14292 | 15236 | 15480 | 15964 | 17284 | 16939 | 17486 | 18350 | 19148 | 20544 | 20443 | 20392 | 20250 | 21413 | 21944 | 22625
2881 | 2881 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 1 | 12846 | 13377 | 14155 | 14248 | 14303 | 15222 | 15458 | 16089 | 16753 | 16557 | 16950 | 18727 | 19230 | 19998 | 20097 | 19399 | 19598 | 21585 | 21703 | 22108
2882 | 2882 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 2 | 12560 | 13180 | 13842 | 13856 | 14084 | 14869 | 15120 | 15828 | 16354 | 16250 | 16679 | 18265 | 18794 | 19478 | 19539 | 19023 | 19246 | 21075 | 21261 | 21520
2883 | 2883 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 3 | 12469 | 13063 | 13714 | 13638 | 13953 | 14696 | 14930 | 15636 | 16236 | 15981 | 16532 | 17952 | 18443 | 19119 | 19098 | 18652 | 18999 | 20632 | 20836 | 21078
2884 | 2884 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 4 | 12536 | 13166 | 13776 | 13640 | 13912 | 14682 | 14878 | 15574 | 16112 | 15758 | 16463 | 17596 | 18004 | 18643 | 18583 | 18188 | 18697 | 19991 | 20233 | 20419
2885 | 2885 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 5 | 13191 | 13783 | 14411 | 13993 | 14030 | 15313 | 15356 | 16054 | 16482 | 15775 | 16777 | 17882 | 18044 | 18733 | 18369 | 17885 | 18735 | 19759 | 20102 | 20302
2886 | 2886 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 6 | 14401 | 14826 | 15473 | 14428 | 14165 | 16449 | 16279 | 16887 | 17273 | 15646 | 17422 | 18614 | 18458 | 19103 | 18118 | 17392 | 19042 | 19902 | 20190 | 20468
2887 | 2887 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 7 | 15732 | 15995 | 16690 | 14735 | 14249 | 17631 | 17385 | 17846 | 18210 | 15453 | 18167 | 19314 | 19166 | 19740 | 17771 | 16929 | 19509 | 20385 | 20522 | 20966
2888 | 2888 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 8 | 16270 | 16373 | 17247 | 15123 | 14344 | 18064 | 17832 | 18140 | 18665 | 15505 | 18579 | 19456 | 19367 | 20049 | 17862 | 16812 | 19819 | 20484 | 20589 | 21227
2889 | 2889 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 9 | 16189 | 16289 | 17122 | 15571 | 14594 | 17891 | 17745 | 17989 | 18455 | 15753 | 18416 | 19136 | 18975 | 19836 | 18075 | 16792 | 19482 | 20013 | 20365 | 21002
2890 | 2890 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 10 | 15935 | 16021 | 16774 | 15745 | 14728 | 17661 | 17573 | 17745 | 18100 | 15983 | 18281 | 18991 | 18906 | 19643 | 18377 | 17091 | 19415 | 19991 | 20269 | 20853
2891 | 2891 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 11 | 15747 | 15873 | 16427 | 15661 | 14803 | 17462 | 17452 | 17601 | 17812 | 16058 | 18177 | 18863 | 18954 | 19472 | 18380 | 17327 | 19463 | 20091 | 20336 | 20724
2892 | 2892 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 12 | 15621 | 15776 | 16243 | 15551 | 14873 | 17333 | 17258 | 17489 | 17653 | 16108 | 18061 | 18757 | 18834 | 19355 | 18295 | 17455 | 19418 | 20002 | 20312 | 20624
2893 | 2893 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 13 | 15558 | 15698 | 16108 | 15321 | 14807 | 17263 | 17188 | 17409 | 17530 | 16027 | 18008 | 18682 | 18774 | 19182 | 18045 | 17386 | 19374 | 19942 | 20210 | 20456
2894 | 2894 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 14 | 15442 | 15607 | 15928 | 14956 | 14716 | 17137 | 16939 | 17319 | 17310 | 15927 | 17914 | 18520 | 18482 | 18840 | 17620 | 17251 | 19244 | 19628 | 19977 | 20093
2895 | 2895 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 15 | 15604 | 15777 | 15981 | 15075 | 14933 | 17278 | 17009 | 17435 | 17311 | 16120 | 17975 | 18630 | 18520 | 18773 | 17681 | 17423 | 19284 | 19642 | 20006 | 19997
2896 | 2896 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 16 | 16250 | 16381 | 16519 | 15615 | 15587 | 18032 | 17412 | 17956 | 17763 | 16717 | 18328 | 19442 | 18828 | 19077 | 18074 | 17957 | 19581 | 19886 | 20314 | 20244
2897 | 2897 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 17 | 16756 | 16774 | 17015 | 16143 | 16349 | 18539 | 17915 | 18413 | 18217 | 17490 | 18782 | 19909 | 19358 | 19630 | 18584 | 18750 | 20062 | 20430 | 20836 | 20797
2898 | 2898 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 18 | 16746 | 16845 | 17070 | 16423 | 16688 | 18569 | 17870 | 18674 | 18548 | 18063 | 19193 | 20078 | 19496 | 20140 | 19300 | 19507 | 20685 | 20666 | 21517 | 21381
2899 | 2899 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 19 | 16532 | 17016 | 17044 | 16448 | 16829 | 18435 | 18074 | 19031 | 18811 | 18357 | 19750 | 20359 | 20067 | 20736 | 19881 | 20032 | 21493 | 21464 | 22403 | 22139
2900 | 2900 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 20 | 16857 | 17471 | 17441 | 16934 | 17202 | 19006 | 18834 | 19676 | 19467 | 18837 | 20295 | 21396 | 21431 | 21813 | 21099 | 20945 | 22281 | 23104 | 23649 | 23395
2901 | 2901 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 21 | 16663 | 17401 | 17274 | 16866 | 17374 | 19006 | 18811 | 19920 | 19649 | 19306 | 20540 | 21931 | 22026 | 22526 | 21886 | 21830 | 22882 | 24041 | 24740 | 24360
2902 | 2902 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 22 | 15351 | 16428 | 16305 | 16016 | 16665 | 17819 | 17942 | 19121 | 18908 | 18792 | 19760 | 21093 | 21535 | 22057 | 21560 | 21563 | 22318 | 23763 | 24426 | 24064
2903 | 2903 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 23 | 13934 | 15242 | 15131 | 15107 | 15722 | 16454 | 16779 | 18028 | 17823 | 17966 | 18667 | 19888 | 20533 | 21086 | 20912 | 20834 | 21295 | 22871 | 23524 | 23167
2904 | 2904 | 121 | 5 | 1 | Spring | 4 | 30 | Winter | 24 | 12905 | 14381 | 14229 | 14403 | 15064 | 15390 | 15850 | 17171 | 16949 | 17361 | 17814 | 18907 | 19707 | 20287 | 20336 | 20284 | 20501 | 22106 | 22826 | 22403
2905 | 2905 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 1 | 12294 | 13317 | 13712 | 13878 | 14056 | 14708 | 15367 | 16027 | 16293 | 16201 | 17313 | 18369 | 19036 | 19384 | 18823 | 19074 | 20330 | 21278 | 21711 | 21409
2906 | 2906 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 2 | 12046 | 13028 | 13351 | 13660 | 13873 | 14393 | 15131 | 15637 | 15859 | 15956 | 16950 | 17950 | 18675 | 18843 | 18459 | 18723 | 19888 | 20844 | 21125 | 20821
2907 | 2907 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 3 | 11902 | 12897 | 13134 | 13452 | 13808 | 14207 | 14949 | 15424 | 15558 | 15822 | 16706 | 17615 | 18345 | 18411 | 18079 | 18475 | 19541 | 20421 | 20677 | 20323
2908 | 2908 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 4 | 11970 | 12994 | 13159 | 13424 | 13953 | 14207 | 14942 | 15351 | 15371 | 15817 | 16522 | 17259 | 17955 | 17927 | 17639 | 18214 | 19075 | 19824 | 20024 | 19665
2909 | 2909 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 5 | 12551 | 13627 | 13535 | 13636 | 14536 | 14738 | 15475 | 15911 | 15546 | 16194 | 16800 | 17388 | 18093 | 17785 | 17390 | 18287 | 18992 | 19729 | 19943 | 19316
2910 | 2910 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 6 | 13646 | 14698 | 13988 | 13800 | 15486 | 15695 | 16343 | 16798 | 15703 | 16879 | 17454 | 17879 | 18423 | 17580 | 16924 | 18610 | 19301 | 19818 | 20109 | 18904
2911 | 2911 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 7 | 15068 | 16063 | 14461 | 14039 | 16601 | 16971 | 17490 | 17935 | 15898 | 17824 | 18218 | 18786 | 19074 | 17396 | 16604 | 19232 | 19781 | 20281 | 20727 | 18568
2912 | 2912 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 8 | 15778 | 16864 | 15118 | 14380 | 17331 | 17661 | 18047 | 18646 | 16458 | 18482 | 18517 | 19276 | 19477 | 17754 | 16755 | 19786 | 19890 | 20612 | 21226 | 18887
2913 | 2913 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 9 | 15894 | 16843 | 15706 | 14774 | 17403 | 17660 | 17986 | 18556 | 16966 | 18373 | 18325 | 19074 | 19464 | 18149 | 16920 | 19618 | 19597 | 20561 | 21167 | 19246
2914 | 2914 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 10 | 15676 | 16500 | 15894 | 14936 | 17203 | 17481 | 17739 | 18253 | 17203 | 18248 | 18252 | 18991 | 19322 | 18446 | 17210 | 19551 | 19590 | 20458 | 21015 | 19593
2915 | 2915 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 11 | 15484 | 16149 | 15802 | 14974 | 16998 | 17360 | 17606 | 17936 | 17080 | 18170 | 18235 | 18969 | 19278 | 18381 | 17382 | 19536 | 19645 | 20463 | 20824 | 19569
2916 | 2916 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 12 | 15279 | 15948 | 15695 | 15025 | 16843 | 17180 | 17510 | 17761 | 16930 | 18080 | 18153 | 18824 | 19202 | 18266 | 17481 | 19471 | 19578 | 20420 | 20697 | 19463
2917 | 2917 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 13 | 15140 | 15783 | 15427 | 14914 | 16748 | 17076 | 17397 | 17593 | 16651 | 17996 | 18057 | 18720 | 19059 | 17970 | 17366 | 19388 | 19488 | 20275 | 20482 | 19159
2918 | 2918 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 14 | 14859 | 15572 | 15027 | 14795 | 16650 | 16793 | 17273 | 17352 | 16241 | 17868 | 17889 | 18402 | 18823 | 17514 | 17199 | 19228 | 19298 | 20006 | 20089 | 18689
2919 | 2919 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 15 | 14885 | 15545 | 15035 | 14904 | 16640 | 16761 | 17289 | 17251 | 16232 | 17830 | 17982 | 18336 | 18777 | 17471 | 17265 | 19158 | 19362 | 19925 | 19886 | 18627
2920 | 2920 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 16 | 15195 | 15923 | 15430 | 15410 | 16917 | 17031 | 17683 | 17571 | 16563 | 18051 | 18560 | 18510 | 19007 | 17728 | 17657 | 19310 | 19919 | 20093 | 19988 | 18847
2921 | 2921 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 17 | 15551 | 16252 | 15800 | 16017 | 17176 | 17389 | 17991 | 17871 | 16959 | 18353 | 18926 | 18894 | 19375 | 18096 | 18309 | 19639 | 20369 | 20460 | 20403 | 19220
2922 | 2922 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 18 | 15374 | 16266 | 15992 | 16298 | 17428 | 17318 | 18175 | 18120 | 17425 | 18712 | 19071 | 18981 | 19934 | 18775 | 19025 | 20233 | 20583 | 21110 | 20967 | 19964
2923 | 2923 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 19 | 15427 | 16252 | 16020 | 16458 | 17810 | 17527 | 18528 | 18352 | 17608 | 19246 | 19697 | 19517 | 20652 | 19357 | 19559 | 21056 | 21506 | 22019 | 21760 | 20678
2924 | 2924 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 20 | 16007 | 16626 | 16457 | 16802 | 18081 | 18245 | 19123 | 18921 | 18326 | 19688 | 20226 | 20780 | 21645 | 20500 | 20440 | 21803 | 22414 | 23259 | 23006 | 21984
2925 | 2925 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 21 | 15715 | 16452 | 16349 | 16940 | 17963 | 18149 | 19297 | 19015 | 18571 | 19847 | 20672 | 21267 | 22416 | 21219 | 21278 | 22362 | 23275 | 24335 | 23956 | 22952
2926 | 2926 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 22 | 14657 | 15475 | 15495 | 16222 | 16966 | 17235 | 18455 | 18236 | 17929 | 19047 | 19929 | 20722 | 21903 | 20868 | 20989 | 21791 | 22787 | 24011 | 23664 | 22767
2927 | 2927 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 23 | 13419 | 14311 | 14589 | 15299 | 15763 | 16046 | 17345 | 17134 | 17145 | 17947 | 18825 | 19700 | 20910 | 20192 | 20253 | 20767 | 21831 | 23106 | 22776 | 22189
2928 | 2928 | 122 | 5 | 2 | Spring | 5 | 1 | Spring | 24 | 12559 | 13440 | 13915 | 14679 | 14931 | 15144 | 16504 | 16265 | 16517 | 17123 | 17977 | 18887 | 20192 | 19639 | 19727 | 20012 | 21048 | 22443 | 22048 | 21680
2929 | 2929 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 1 | 12622 | 13305 | 13799 | 13989 | 14462 | 15046 | 15724 | 15936 | 15917 | 16914 | 17843 | 18565 | 19398 | 18530 | 18852 | 20125 | 20996 | 21661 | 21380 | 20296
2930 | 2930 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 2 | 12417 | 12946 | 13571 | 13785 | 14162 | 14806 | 15324 | 15491 | 15609 | 16549 | 17419 | 18197 | 18861 | 18156 | 18488 | 19652 | 20466 | 21052 | 20758 | 19876
2931 | 2931 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 3 | 12338 | 12767 | 13410 | 13766 | 14074 | 14675 | 15171 | 15250 | 15390 | 16372 | 17160 | 17922 | 18552 | 17830 | 18292 | 19342 | 20087 | 20654 | 20306 | 19497
2932 | 2932 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 4 | 12444 | 12783 | 13381 | 13920 | 14150 | 14685 | 15125 | 15114 | 15224 | 16224 | 16920 | 17593 | 18127 | 17424 | 18058 | 18903 | 19573 | 20022 | 19656 | 18949
2933 | 2933 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 5 | 13074 | 13169 | 13611 | 14526 | 14682 | 15270 | 15754 | 15364 | 15297 | 16596 | 17101 | 17816 | 18302 | 17221 | 18174 | 18865 | 19411 | 19958 | 19327 | 18579
2934 | 2934 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 6 | 14110 | 13634 | 13808 | 15499 | 15656 | 16183 | 16717 | 15597 | 15207 | 17327 | 17682 | 18238 | 18734 | 16802 | 18538 | 19212 | 19660 | 20142 | 18927 | 17993
2935 | 2935 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 7 | 15368 | 14094 | 14042 | 16608 | 16762 | 17315 | 17867 | 15835 | 15145 | 18116 | 18511 | 18923 | 19496 | 16471 | 19141 | 19679 | 20138 | 20728 | 18548 | 17544
2936 | 2936 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 8 | 15905 | 14662 | 14323 | 17240 | 17200 | 17796 | 18508 | 16330 | 15360 | 18383 | 18924 | 19258 | 19978 | 16527 | 19597 | 19702 | 20319 | 21118 | 18744 | 17576
2937 | 2937 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 9 | 15735 | 15127 | 14589 | 17099 | 16940 | 17630 | 18326 | 16659 | 15450 | 18146 | 18825 | 19035 | 19714 | 16469 | 19206 | 19188 | 19960 | 20819 | 18871 | 17491
2938 | 2938 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 10 | 15305 | 15161 | 14600 | 16741 | 16614 | 17227 | 17874 | 16748 | 15515 | 17922 | 18688 | 18714 | 19358 | 16589 | 18972 | 19009 | 19862 | 20511 | 19053 | 17657
2939 | 2939 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 11 | 15100 | 15031 | 14601 | 16548 | 16460 | 17049 | 17506 | 16665 | 15578 | 17853 | 18660 | 18630 | 19085 | 16722 | 18921 | 19026 | 19900 | 20286 | 19000 | 17831
2940 | 2940 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 12 | 15052 | 14943 | 14694 | 16477 | 16407 | 16987 | 17368 | 16608 | 15712 | 17799 | 18680 | 18607 | 18998 | 16870 | 18906 | 19020 | 19988 | 20215 | 18960 | 17987
2941 | 2941 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 13 | 15090 | 14818 | 14729 | 16529 | 16463 | 17003 | 17331 | 16469 | 15758 | 17829 | 18739 | 18618 | 18932 | 16921 | 18979 | 19085 | 20074 | 20157 | 18821 | 18032
2942 | 2942 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 14 | 15206 | 14653 | 14833 | 16640 | 16572 | 17081 | 17293 | 16244 | 15872 | 17849 | 18759 | 18635 | 18811 | 17016 | 19080 | 19148 | 20130 | 20015 | 18603 | 18110
2943 | 2943 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 15 | 15581 | 14952 | 15235 | 16923 | 16987 | 17397 | 17486 | 16523 | 16262 | 18229 | 18928 | 18898 | 18939 | 17390 | 19318 | 19512 | 20282 | 20118 | 18846 | 18470
2944 | 2944 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 16 | 16252 | 15521 | 15920 | 17384 | 17694 | 17971 | 17988 | 17032 | 16917 | 18960 | 19268 | 19347 | 19306 | 17990 | 19677 | 20276 | 20580 | 20423 | 19262 | 19045
2945 | 2945 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 17 | 16393 | 15809 | 16427 | 17549 | 18013 | 18205 | 18213 | 17340 | 17428 | 19241 | 19413 | 19612 | 19617 | 18538 | 19911 | 20614 | 20661 | 20737 | 19527 | 19598
2946 | 2946 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 18 | 16332 | 15897 | 16571 | 17692 | 17987 | 18307 | 18356 | 17675 | 17862 | 19297 | 19327 | 20044 | 20006 | 19171 | 20419 | 20736 | 20695 | 21231 | 20200 | 20279
2947 | 2947 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 19 | 16362 | 15753 | 16548 | 17901 | 18145 | 18473 | 18385 | 17646 | 18001 | 19693 | 19705 | 20554 | 20436 | 19529 | 21064 | 21493 | 21453 | 21866 | 20765 | 20742
2948 | 2948 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 20 | 16751 | 16080 | 16796 | 18085 | 18287 | 18973 | 18821 | 18229 | 18379 | 20052 | 20589 | 21431 | 21375 | 20310 | 21722 | 22306 | 22763 | 23046 | 22025 | 21632
2949 | 2949 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 21 | 16625 | 15933 | 16890 | 17926 | 18270 | 19084 | 18834 | 18392 | 18753 | 20407 | 20971 | 22077 | 21973 | 21063 | 22209 | 23111 | 23586 | 23945 | 22959 | 22586
2950 | 2950 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 22 | 15632 | 15051 | 16123 | 16892 | 17218 | 18163 | 17966 | 17664 | 18183 | 19562 | 20315 | 21469 | 21452 | 20701 | 21581 | 22565 | 23252 | 23615 | 22728 | 22368
2951 | 2951 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 23 | 14453 | 14113 | 15169 | 15666 | 15970 | 16991 | 16797 | 16799 | 17343 | 18398 | 19135 | 20442 | 20462 | 19946 | 20546 | 21594 | 22232 | 22715 | 22136 | 21700
2952 | 2952 | 123 | 5 | 3 | Spring | 5 | 2 | Spring | 24 | 13624 | 13439 | 14542 | 14836 | 15052 | 16145 | 15915 | 16143 | 16748 | 17531 | 18226 | 19695 | 19674 | 19410 | 19768 | 20794 | 21384 | 21980 | 21618 | 21196
2953 | 2953 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 1 | 12608 | 13033 | 13526 | 14025 | 14461 | 15011 | 15250 | 15306 | 15642 | 17011 | 17471 | 18560 | 18798 | 18216 | 19529 | 20398 | 20756 | 20991 | 19933 | 19957
2954 | 2954 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 2 | 12311 | 12817 | 13345 | 13739 | 14120 | 14629 | 14820 | 15020 | 15394 | 16612 | 17102 | 18054 | 18250 | 17872 | 19072 | 19889 | 20297 | 20382 | 19518 | 19567
2955 | 2955 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 3 | 12221 | 12656 | 13325 | 13654 | 13967 | 14490 | 14589 | 14807 | 15312 | 16374 | 16830 | 17765 | 17872 | 17685 | 18777 | 19519 | 19893 | 19926 | 19137 | 19327
2956 | 2956 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 4 | 12310 | 12628 | 13475 | 13727 | 13998 | 14469 | 14488 | 14657 | 15321 | 16184 | 16641 | 17393 | 17428 | 17477 | 18363 | 19026 | 19362 | 19284 | 18594 | 18980
2957 | 2957 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 5 | 12974 | 12885 | 14104 | 14312 | 14501 | 15151 | 14810 | 14820 | 15796 | 16460 | 16745 | 17675 | 17379 | 17661 | 18395 | 18932 | 18977 | 18999 | 18260 | 19002
2958 | 2958 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 6 | 14043 | 13085 | 15099 | 15313 | 15451 | 16139 | 15108 | 14799 | 16542 | 17111 | 17083 | 18186 | 17237 | 18062 | 18785 | 19216 | 18852 | 18620 | 17683 | 19253
2959 | 2959 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 7 | 15311 | 13299 | 16187 | 16411 | 16524 | 17268 | 15360 | 14753 | 17426 | 17963 | 17647 | 18967 | 17007 | 18631 | 19233 | 19670 | 19119 | 18191 | 17176 | 19721
2960 | 2960 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 8 | 15897 | 13501 | 16732 | 16757 | 16974 | 17813 | 15769 | 14905 | 17929 | 18315 | 18028 | 19361 | 17167 | 19002 | 19155 | 19737 | 19359 | 18278 | 17090 | 20070
2961 | 2961 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 9 | 15625 | 13754 | 16573 | 16546 | 16947 | 17595 | 16071 | 15121 | 17710 | 18200 | 17817 | 19074 | 17292 | 18585 | 18605 | 19343 | 19031 | 18363 | 16962 | 19620
2962 | 2962 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 10 | 15241 | 13864 | 16316 | 16338 | 16833 | 17235 | 16255 | 15306 | 17541 | 18164 | 17733 | 18806 | 17532 | 18444 | 18532 | 19347 | 19031 | 18645 | 17232 | 19520
2963 | 2963 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 11 | 14903 | 13892 | 16146 | 16197 | 16758 | 16880 | 16184 | 15384 | 17449 | 18147 | 17711 | 18542 | 17463 | 18410 | 18564 | 19411 | 19120 | 18610 | 17427 | 19523
2964 | 2964 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 12 | 14721 | 13954 | 16045 | 16095 | 16723 | 16713 | 16096 | 15459 | 17368 | 18131 | 17687 | 18407 | 17377 | 18361 | 18529 | 19451 | 19159 | 18526 | 17554 | 19485
2965 | 2965 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 13 | 14639 | 13932 | 16045 | 16084 | 16720 | 16619 | 15904 | 15424 | 17335 | 18133 | 17675 | 18297 | 17175 | 18380 | 18538 | 19499 | 19166 | 18332 | 17544 | 19501
2966 | 2966 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 14 | 14447 | 13804 | 15938 | 15937 | 16578 | 16367 | 15461 | 15259 | 17178 | 17931 | 17516 | 17971 | 16762 | 18261 | 18382 | 19345 | 19059 | 17892 | 17398 | 19366
2967 | 2967 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 15 | 14450 | 13917 | 15937 | 16062 | 16495 | 16282 | 15460 | 15355 | 17139 | 17820 | 17510 | 17826 | 16739 | 18213 | 18459 | 19217 | 19021 | 17845 | 17468 | 19303
2968 | 2968 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 16 | 14769 | 14378 | 16171 | 16489 | 16688 | 16569 | 15748 | 15750 | 17280 | 17938 | 17626 | 17982 | 16960 | 18339 | 18990 | 19291 | 19066 | 18024 | 17797 | 19401
2969 | 2969 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 17 | 15216 | 15118 | 16574 | 17079 | 17033 | 17036 | 16297 | 16530 | 17718 | 18320 | 18220 | 18537 | 17435 | 18818 | 19578 | 19621 | 19613 | 18545 | 18595 | 19890
2970 | 2970 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 18 | 15454 | 15541 | 16964 | 17392 | 17140 | 17468 | 16903 | 17244 | 18288 | 18524 | 19156 | 19200 | 18317 | 19632 | 20015 | 19966 | 20685 | 19532 | 19592 | 20745
2971 | 2971 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 19 | 15552 | 15794 | 17450 | 17810 | 17578 | 17764 | 17134 | 17625 | 18894 | 19114 | 19817 | 19846 | 18978 | 20514 | 21007 | 20984 | 21598 | 20382 | 20342 | 21745
2972 | 2972 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 20 | 15915 | 16074 | 17668 | 17948 | 18129 | 18239 | 17733 | 17984 | 19278 | 19969 | 20346 | 20770 | 20081 | 21198 | 21825 | 22316 | 22601 | 21702 | 21303 | 22537
2973 | 2973 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 21 | 15718 | 16139 | 17480 | 17898 | 18026 | 18198 | 17818 | 18306 | 19373 | 20260 | 20917 | 21282 | 20692 | 21648 | 22577 | 23085 | 23604 | 22611 | 22250 | 23167
2974 | 2974 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 22 | 14739 | 15397 | 16478 | 16858 | 17098 | 17331 | 17092 | 17719 | 18535 | 19594 | 20323 | 20741 | 20304 | 21030 | 22050 | 22754 | 23307 | 22422 | 22073 | 22676
2975 | 2975 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 23 | 13557 | 14447 | 15245 | 15574 | 15779 | 16133 | 16191 | 16801 | 17373 | 18377 | 19336 | 19697 | 19604 | 19979 | 21062 | 21723 | 22519 | 21806 | 21389 | 21690
2976 | 2976 | 124 | 5 | 4 | Spring | 5 | 3 | Spring | 24 | 12696 | 13821 | 14412 | 14659 | 14805 | 15243 | 15515 | 16191 | 16529 | 17449 | 18534 | 18881 | 19029 | 19192 | 20239 | 20866 | 21791 | 21278 | 20882 | 20933
2977 | 2977 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 1 | 12676 | 13241 | 14014 | 14440 | 14389 | 15030 | 15179 | 15475 | 16309 | 17092 | 17937 | 18450 | 18090 | 19306 | 20227 | 20626 | 21263 | 20016 | 20046 | 21228
2978 | 2978 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 2 | 12346 | 13062 | 13739 | 14099 | 14146 | 14602 | 14895 | 15232 | 15971 | 16738 | 17520 | 17914 | 17743 | 18853 | 19723 | 20166 | 20742 | 19605 | 19656 | 20731
2979 | 2979 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 3 | 12159 | 13038 | 13652 | 13944 | 13989 | 14374 | 14682 | 15154 | 15799 | 16483 | 17274 | 17551 | 17416 | 18560 | 19355 | 19762 | 20363 | 19214 | 19411 | 20375
2980 | 2980 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 4 | 12188 | 13190 | 13747 | 14004 | 14099 | 14320 | 14579 | 15216 | 15709 | 16374 | 17003 | 17179 | 17054 | 18204 | 18912 | 19276 | 19740 | 18691 | 19084 | 19852
2981 | 2981 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 5 | 12577 | 13777 | 14293 | 14480 | 14465 | 14637 | 14736 | 15687 | 16131 | 16515 | 17175 | 17171 | 16897 | 18252 | 18831 | 18898 | 19430 | 18341 | 19081 | 19706
2982 | 2982 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 6 | 13049 | 14777 | 15299 | 15462 | 15231 | 14983 | 14777 | 16506 | 16922 | 16954 | 17654 | 17112 | 16524 | 18688 | 19155 | 18807 | 19399 | 17770 | 19324 | 19944
2983 | 2983 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 7 | 13465 | 15888 | 16418 | 16556 | 16165 | 15257 | 14766 | 17448 | 17715 | 17576 | 18265 | 16943 | 16160 | 19161 | 19634 | 19083 | 19628 | 17251 | 19769 | 20268
2984 | 2984 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 8 | 14128 | 16652 | 17013 | 17233 | 16854 | 15871 | 15139 | 18193 | 18103 | 18203 | 18700 | 17337 | 16320 | 19317 | 19941 | 19532 | 19935 | 17367 | 20321 | 20353
2985 | 2985 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 9 | 14963 | 16879 | 17210 | 17602 | 17064 | 16544 | 15739 | 18379 | 18236 | 18376 | 18842 | 17878 | 16633 | 19167 | 19948 | 19609 | 20082 | 17627 | 20260 | 20160
2986 | 2986 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 10 | 15354 | 16872 | 17249 | 17717 | 17131 | 16956 | 16146 | 18428 | 18354 | 18504 | 18869 | 18362 | 17091 | 19343 | 20201 | 19851 | 20188 | 18149 | 20414 | 20382
2987 | 2987 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 11 | 15462 | 16892 | 17290 | 17799 | 17231 | 17035 | 16368 | 18463 | 18510 | 18599 | 18870 | 18491 | 17455 | 19587 | 20477 | 20142 | 20367 | 18562 | 20637 | 20670
2988 | 2988 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 12 | 15333 | 16773 | 17164 | 17722 | 17174 | 16913 | 16402 | 18328 | 18427 | 18518 | 18745 | 18385 | 17569 | 19538 | 20505 | 20158 | 20345 | 18679 | 20583 | 20633
2989 | 2989 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 13 | 15037 | 16651 | 17030 | 17614 | 17048 | 16603 | 16253 | 18196 | 18290 | 18396 | 18627 | 18067 | 17455 | 19415 | 20412 | 20049 | 20266 | 18537 | 20467 | 20505
2990 | 2990 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 14 | 14662 | 16577 | 16937 | 17527 | 16955 | 16236 | 16170 | 18121 | 18101 | 18334 | 18463 | 17670 | 17339 | 19275 | 20271 | 19952 | 20064 | 18404 | 20350 | 20346
2991 | 2991 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 15 | 14840 | 16772 | 17252 | 17637 | 17171 | 16432 | 16462 | 18284 | 18374 | 18531 | 18525 | 17832 | 17598 | 19531 | 20326 | 20096 | 20071 | 18654 | 20467 | 20583
2992 | 2992 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 16 | 15099 | 16963 | 17581 | 17812 | 17346 | 16705 | 16842 | 18425 | 18793 | 18649 | 18532 | 18019 | 17897 | 20014 | 20350 | 20099 | 19955 | 18927 | 20506 | 21028
2993 | 2993 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 17 | 15296 | 16941 | 17751 | 17771 | 17577 | 16838 | 17194 | 18463 | 18976 | 18809 | 18557 | 18129 | 18344 | 20195 | 20268 | 20280 | 20040 | 19328 | 20586 | 21228
2994 | 2994 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 18 | 15340 | 16907 | 17671 | 17498 | 17863 | 17044 | 17477 | 18593 | 18984 | 19310 | 18687 | 18608 | 18925 | 20246 | 20226 | 20993 | 20425 | 19955 | 21076 | 21337
2995 | 2995 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 19 | 15209 | 17097 | 17787 | 17649 | 17994 | 16971 | 17559 | 18907 | 19356 | 19640 | 19182 | 18937 | 19270 | 20918 | 20937 | 21616 | 21257 | 20429 | 21808 | 22164
2996 | 2996 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 20 | 15503 | 17256 | 17856 | 18121 | 18178 | 17511 | 17857 | 19202 | 19635 | 20033 | 19995 | 19899 | 20005 | 21639 | 22170 | 22527 | 22413 | 21352 | 22563 | 23047
2997 | 2997 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 21 | 15370 | 17075 | 17799 | 17997 | 18311 | 17555 | 18138 | 19243 | 19939 | 20508 | 20525 | 20460 | 20728 | 22365 | 22922 | 23521 | 23410 | 22318 | 23222 | 24006
2998 | 2998 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 22 | 14492 | 16021 | 16708 | 17012 | 17378 | 16757 | 17477 | 18330 | 19053 | 19836 | 20015 | 19977 | 20341 | 21755 | 22512 | 23146 | 23187 | 22087 | 22684 | 23554
2999 | 2999 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 23 | 13551 | 14843 | 15465 | 15734 | 16274 | 15892 | 16603 | 17201 | 17864 | 18895 | 19087 | 19256 | 19576 | 20761 | 21476 | 22342 | 22386 | 21410 | 21706 | 22653
3000 | 3000 | 125 | 5 | 5 | Spring | 5 | 4 | Spring | 24 | 12877 | 14023 | 14550 | 14765 | 15411 | 15213 | 15989 | 16349 | 16977 | 18078 | 18290 | 18656 | 19021 | 19926 | 20609 | 21632 | 21688 | 20891 | 20945 | 21865
3001 | 3001 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 1 | 12787 | 13477 | 14211 | 14216 | 14662 | 14820 | 15150 | 15938 | 16717 | 17338 | 17341 | 17673 | 18107 | 19765 | 20222 | 20966 | 20543 | 19932 | 21087 | 21774
3002 | 3002 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 2 | 12570 | 13234 | 13898 | 13978 | 14357 | 14560 | 14932 | 15617 | 16330 | 16959 | 16809 | 17340 | 17768 | 19293 | 19791 | 20451 | 19886 | 19555 | 20609 | 21248
3003 | 3003 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 3 | 12394 | 13148 | 13746 | 13824 | 14230 | 14350 | 14859 | 15457 | 16096 | 16735 | 16464 | 17027 | 17576 | 18935 | 19400 | 20078 | 19418 | 19300 | 20254 | 20821
3004 | 3004 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 4 | 12393 | 13267 | 13841 | 13979 | 14262 | 14303 | 14986 | 15448 | 15982 | 16569 | 16084 | 16729 | 17429 | 18553 | 18970 | 19504 | 18728 | 19004 | 19757 | 20269
3005 | 3005 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 5 | 12624 | 13809 | 14322 | 14355 | 14781 | 14486 | 15492 | 15906 | 16283 | 16823 | 15972 | 16634 | 17634 | 18531 | 18645 | 19237 | 18239 | 19023 | 19626 | 20046
3006 | 3006 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 6 | 12822 | 14831 | 15290 | 15148 | 15653 | 14540 | 16347 | 16749 | 17006 | 17373 | 15744 | 16320 | 18068 | 18901 | 18591 | 19224 | 17623 | 19275 | 19860 | 20200
3007 | 3007 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 7 | 13155 | 16068 | 16492 | 16216 | 16683 | 14651 | 17434 | 17705 | 18009 | 18155 | 15747 | 16117 | 18760 | 19532 | 19001 | 19588 | 17340 | 19824 | 20280 | 20648
3008 | 3008 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 8 | 13623 | 16717 | 17193 | 16934 | 17296 | 15029 | 18187 | 18160 | 18631 | 18622 | 16322 | 16343 | 19392 | 19882 | 19499 | 19946 | 17780 | 20398 | 20407 | 20925
3009 | 3009 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 9 | 14050 | 16665 | 17298 | 16836 | 17282 | 15321 | 18063 | 17965 | 18667 | 18430 | 16590 | 16444 | 19153 | 19683 | 19366 | 19868 | 17960 | 20119 | 20003 | 20665
3010 | 3010 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 10 | 14025 | 16318 | 17037 | 16510 | 16864 | 15331 | 17716 | 17678 | 18480 | 18060 | 16521 | 16524 | 18885 | 19550 | 19214 | 19600 | 17976 | 19883 | 19830 | 20578
3011 | 3011 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 11 | 13974 | 16114 | 16888 | 16333 | 16541 | 15338 | 17545 | 17564 | 18319 | 17864 | 16420 | 16609 | 18795 | 19543 | 19219 | 19501 | 17955 | 19826 | 19840 | 20610
3012 | 3012 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 12 | 14025 | 16043 | 16878 | 16313 | 16415 | 15448 | 17489 | 17515 | 18270 | 17819 | 16357 | 16750 | 18748 | 19605 | 19275 | 19513 | 17901 | 19815 | 19840 | 20696
3013 | 3013 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 13 | 14035 | 16088 | 16933 | 16344 | 16451 | 15468 | 17535 | 17549 | 18328 | 17880 | 16145 | 16771 | 18798 | 19681 | 19321 | 19566 | 17691 | 19857 | 19870 | 20757
3014 | 3014 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 14 | 13915 | 15983 | 16818 | 16277 | 16293 | 15360 | 17436 | 17413 | 18199 | 17697 | 15839 | 16636 | 18673 | 19515 | 19200 | 19343 | 17356 | 19706 | 19683 | 20574
3015 | 3015 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 15 | 14182 | 16243 | 16900 | 16482 | 16376 | 15625 | 17572 | 17680 | 18260 | 17737 | 15795 | 16878 | 18780 | 19545 | 19320 | 19330 | 17281 | 19792 | 19891 | 20588
3016 | 3016 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 16 | 14590 | 16545 | 17077 | 16695 | 16488 | 16006 | 17715 | 18110 | 18364 | 17758 | 15936 | 17194 | 18846 | 19574 | 19319 | 19229 | 17342 | 19824 | 20327 | 20575
3017 | 3017 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 17 | 15191 | 16958 | 17330 | 17141 | 16735 | 16651 | 18032 | 18487 | 18595 | 18066 | 16470 | 17872 | 19194 | 19783 | 19790 | 19557 | 17944 | 20198 | 20811 | 20807
3018 | 3018 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 18 | 15384 | 17039 | 17231 | 17522 | 16850 | 17087 | 18288 | 18603 | 18567 | 18322 | 17242 | 18552 | 19775 | 19897 | 20657 | 20070 | 18838 | 20850 | 21083 | 21001
3019 | 3019 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 19 | 15495 | 17276 | 17510 | 17772 | 17206 | 17310 | 18732 | 19069 | 18985 | 18895 | 17624 | 18991 | 20515 | 20705 | 21397 | 21000 | 19506 | 21735 | 22073 | 21973
3020 | 3020 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 20 | 15760 | 17359 | 17976 | 17987 | 17704 | 17638 | 19046 | 19364 | 19736 | 19647 | 18010 | 19717 | 21140 | 21908 | 22301 | 22173 | 20262 | 22538 | 23006 | 23357
3021 | 3021 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 21 | 15815 | 17265 | 17797 | 18050 | 17738 | 17861 | 19021 | 19553 | 19919 | 20042 | 18700 | 20353 | 21533 | 22572 | 23222 | 23110 | 21396 | 23170 | 23943 | 24285
3022 | 3022 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 22 | 15008 | 16149 | 16794 | 17099 | 16898 | 17164 | 18065 | 18618 | 19172 | 19482 | 18230 | 19910 | 20837 | 22103 | 22804 | 22847 | 21204 | 22610 | 23470 | 23998
3023 | 3023 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 23 | 14072 | 14903 | 15512 | 16033 | 15796 | 16264 | 16906 | 17454 | 17997 | 18530 | 17419 | 19123 | 19777 | 21046 | 21979 | 22037 | 20532 | 21615 | 22555 | 23018
3024 | 3024 | 126 | 5 | 6 | Spring | 5 | 5 | Spring | 24 | 13450 | 13990 | 14537 | 15175 | 14959 | 15642 | 16040 | 16548 | 17067 | 17709 | 16673 | 18557 | 18982 | 20173 | 21253 | 21338 | 19856 | 20853 | 21762 | 22196
3025 | 3025 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 1 | 12525 | 13443 | 13766 | 14199 | 13979 | 14594 | 15357 | 16045 | 16326 | 16569 | 15971 | 17421 | 18677 | 19541 | 20354 | 19970 | 18683 | 20745 | 21455 | 21598
3026 | 3026 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 2 | 12390 | 13162 | 13565 | 13938 | 13574 | 14404 | 15065 | 15703 | 16028 | 16081 | 15570 | 17132 | 18279 | 19145 | 19871 | 19373 | 18197 | 20292 | 20938 | 21148
3027 | 3027 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 3 | 12352 | 13009 | 13414 | 13814 | 13338 | 14333 | 14913 | 15484 | 15781 | 15755 | 15284 | 16953 | 17993 | 18766 | 19507 | 18903 | 17806 | 19925 | 20506 | 20696
3028 | 3028 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 4 | 12509 | 13104 | 13576 | 13883 | 13238 | 14483 | 14942 | 15443 | 15761 | 15432 | 14985 | 16858 | 17696 | 18381 | 18979 | 18253 | 17248 | 19451 | 19966 | 20146
3029 | 3029 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 5 | 13096 | 13602 | 13960 | 14414 | 13408 | 15015 | 15447 | 15791 | 15966 | 15393 | 14802 | 17118 | 17806 | 18112 | 18761 | 17793 | 16820 | 19342 | 19754 | 19677
3030 | 3030 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 6 | 14109 | 14604 | 14818 | 15344 | 13569 | 15936 | 16375 | 16598 | 16488 | 15278 | 14412 | 17649 | 18309 | 18147 | 18837 | 17243 | 16167 | 19627 | 19950 | 19512
3031 | 3031 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 7 | 15385 | 15875 | 15967 | 16449 | 13996 | 17085 | 17433 | 17692 | 17312 | 15391 | 14311 | 18435 | 18967 | 18639 | 19269 | 17019 | 15782 | 20097 | 20444 | 19856
3032 | 3032 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 8 | 16183 | 16637 | 16733 | 17070 | 14779 | 17862 | 17944 | 18329 | 17974 | 16042 | 14905 | 19112 | 19203 | 19188 | 19660 | 17496 | 16260 | 20246 | 20739 | 20344
3033 | 3033 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 9 | 16217 | 16823 | 16731 | 17057 | 15256 | 17808 | 17838 | 18345 | 17882 | 16400 | 15321 | 18957 | 18927 | 19119 | 19648 | 17756 | 16746 | 19902 | 20542 | 20253
3034 | 3034 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 10 | 15962 | 16711 | 16537 | 16758 | 15225 | 17580 | 17671 | 18278 | 17752 | 16450 | 15663 | 18806 | 18839 | 19090 | 19507 | 17884 | 17145 | 19859 | 20593 | 20273
3035 | 3035 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 11 | 15806 | 16639 | 16426 | 16549 | 15101 | 17468 | 17615 | 18265 | 17720 | 16411 | 15934 | 18774 | 18868 | 19157 | 19472 | 17925 | 17372 | 19938 | 20698 | 20388
3036 | 3036 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 12 | 15749 | 16614 | 16385 | 16458 | 15005 | 17394 | 17552 | 18269 | 17728 | 16323 | 16170 | 18730 | 18856 | 19184 | 19463 | 17869 | 17589 | 19921 | 20760 | 20428
3037 | 3037 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 13 | 15765 | 16644 | 16405 | 16486 | 14768 | 17422 | 17573 | 18318 | 17759 | 16100 | 16292 | 18758 | 18866 | 19219 | 19506 | 17641 | 17669 | 19939 | 20809 | 20473
3038 | 3038 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 14 | 15454 | 16322 | 16155 | 16140 | 14288 | 17140 | 17256 | 18004 | 17475 | 15615 | 16156 | 18447 | 18499 | 18919 | 19102 | 17119 | 17487 | 19568 | 20448 | 20154
3039 | 3039 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 15 | 15600 | 16373 | 16343 | 16204 | 14249 | 17261 | 17505 | 18046 | 17623 | 15556 | 16420 | 18539 | 18703 | 19025 | 19074 | 17025 | 17718 | 19763 | 20436 | 20236
3040 | 3040 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 16 | 15724 | 16443 | 16465 | 16224 | 14399 | 17308 | 17796 | 18060 | 17683 | 15605 | 16614 | 18516 | 19111 | 18942 | 18881 | 16989 | 17886 | 20095 | 20325 | 20101
3041 | 3041 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 17 | 16002 | 16702 | 16908 | 16482 | 14970 | 17639 | 18177 | 18300 | 18129 | 16130 | 17219 | 18878 | 19576 | 19413 | 19213 | 17599 | 18455 | 20582 | 20557 | 20579
3042 | 3042 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 18 | 16129 | 16627 | 17246 | 16584 | 15511 | 17907 | 18309 | 18277 | 18769 | 16878 | 17882 | 19436 | 19779 | 20284 | 19736 | 18496 | 19247 | 20876 | 20776 | 21519
3043 | 3043 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 19 | 16416 | 16858 | 17428 | 16881 | 15527 | 18300 | 18712 | 18603 | 19156 | 17152 | 18144 | 20096 | 20530 | 20951 | 20604 | 19120 | 19812 | 21824 | 21702 | 22330
3044 | 3044 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 20 | 16597 | 17280 | 17605 | 17344 | 15589 | 18596 | 18964 | 19315 | 19520 | 17447 | 18495 | 20671 | 21239 | 21790 | 21715 | 19853 | 20475 | 22758 | 23097 | 23347
3045 | 3045 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 21 | 16366 | 17068 | 17599 | 17311 | 15802 | 18495 | 19052 | 19388 | 19866 | 18013 | 19004 | 20971 | 21851 | 22608 | 22562 | 20925 | 21355 | 23645 | 23981 | 24414
3046 | 3046 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 22 | 15321 | 16052 | 16668 | 16486 | 15068 | 17543 | 18105 | 18617 | 19153 | 17520 | 18469 | 20256 | 21219 | 22193 | 22296 | 20733 | 21042 | 23191 | 23719 | 24156
3047 | 3047 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 23 | 14144 | 14770 | 15588 | 15384 | 14126 | 16367 | 16900 | 17410 | 18187 | 16681 | 17632 | 19175 | 20198 | 21351 | 21482 | 20047 | 20299 | 22271 | 22726 | 23386
3048 | 3048 | 127 | 5 | 7 | Spring | 5 | 6 | Spring | 24 | 13325 | 13810 | 14722 | 14539 | 13311 | 15497 | 15981 | 16443 | 17346 | 15914 | 16916 | 18356 | 19342 | 20587 | 20756 | 19347 | 19645 | 21454 | 21887 | 22654
3049 | 3049 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 1 | 12627 | 13129 | 13821 | 13653 | 13208 | 14840 | 15518 | 15766 | 16443 | 15398 | 16424 | 18033 | 19005 | 19730 | 19461 | 18272 | 19105 | 21174 | 21353 | 21830
3050 | 3050 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 2 | 12407 | 12919 | 13572 | 13247 | 12870 | 14554 | 15184 | 15472 | 16098 | 15009 | 16075 | 17645 | 18566 | 19263 | 18861 | 17786 | 18686 | 20667 | 20888 | 21297
3051 | 3051 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 3 | 12357 | 12822 | 13491 | 13056 | 12711 | 14449 | 15013 | 15285 | 15928 | 14779 | 15839 | 17411 | 18253 | 18953 | 18439 | 17440 | 18355 | 20267 | 20473 | 20912
3052 | 3052 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 4 | 12482 | 12964 | 13576 | 12979 | 12641 | 14515 | 15020 | 15325 | 15834 | 14532 | 15659 | 17177 | 17932 | 18473 | 17830 | 16914 | 17949 | 19741 | 19926 | 20252
3053 | 3053 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 5 | 12998 | 13346 | 14100 | 13150 | 12675 | 15040 | 15400 | 15575 | 16137 | 14392 | 15842 | 17337 | 17950 | 18295 | 17398 | 16500 | 17859 | 19527 | 19449 | 19868
3054 | 3054 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 6 | 14043 | 14219 | 15048 | 13340 | 12578 | 16008 | 16256 | 16182 | 16780 | 14055 | 16371 | 17905 | 18391 | 18413 | 16879 | 15867 | 18100 | 19728 | 19275 | 19782
3055 | 3055 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 7 | 15164 | 15245 | 16019 | 13625 | 12562 | 16927 | 17216 | 16905 | 17494 | 13834 | 17159 | 18457 | 18933 | 18726 | 16521 | 15329 | 18679 | 20062 | 19455 | 19946
3056 | 3056 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 8 | 15680 | 15819 | 16484 | 14247 | 13092 | 17266 | 17704 | 17427 | 17839 | 14281 | 17730 | 18563 | 19174 | 18962 | 16834 | 15642 | 19157 | 20204 | 19767 | 20135
3057 | 3057 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 9 | 15596 | 15767 | 16422 | 14648 | 13587 | 17087 | 17663 | 17270 | 17631 | 14632 | 17837 | 18214 | 18962 | 18869 | 17016 | 16038 | 19137 | 19928 | 19581 | 20021
3058 | 3058 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 10 | 15396 | 15577 | 16152 | 14634 | 13870 | 16930 | 17601 | 17159 | 17397 | 14993 | 17968 | 18141 | 18964 | 18745 | 17163 | 16457 | 19308 | 19990 | 19627 | 19935
3059 | 3059 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 11 | 15212 | 15380 | 15875 | 14441 | 14023 | 16791 | 17512 | 17052 | 17213 | 15191 | 18161 | 18099 | 18978 | 18635 | 17133 | 16619 | 19574 | 20028 | 19674 | 19872
3060 | 3060 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 12 | 15047 | 15249 | 15701 | 14239 | 14159 | 16639 | 17429 | 16955 | 17070 | 15342 | 18243 | 17981 | 18942 | 18527 | 16994 | 16735 | 19679 | 20006 | 19638 | 19784
3061 | 3061 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 13 | 15026 | 15211 | 15679 | 13963 | 14224 | 16610 | 17429 | 16944 | 17061 | 15414 | 18449 | 17954 | 18935 | 18520 | 16717 | 16778 | 19868 | 20008 | 19628 | 19796
3062 | 3062 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 14 | 15004 | 15210 | 15590 | 13757 | 14374 | 16551 | 17375 | 16940 | 16963 | 15541 | 18553 | 17865 | 18852 | 18375 | 16452 | 16869 | 19951 | 19894 | 19562 | 19634
3063 | 3063 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 15 | 15175 | 15307 | 15584 | 13649 | 14595 | 16726 | 17343 | 17020 | 16925 | 15728 | 18751 | 18011 | 18800 | 18279 | 16287 | 17034 | 20131 | 19812 | 19568 | 19515
3064 | 3064 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 16 | 15441 | 15526 | 15694 | 13851 | 14926 | 17099 | 17447 | 17142 | 16933 | 16012 | 18956 | 18452 | 18807 | 18185 | 16343 | 17254 | 20260 | 19777 | 19527 | 19364
3065 | 3065 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 17 | 15930 | 16056 | 16027 | 14506 | 15594 | 17580 | 17770 | 17675 | 17322 | 16695 | 19489 | 19009 | 19096 | 18599 | 17035 | 17909 | 20813 | 20088 | 20086 | 19772
3066 | 3066 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 18 | 16181 | 16487 | 16198 | 15164 | 16176 | 17845 | 17864 | 18413 | 17709 | 17455 | 20067 | 19339 | 19348 | 19253 | 18061 | 18858 | 21536 | 20432 | 21177 | 20494
3067 | 3067 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 19 | 16471 | 16761 | 16569 | 15262 | 16390 | 18322 | 18264 | 18846 | 18305 | 17758 | 20197 | 20139 | 20188 | 20171 | 18755 | 19505 | 21864 | 21468 | 22083 | 21563
3068 | 3068 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 20 | 16528 | 16891 | 16992 | 15290 | 16427 | 18536 | 18927 | 19118 | 18970 | 18017 | 20290 | 20776 | 21330 | 21223 | 19452 | 20121 | 22308 | 22860 | 23091 | 22793
3069 | 3069 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 21 | 16379 | 16862 | 16920 | 15454 | 16561 | 18567 | 18926 | 19366 | 19251 | 18440 | 20561 | 21293 | 21885 | 21995 | 20455 | 20955 | 22949 | 23720 | 24144 | 23816
3070 | 3070 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 22 | 15288 | 15944 | 16076 | 14708 | 15792 | 17585 | 18097 | 18616 | 18662 | 17869 | 19700 | 20604 | 21411 | 21683 | 20226 | 20632 | 22307 | 23432 | 23881 | 23681
3071 | 3071 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 23 | 14029 | 14880 | 14972 | 13764 | 14833 | 16362 | 16868 | 17611 | 17663 | 17026 | 18503 | 19537 | 20313 | 20850 | 19522 | 19876 | 21192 | 22432 | 23112 | 22921
3072 | 3072 | 128 | 5 | 8 | Spring | 5 | 7 | Spring | 24 | 13147 | 14046 | 14148 | 12981 | 14085 | 15459 | 15913 | 16780 | 16845 | 16326 | 17521 | 18699 | 19444 | 20138 | 18834 | 19246 | 20262 | 21613 | 22400 | 22248
3073 | 3073 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 1 | 12829 | 13322 | 13468 | 13084 | 13833 | 15131 | 15382 | 16016 | 15983 | 16007 | 17204 | 18500 | 19021 | 19057 | 18000 | 18880 | 20263 | 21266 | 21759 | 21076
3074 | 3074 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 2 | 12531 | 13061 | 13058 | 12731 | 13543 | 14785 | 15077 | 15664 | 15485 | 15648 | 16736 | 18055 | 18608 | 18451 | 17506 | 18442 | 19684 | 20783 | 21207 | 20409
3075 | 3075 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 3 | 12411 | 12974 | 12875 | 12571 | 13396 | 14625 | 14905 | 15511 | 15216 | 15432 | 16431 | 17760 | 18285 | 18048 | 17169 | 18117 | 19264 | 20372 | 20824 | 19935
3076 | 3076 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 4 | 12516 | 13084 | 12822 | 12511 | 13429 | 14675 | 14998 | 15472 | 14961 | 15309 | 16204 | 17498 | 17966 | 17493 | 16682 | 17736 | 18755 | 19849 | 20181 | 19211
3077 | 3077 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 5 | 13041 | 13625 | 13036 | 12587 | 13875 | 15123 | 15323 | 15871 | 15010 | 15577 | 16342 | 17623 | 17784 | 17148 | 16337 | 17710 | 18574 | 19422 | 19839 | 18657
3078 | 3078 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 6 | 14030 | 14587 | 13252 | 12516 | 14741 | 16023 | 15991 | 16604 | 14961 | 16163 | 16924 | 18140 | 17875 | 16679 | 15735 | 17979 | 18791 | 19259 | 19755 | 17979
3079 | 3079 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 7 | 15286 | 15755 | 13737 | 12682 | 15996 | 17185 | 16939 | 17555 | 15109 | 17180 | 17785 | 18894 | 18403 | 16517 | 15372 | 18732 | 19282 | 19589 | 20058 | 17667
3080 | 3080 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 8 | 16048 | 16400 | 14563 | 13392 | 16783 | 17856 | 17655 | 18098 | 15772 | 17953 | 18343 | 19329 | 18942 | 17013 | 15868 | 19368 | 19679 | 20068 | 20409 | 18128
3081 | 3081 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 9 | 16214 | 16396 | 15058 | 13977 | 17033 | 17888 | 17580 | 17990 | 16127 | 18133 | 18485 | 19201 | 18844 | 17258 | 16332 | 19411 | 19755 | 19936 | 20353 | 18344
3082 | 3082 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 10 | 15974 | 15953 | 14859 | 14079 | 16943 | 17630 | 17277 | 17576 | 16037 | 18082 | 18624 | 19022 | 18685 | 17209 | 16554 | 19407 | 19983 | 19796 | 20088 | 18353
3083 | 3083 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 11 | 15769 | 15597 | 14595 | 14141 | 16982 | 17460 | 17090 | 17294 | 15847 | 18196 | 18827 | 18940 | 18600 | 17101 | 16645 | 19583 | 20245 | 19773 | 19956 | 18293
3084 | 3084 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 12 | 15712 | 15499 | 14458 | 14334 | 17106 | 17441 | 17061 | 17208 | 15735 | 18343 | 19049 | 18962 | 18613 | 17026 | 16825 | 19751 | 20485 | 19800 | 19933 | 18232
3085 | 3085 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 13 | 15711 | 15504 | 14201 | 14432 | 17338 | 17462 | 17068 | 17229 | 15486 | 18570 | 19321 | 18987 | 18622 | 16773 | 16893 | 19971 | 20755 | 19813 | 19957 | 17974
3086 | 3086 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 14 | 15579 | 15357 | 13938 | 14516 | 17412 | 17350 | 17003 | 17069 | 15209 | 18618 | 19448 | 18844 | 18526 | 16457 | 16930 | 19991 | 20854 | 19690 | 19739 | 17638
3087 | 3087 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 15 | 15477 | 15272 | 13762 | 14658 | 17567 | 17253 | 17021 | 16956 | 14998 | 18754 | 19688 | 18718 | 18485 | 16225 | 17026 | 20092 | 21048 | 19627 | 19549 | 17388
3088 | 3088 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 16 | 15716 | 15478 | 14050 | 15084 | 17930 | 17449 | 17236 | 17073 | 15219 | 19053 | 20363 | 18831 | 18580 | 16373 | 17334 | 20318 | 21710 | 19666 | 19481 | 17499
3089 | 3089 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 17 | 16072 | 15828 | 14694 | 15748 | 18452 | 17774 | 17765 | 17462 | 15827 | 19572 | 20736 | 19123 | 19138 | 17065 | 17984 | 20872 | 22108 | 20226 | 19890 | 18195
3090 | 3090 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 18 | 16041 | 15866 | 15196 | 16197 | 18680 | 17770 | 18368 | 17690 | 16586 | 20024 | 20764 | 19261 | 20036 | 17985 | 18818 | 21509 | 22313 | 21220 | 20530 | 19173
3091 | 3091 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 19 | 16283 | 16128 | 15178 | 16298 | 18511 | 18055 | 18676 | 18130 | 16819 | 20006 | 21087 | 19940 | 20652 | 18546 | 19355 | 21717 | 22933 | 22043 | 21514 | 19860
3092 | 3092 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 20 | 16664 | 16494 | 15155 | 16302 | 18388 | 18681 | 18898 | 18718 | 17020 | 19997 | 21266 | 20999 | 21418 | 19173 | 19949 | 22124 | 23429 | 23038 | 22737 | 20643
3093 | 3093 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 21 | 16436 | 16425 | 15299 | 16419 | 18291 | 18634 | 19090 | 18922 | 17488 | 20205 | 21716 | 21475 | 22152 | 20126 | 20753 | 22731 | 24292 | 24088 | 23765 | 21834
3094 | 3094 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 22 | 15365 | 15569 | 14538 | 15631 | 17183 | 17761 | 18289 | 18262 | 16918 | 19317 | 20811 | 20938 | 21665 | 19856 | 20390 | 22077 | 23629 | 23808 | 23623 | 21727
3095 | 3095 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 23 | 14093 | 14453 | 13564 | 14659 | 15875 | 16480 | 17231 | 17224 | 16058 | 18075 | 19539 | 19795 | 20803 | 19108 | 19592 | 20936 | 22515 | 23002 | 22830 | 21074
3096 | 3096 | 129 | 5 | 9 | Spring | 5 | 8 | Spring | 24 | 13174 | 13617 | 12757 | 13905 | 14844 | 15503 | 16371 | 16371 | 15299 | 17074 | 18479 | 18888 | 20045 | 18394 | 18931 | 19976 | 21539 | 22280 | 22136 | 20417
3097 | 3097 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 1 | 12570 | 12860 | 12819 | 13580 | 14137 | 14873 | 15521 | 15447 | 14907 | 16614 | 18153 | 18353 | 19251 | 17519 | 18469 | 19847 | 21345 | 21520 | 20870 | 19277
3098 | 3098 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 2 | 12354 | 12468 | 12486 | 13299 | 13770 | 14591 | 15186 | 14969 | 14520 | 16172 | 17559 | 17970 | 18784 | 17044 | 18046 | 19292 | 20649 | 20969 | 20212 | 18753
3099 | 3099 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 3 | 12229 | 12268 | 12311 | 13134 | 13543 | 14410 | 15031 | 14696 | 14270 | 15871 | 17215 | 17646 | 18461 | 16699 | 17711 | 18857 | 20155 | 20571 | 19717 | 18353
3100 | 3100 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 4 | 12373 | 12224 | 12246 | 13161 | 13581 | 14507 | 15005 | 14462 | 14082 | 15659 | 16888 | 17398 | 18052 | 16255 | 17366 | 18385 | 19566 | 19960 | 19001 | 17768
3101 | 3101 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 5 | 12783 | 12390 | 12277 | 13547 | 14030 | 14789 | 15369 | 14466 | 14013 | 15758 | 16990 | 17278 | 17967 | 15947 | 17371 | 18227 | 19352 | 19633 | 18453 | 17294
3102 | 3102 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 6 | 13681 | 12624 | 12220 | 14414 | 14995 | 15468 | 16139 | 14455 | 13744 | 16366 | 17520 | 17466 | 18168 | 15404 | 17688 | 18489 | 19570 | 19581 | 17800 | 16587
3103 | 3103 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 7 | 14937 | 13179 | 12463 | 15747 | 16225 | 16484 | 17196 | 14733 | 13787 | 17335 | 18522 | 18106 | 18743 | 15116 | 18512 | 19057 | 20312 | 19953 | 17531 | 16186
3104 | 3104 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 8 | 15721 | 14062 | 13254 | 16600 | 17025 | 17272 | 17819 | 15507 | 14479 | 18008 | 19350 | 18728 | 19202 | 15660 | 19194 | 19507 | 20933 | 20324 | 18021 | 16712
3105 | 3105 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 9 | 15692 | 14585 | 13912 | 16916 | 17289 | 17293 | 17822 | 16003 | 14877 | 18302 | 19716 | 18623 | 19127 | 16103 | 19220 | 19560 | 20977 | 20226 | 18208 | 17132
3106 | 3106 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 10 | 15208 | 14308 | 13940 | 16715 | 17254 | 16902 | 17335 | 15806 | 14953 | 18365 | 19876 | 18328 | 18727 | 16232 | 19132 | 19667 | 21182 | 19875 | 18127 | 17306
3107 | 3107 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 11 | 14950 | 14043 | 14006 | 16758 | 17382 | 16709 | 17046 | 15619 | 15091 | 18566 | 20129 | 18242 | 18552 | 16320 | 19306 | 19935 | 21524 | 19742 | 18069 | 17430
3108 | 3108 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 12 | 14863 | 13904 | 14198 | 16887 | 17564 | 16669 | 16953 | 15505 | 15291 | 18780 | 20441 | 18245 | 18495 | 16499 | 19463 | 20179 | 21862 | 19722 | 18012 | 17616
3109 | 3109 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 13 | 14921 | 13723 | 14372 | 17193 | 17910 | 16746 | 17046 | 15328 | 15462 | 19124 | 20753 | 18330 | 18586 | 16645 | 19760 | 20524 | 22186 | 19817 | 17830 | 17753
3110 | 3110 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 14 | 14876 | 13460 | 14473 | 17281 | 18077 | 16703 | 16907 | 15067 | 15548 | 19277 | 20831 | 18253 | 18405 | 16702 | 19798 | 20632 | 22268 | 19618 | 17509 | 17794
3111 | 3111 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 15 | 15066 | 13449 | 14777 | 17610 | 18507 | 16888 | 16960 | 15031 | 15837 | 19678 | 21088 | 18392 | 18408 | 16968 | 20068 | 21011 | 22498 | 19594 | 17426 | 18046
3112 | 3112 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 16 | 15330 | 13688 | 15152 | 17934 | 19065 | 17069 | 17040 | 15215 | 16159 | 20305 | 21305 | 18456 | 18357 | 17234 | 20251 | 21637 | 22621 | 19481 | 17487 | 18285
3113 | 3113 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 17 | 15860 | 14326 | 15803 | 18446 | 19380 | 17596 | 17429 | 15812 | 16827 | 20667 | 21622 | 19005 | 18770 | 17880 | 20805 | 22032 | 22976 | 19897 | 18173 | 18926
3114 | 3114 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 18 | 16091 | 14719 | 16105 | 18564 | 19287 | 18095 | 17538 | 16433 | 17382 | 20585 | 21661 | 19770 | 19239 | 18630 | 21352 | 22147 | 23074 | 20456 | 19072 | 19726
3115 | 3115 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 19 | 16231 | 14653 | 16136 | 18337 | 19310 | 18342 | 17892 | 16572 | 17518 | 20797 | 21887 | 20306 | 19968 | 19093 | 21491 | 22699 | 23603 | 21400 | 19727 | 20297
3116 | 3116 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 20 | 16311 | 14579 | 16083 | 18162 | 19140 | 18521 | 18395 | 16680 | 17688 | 20856 | 22236 | 20979 | 20907 | 19610 | 21834 | 23140 | 24412 | 22578 | 20484 | 20934
3117 | 3117 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 21 | 16261 | 14646 | 16139 | 18020 | 19133 | 18630 | 18495 | 17051 | 18042 | 21179 | 22677 | 21596 | 21595 | 20332 | 22368 | 23936 | 25329 | 23558 | 21642 | 21855
3118 | 3118 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 22 | 15350 | 13856 | 15320 | 16913 | 17962 | 17764 | 17773 | 16437 | 17439 | 20218 | 21821 | 21059 | 21267 | 19923 | 21675 | 23253 | 24778 | 23385 | 21512 | 21569
3119 | 3119 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 23 | 14255 | 12898 | 14351 | 15590 | 16512 | 16701 | 16717 | 15534 | 16543 | 18934 | 20459 | 20137 | 20364 | 19120 | 20532 | 22095 | 23561 | 22596 | 20853 | 20852
3120 | 3120 | 130 | 5 | 10 | Spring | 5 | 9 | Spring | 24 | 13423 | 12128 | 13609 | 14575 | 15398 | 15858 | 15872 | 14763 | 15812 | 17882 | 19283 | 19376 | 19614 | 18467 | 19584 | 21131 | 22416 | 21917 | 20216 | 20232
3121 | 3121 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 1 | 12598 | 12206 | 13271 | 13853 | 15001 | 14979 | 14937 | 14466 | 15410 | 17572 | 18770 | 18562 | 18431 | 17984 | 19400 | 20916 | 21991 | 20622 | 19078 | 19717
3122 | 3122 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 2 | 12372 | 11905 | 13030 | 13509 | 14529 | 14681 | 14493 | 14111 | 15095 | 17024 | 18187 | 18130 | 17868 | 17599 | 18870 | 20251 | 21302 | 19990 | 18578 | 19287
3123 | 3123 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 3 | 12270 | 11731 | 12863 | 13300 | 14300 | 14537 | 14232 | 13884 | 14881 | 16690 | 17808 | 17840 | 17469 | 17272 | 18450 | 19776 | 20793 | 19495 | 18175 | 18907
3124 | 3124 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 4 | 12374 | 11669 | 12897 | 13328 | 14261 | 14547 | 14044 | 13694 | 14764 | 16410 | 17405 | 17494 | 16976 | 16961 | 18013 | 19217 | 20124 | 18796 | 17596 | 18458
3125 | 3125 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 5 | 12872 | 11711 | 13288 | 13739 | 14643 | 14949 | 14107 | 13582 | 14976 | 16550 | 17396 | 17486 | 16686 | 17004 | 17897 | 19042 | 19877 | 18269 | 17128 | 18342
3126 | 3126 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 6 | 13839 | 11695 | 14183 | 14703 | 15532 | 15766 | 14173 | 13330 | 15573 | 17155 | 17743 | 17777 | 16297 | 17362 | 18204 | 19288 | 19920 | 17637 | 16429 | 18552
3127 | 3127 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 7 | 15067 | 11968 | 15561 | 15984 | 16891 | 16874 | 14529 | 13442 | 16675 | 18244 | 18633 | 18432 | 16232 | 18225 | 18828 | 20069 | 20457 | 17392 | 16043 | 19314
3128 | 3128 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 8 | 15744 | 12776 | 16433 | 16807 | 17866 | 17500 | 15314 | 14181 | 17533 | 19089 | 19503 | 18912 | 16779 | 18921 | 19276 | 20683 | 21142 | 17868 | 16551 | 19992
3129 | 3129 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 9 | 15812 | 13503 | 16834 | 17236 | 18324 | 17559 | 15881 | 14816 | 17924 | 19478 | 19944 | 18922 | 17076 | 19018 | 19392 | 20816 | 21372 | 18109 | 17023 | 20056
3130 | 3130 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 10 | 15510 | 13748 | 16845 | 17429 | 18597 | 17277 | 15883 | 15120 | 18002 | 19846 | 20329 | 18729 | 17142 | 19132 | 19713 | 21235 | 21810 | 18237 | 17407 | 20210
3131 | 3131 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 11 | 15211 | 13896 | 16963 | 17611 | 18829 | 17051 | 15757 | 15318 | 18175 | 20175 | 20653 | 18605 | 17087 | 19377 | 20049 | 21633 | 22195 | 18250 | 17606 | 20490
3132 | 3132 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 12 | 15049 | 14008 | 17005 | 17723 | 19025 | 16873 | 15555 | 15441 | 18245 | 20398 | 20927 | 18472 | 16941 | 19458 | 20211 | 21895 | 22515 | 18107 | 17704 | 20579
3133 | 3133 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 13 | 14998 | 14046 | 17172 | 17931 | 19209 | 16820 | 15241 | 15475 | 18416 | 20582 | 21180 | 18427 | 16631 | 19620 | 20418 | 22081 | 22769 | 17788 | 17705 | 20736
3134 | 3134 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 14 | 14851 | 14090 | 17239 | 18088 | 19331 | 16662 | 14964 | 15547 | 18469 | 20686 | 21252 | 18234 | 16316 | 19643 | 20517 | 22146 | 22794 | 17448 | 17726 | 20742
3135 | 3135 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 15 | 14913 | 14358 | 17535 | 18478 | 19602 | 16683 | 14893 | 15796 | 18740 | 20909 | 21405 | 18207 | 16229 | 19879 | 20856 | 22345 | 22923 | 17327 | 17940 | 20964
3136 | 3136 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 16 | 15059 | 14715 | 17831 | 18968 | 19870 | 16740 | 15050 | 16091 | 18972 | 21086 | 21492 | 18144 | 16314 | 20031 | 21452 | 22438 | 22933 | 17350 | 18139 | 21087
3137 | 3137 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 17 | 15398 | 15310 | 18310 | 19267 | 20174 | 17108 | 15619 | 16729 | 19463 | 21333 | 21769 | 18528 | 16974 | 20549 | 21819 | 22771 | 23162 | 18017 | 18763 | 21615
3138 | 3138 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 18 | 15306 | 15533 | 18310 | 19146 | 20037 | 17156 | 16153 | 17181 | 19758 | 21275 | 22069 | 18903 | 17748 | 21032 | 21890 | 22814 | 23652 | 18868 | 19519 | 22154
3139 | 3139 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 19 | 15485 | 15515 | 18031 | 19112 | 19885 | 17449 | 16224 | 17242 | 19630 | 21380 | 22119 | 19554 | 18199 | 21112 | 22366 | 23285 | 24078 | 19497 | 20063 | 22337
3140 | 3140 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 20 | 15782 | 15425 | 17815 | 18874 | 19932 | 17905 | 16279 | 17344 | 19531 | 21674 | 22371 | 20392 | 18728 | 21416 | 22744 | 24045 | 24721 | 20246 | 20693 | 22746
3141 | 3141 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 21 | 15661 | 15445 | 17644 | 18805 | 19891 | 17947 | 16576 | 17610 | 19635 | 22013 | 22752 | 20967 | 19566 | 21894 | 23476 | 24895 | 25574 | 21376 | 21602 | 23419
3142 | 3142 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 22 | 14775 | 14624 | 16513 | 17578 | 18721 | 17182 | 15908 | 16928 | 18678 | 21093 | 21941 | 20544 | 19228 | 21145 | 22757 | 24274 | 25043 | 21222 | 21309 | 22800
3143 | 3143 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 23 | 13674 | 13647 | 15193 | 16150 | 17234 | 16109 | 14980 | 16029 | 17432 | 19734 | 20706 | 19627 | 18466 | 19992 | 21591 | 23071 | 23911 | 20565 | 20577 | 21719
3144 | 3144 | 131 | 5 | 11 | Spring | 5 | 10 | Spring | 24 | 12864 | 12900 | 14170 | 15055 | 15985 | 15255 | 14187 | 15299 | 16431 | 18534 | 19683 | 18872 | 17744 | 19034 | 20616 | 21923 | 22961 | 19911 | 19956 | 20780
3145 | 3145 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 1 | 12123 | 12569 | 13439 | 14618 | 15438 | 14333 | 13944 | 14868 | 15897 | 17996 | 19021 | 17717 | 16946 | 18806 | 20367 | 21488 | 22374 | 18787 | 19437 | 20729
3146 | 3146 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 2 | 11786 | 12356 | 13132 | 14171 | 14967 | 13916 | 13617 | 14583 | 15508 | 17452 | 18516 | 17190 | 16524 | 18305 | 19734 | 20827 | 21767 | 18307 | 19037 | 20174
3147 | 3147 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 3 | 11567 | 12195 | 12912 | 13921 | 14695 | 13651 | 13383 | 14353 | 15207 | 17082 | 18151 | 16788 | 16169 | 17881 | 19255 | 20306 | 21266 | 17889 | 18640 | 19691
3148 | 3148 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 4 | 11555 | 12296 | 12994 | 13944 | 14624 | 13555 | 13286 | 14336 | 15069 | 16816 | 17761 | 16371 | 15785 | 17507 | 18755 | 19687 | 20543 | 17344 | 18218 | 19155
3149 | 3149 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 5 | 11718 | 12717 | 13448 | 14393 | 14950 | 13723 | 13288 | 14676 | 15223 | 16980 | 17628 | 16145 | 15517 | 17431 | 18614 | 19470 | 20042 | 16883 | 18099 | 18883
3150 | 3150 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 6 | 11992 | 13671 | 14470 | 15376 | 15737 | 13905 | 13166 | 15425 | 15932 | 17502 | 17721 | 15869 | 15052 | 17810 | 18938 | 19568 | 19754 | 16220 | 18332 | 19063
3151 | 3151 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 7 | 12583 | 15065 | 15787 | 16786 | 16932 | 14302 | 13332 | 16609 | 16982 | 18471 | 18219 | 15894 | 14816 | 18474 | 19749 | 20145 | 19957 | 15836 | 19094 | 19576
3152 | 3152 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 8 | 13457 | 15962 | 16643 | 17776 | 17940 | 15068 | 14070 | 17480 | 17675 | 19370 | 18595 | 16471 | 15365 | 18967 | 20406 | 20849 | 20218 | 16347 | 19773 | 20013
3153 | 3153 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 9 | 14137 | 16448 | 17147 | 18259 | 18599 | 15635 | 14710 | 17864 | 18158 | 19785 | 18617 | 16880 | 15995 | 19208 | 20651 | 21185 | 20280 | 16932 | 19950 | 20193
3154 | 3154 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 10 | 14214 | 16626 | 17493 | 18676 | 19037 | 15771 | 15145 | 18080 | 18569 | 20293 | 18721 | 17104 | 16469 | 19681 | 21223 | 21781 | 20436 | 17472 | 20261 | 20711
3155 | 3155 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 11 | 14144 | 16851 | 17790 | 19032 | 19390 | 15745 | 15448 | 18375 | 18957 | 20714 | 18743 | 17171 | 16750 | 20127 | 21736 | 22295 | 20451 | 17788 | 20659 | 21200
3156 | 3156 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 12 | 13893 | 16889 | 17878 | 19188 | 19598 | 15518 | 15545 | 18407 | 19058 | 20956 | 18645 | 16985 | 16817 | 20262 | 21976 | 22583 | 20341 | 17867 | 20724 | 21347
3157 | 3157 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 13 | 13551 | 17031 | 18061 | 19345 | 19811 | 15180 | 15557 | 18552 | 19244 | 21191 | 18533 | 16650 | 16804 | 20447 | 22138 | 22810 | 20202 | 17847 | 20859 | 21530
3158 | 3158 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 14 | 13239 | 17066 | 18195 | 19444 | 19880 | 14882 | 15610 | 18585 | 19357 | 21245 | 18365 | 16321 | 16820 | 20531 | 22186 | 22823 | 19994 | 17849 | 20846 | 21593
3159 | 3159 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 15 | 13070 | 17225 | 18481 | 19600 | 19961 | 14712 | 15759 | 18747 | 19603 | 21304 | 18248 | 16119 | 16927 | 20766 | 22285 | 22831 | 19816 | 17954 | 20959 | 21812
3160 | 3160 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 16 | 13401 | 17661 | 19042 | 19989 | 20295 | 15013 | 16194 | 19109 | 20313 | 21540 | 18214 | 16336 | 17288 | 21487 | 22518 | 22954 | 19672 | 18280 | 21210 | 22516
3161 | 3161 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 17 | 13841 | 17966 | 19169 | 20121 | 20389 | 15417 | 16658 | 19417 | 20479 | 21635 | 18328 | 16826 | 17732 | 21686 | 22673 | 23013 | 19800 | 18737 | 21572 | 22723
3162 | 3162 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 18 | 14075 | 17821 | 18933 | 19872 | 20347 | 15836 | 16963 | 19555 | 20241 | 21795 | 18584 | 17454 | 18311 | 21637 | 22591 | 23386 | 20232 | 19397 | 22004 | 22737
3163 | 3163 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 19 | 13930 | 17470 | 18841 | 19649 | 20136 | 15844 | 16959 | 19344 | 20316 | 21736 | 18999 | 17797 | 18672 | 22035 | 22980 | 23740 | 20895 | 19902 | 22149 | 23278
3164 | 3164 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 20 | 13847 | 17257 | 18598 | 19686 | 20000 | 15894 | 17064 | 19219 | 20305 | 21914 | 19453 | 18270 | 19160 | 22375 | 23720 | 24379 | 21808 | 20554 | 22593 | 23780
3165 | 3165 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 21 | 13914 | 17107 | 18530 | 19637 | 19952 | 16168 | 17309 | 19291 | 20574 | 22227 | 19958 | 19050 | 19848 | 23076 | 24542 | 25215 | 22784 | 21473 | 23288 | 24718
3166 | 3166 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 22 | 13097 | 15943 | 17275 | 18425 | 18824 | 15452 | 16570 | 18271 | 19545 | 21344 | 19623 | 18643 | 19377 | 22318 | 23871 | 24639 | 22733 | 21153 | 22651 | 24104
3167 | 3167 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 23 | 12159 | 14626 | 15854 | 16950 | 17463 | 14515 | 15661 | 17023 | 18248 | 20103 | 18998 | 17867 | 18573 | 21151 | 22643 | 23533 | 22237 | 20438 | 21575 | 23029
3168 | 3168 | 132 | 5 | 12 | Spring | 5 | 11 | Spring | 24 | 11401 | 13617 | 14749 | 15702 | 16373 | 13708 | 14911 | 15995 | 17174 | 19047 | 18428 | 17124 | 17905 | 20138 | 21497 | 22557 | 21770 | 19807 | 20629 | 22058
3169 | 3169 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 1 | 11745 | 13137 | 14590 | 15379 | 15939 | 13797 | 14754 | 15620 | 17061 | 18640 | 17062 | 16654 | 17675 | 20127 | 21300 | 22209 | 20271 | 19538 | 20806 | 22124
3170 | 3170 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 2 | 11438 | 12819 | 14128 | 14884 | 15534 | 13448 | 14445 | 15218 | 16515 | 18127 | 16547 | 16218 | 17288 | 19480 | 20622 | 21582 | 19635 | 19098 | 20234 | 21414
3171 | 3171 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 3 | 11293 | 12645 | 13934 | 14666 | 15342 | 13265 | 14268 | 14976 | 16225 | 17831 | 16191 | 15926 | 16997 | 19063 | 20161 | 21119 | 19142 | 18745 | 19793 | 20931
3172 | 3172 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 4 | 11228 | 12670 | 13914 | 14589 | 15209 | 13136 | 14223 | 14869 | 16023 | 17447 | 15806 | 15543 | 16700 | 18562 | 19537 | 20379 | 18473 | 18290 | 19221 | 20269
3173 | 3173 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 5 | 11299 | 13129 | 14366 | 14995 | 15393 | 13167 | 14603 | 15173 | 16317 | 17405 | 15579 | 15331 | 16781 | 18475 | 19355 | 19916 | 17885 | 18188 | 18957 | 19972
3174 | 3174 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 6 | 11286 | 14113 | 15303 | 15804 | 15865 | 13033 | 15365 | 15958 | 17029 | 17552 | 15397 | 14878 | 17154 | 18802 | 19459 | 19607 | 17287 | 18381 | 19091 | 20081
3175 | 3175 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 7 | 11454 | 15331 | 16590 | 16911 | 16611 | 13093 | 16468 | 16957 | 18062 | 17997 | 15364 | 14572 | 17925 | 19536 | 19938 | 19707 | 16890 | 19013 | 19469 | 20641
3176 | 3176 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 8 | 12210 | 16165 | 17533 | 17867 | 17033 | 13786 | 17309 | 17651 | 18851 | 18368 | 15999 | 15085 | 18581 | 20137 | 20585 | 19922 | 17389 | 19601 | 19821 | 21157
3177 | 3177 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 9 | 12857 | 16576 | 17930 | 18348 | 16986 | 14362 | 17651 | 17977 | 19070 | 18372 | 16421 | 15555 | 18654 | 20220 | 20758 | 19813 | 17657 | 19608 | 19852 | 21184
3178 | 3178 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 10 | 13063 | 16733 | 18147 | 18581 | 16814 | 14577 | 17647 | 18170 | 19379 | 18251 | 16530 | 15837 | 18726 | 20586 | 21142 | 19781 | 17852 | 19710 | 20157 | 21598
3179 | 3179 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 11 | 13221 | 16895 | 18366 | 18774 | 16628 | 14711 | 17764 | 18365 | 19700 | 18067 | 16466 | 16014 | 18973 | 20992 | 21557 | 19693 | 17944 | 20015 | 20555 | 22053
3180 | 3180 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 12 | 13365 | 17019 | 18553 | 19009 | 16543 | 14821 | 17803 | 18473 | 19947 | 17962 | 16355 | 16136 | 19080 | 21282 | 21892 | 19628 | 17916 | 20133 | 20752 | 22361
3181 | 3181 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 13 | 13440 | 17252 | 18750 | 19262 | 16476 | 14870 | 17984 | 18689 | 20164 | 17885 | 16079 | 16177 | 19280 | 21494 | 22171 | 19540 | 17658 | 20320 | 20987 | 22572
3182 | 3182 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 14 | 13450 | 17378 | 18847 | 19331 | 16341 | 14922 | 18018 | 18806 | 20253 | 17725 | 15808 | 16202 | 19292 | 21545 | 22179 | 19339 | 17368 | 20305 | 21050 | 22606
3183 | 3183 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 15 | 13563 | 17625 | 18987 | 19414 | 16222 | 15056 | 18167 | 19057 | 20336 | 17598 | 15726 | 16312 | 19368 | 21629 | 22177 | 19162 | 17221 | 20400 | 21251 | 22677
3184 | 3184 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 16 | 14012 | 18106 | 19352 | 19727 | 16253 | 15466 | 18503 | 19701 | 20613 | 17549 | 15913 | 16654 | 19612 | 21839 | 22275 | 18995 | 17320 | 20615 | 21915 | 22852
3185 | 3185 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 17 | 14583 | 18353 | 19610 | 19945 | 16517 | 16060 | 18933 | 19992 | 20841 | 17784 | 16566 | 17224 | 20111 | 22120 | 22465 | 19255 | 18023 | 21097 | 22246 | 23147
3186 | 3186 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 18 | 14960 | 18400 | 19655 | 20156 | 16754 | 16637 | 19315 | 20013 | 20946 | 18284 | 17414 | 18048 | 20756 | 22318 | 23112 | 19968 | 19092 | 21823 | 22539 | 23419
3187 | 3187 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 19 | 15046 | 18448 | 19567 | 20079 | 17031 | 16778 | 19239 | 20208 | 21109 | 18785 | 17983 | 18520 | 20917 | 22813 | 23589 | 20770 | 19948 | 22129 | 23239 | 24071
3188 | 3188 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 20 | 14995 | 18215 | 19587 | 19937 | 17220 | 16894 | 19107 | 20170 | 21380 | 19159 | 18360 | 18971 | 21235 | 23509 | 24206 | 21673 | 20660 | 22608 | 23776 | 24947
3189 | 3189 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 21 | 15042 | 18127 | 19523 | 19866 | 17278 | 17111 | 19142 | 20377 | 21676 | 19579 | 18746 | 19599 | 21706 | 24282 | 25006 | 22620 | 21489 | 23314 | 24736 | 25982
3190 | 3190 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 22 | 14195 | 16864 | 18293 | 18720 | 16638 | 16338 | 18081 | 19292 | 20680 | 19186 | 18419 | 19076 | 20903 | 23574 | 24391 | 22534 | 21434 | 22661 | 24108 | 25447
3191 | 3191 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 23 | 13207 | 15415 | 16796 | 17340 | 15856 | 15398 | 16802 | 17950 | 19292 | 18518 | 17669 | 18238 | 19732 | 22320 | 23229 | 22011 | 20820 | 21557 | 23005 | 24272
3192 | 3192 | 133 | 5 | 13 | Spring | 5 | 12 | Spring | 24 | 12453 | 14348 | 15557 | 16255 | 15232 | 14659 | 15781 | 16860 | 18085 | 17943 | 17004 | 17557 | 18766 | 21162 | 22268 | 21522 | 20253 | 20637 | 22044 | 23163
3193 | 3193 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 1 | 12103 | 13939 | 14978 | 15588 | 13772 | 14265 | 15103 | 16494 | 17504 | 16369 | 15942 | 17075 | 18440 | 20675 | 21639 | 19785 | 18612 | 20527 | 21842 | 22719
3194 | 3194 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 2 | 11874 | 13537 | 14513 | 15202 | 13378 | 13975 | 14720 | 15979 | 16956 | 15890 | 15527 | 16714 | 17940 | 20022 | 21044 | 19170 | 18105 | 19960 | 21152 | 22013
3195 | 3195 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 3 | 11760 | 13330 | 14304 | 15020 | 13150 | 13803 | 14491 | 15709 | 16649 | 15557 | 15214 | 16440 | 17572 | 19577 | 20613 | 18686 | 17683 | 19513 | 20667 | 21495
3196 | 3196 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 4 | 11834 | 13346 | 14277 | 14934 | 13082 | 13822 | 14465 | 15582 | 16402 | 15276 | 14903 | 16215 | 17222 | 19027 | 19931 | 18074 | 17105 | 18975 | 20025 | 20767
3197 | 3197 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 5 | 12270 | 13815 | 14709 | 15156 | 13225 | 14244 | 14831 | 15952 | 16660 | 15137 | 14722 | 16369 | 17222 | 18932 | 19536 | 17543 | 16610 | 18752 | 19759 | 20471
3198 | 3198 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 6 | 13164 | 14757 | 15533 | 15653 | 13424 | 15020 | 15660 | 16722 | 17210 | 15016 | 14472 | 16796 | 17593 | 19081 | 19267 | 16967 | 16059 | 18896 | 19869 | 20422
3199 | 3199 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 7 | 14439 | 16081 | 16676 | 16430 | 13693 | 16141 | 16715 | 17805 | 18119 | 15043 | 14224 | 17625 | 18172 | 19608 | 19400 | 16593 | 15608 | 19291 | 20442 | 20806
3200 | 3200 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 8 | 15235 | 16940 | 17571 | 16787 | 14404 | 16880 | 17343 | 18549 | 18955 | 15621 | 14674 | 18236 | 18581 | 20194 | 19566 | 17038 | 16019 | 19579 | 20906 | 21339
3201 | 3201 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 9 | 15627 | 17329 | 18049 | 16768 | 14935 | 17160 | 17616 | 18814 | 19369 | 15972 | 14959 | 18339 | 18691 | 20406 | 19497 | 17330 | 16367 | 19644 | 20968 | 21530
3202 | 3202 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 10 | 15570 | 17516 | 18238 | 16531 | 14903 | 17100 | 17752 | 19058 | 19616 | 16021 | 15168 | 18350 | 18905 | 20736 | 19411 | 17458 | 16646 | 19900 | 21335 | 21898
3203 | 3203 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 11 | 15601 | 17682 | 18396 | 16271 | 14711 | 17199 | 17936 | 19306 | 19771 | 15962 | 15338 | 18529 | 19186 | 21059 | 19235 | 17484 | 16796 | 20214 | 21709 | 22269
3204 | 3204 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 12 | 15785 | 17994 | 18772 | 16298 | 14689 | 17396 | 18204 | 19665 | 20114 | 16013 | 15535 | 18750 | 19476 | 21506 | 19282 | 17572 | 16945 | 20528 | 22133 | 22735
3205 | 3205 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 13 | 16011 | 18250 | 19080 | 16269 | 14473 | 17639 | 18488 | 19921 | 20426 | 15803 | 15565 | 18989 | 19757 | 21830 | 19240 | 17353 | 16949 | 20808 | 22388 | 23069
3206 | 3206 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 14 | 16049 | 18363 | 19174 | 16154 | 14237 | 17698 | 18631 | 20031 | 20494 | 15561 | 15509 | 19020 | 19852 | 21873 | 19065 | 17079 | 16853 | 20893 | 22444 | 23096
3207 | 3207 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 15 | 16350 | 18626 | 19389 | 16190 | 14345 | 17972 | 19005 | 20268 | 20707 | 15603 | 15758 | 19263 | 20238 | 22004 | 19017 | 17091 | 17123 | 21220 | 22640 | 23202
3208 | 3208 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 16 | 16858 | 19087 | 19802 | 16333 | 14694 | 18409 | 19714 | 20658 | 21017 | 15892 | 16173 | 19624 | 21023 | 22215 | 18956 | 17298 | 17476 | 21980 | 22908 | 23354
3209 | 3209 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 17 | 17314 | 19393 | 20054 | 16613 | 15298 | 18894 | 20052 | 20911 | 21263 | 16584 | 16771 | 20138 | 21363 | 22450 | 19264 | 18015 | 18121 | 22358 | 23248 | 23594
3210 | 3210 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 18 | 17290 | 19269 | 20040 | 16667 | 15809 | 19111 | 19908 | 20850 | 21525 | 17228 | 17442 | 20588 | 21428 | 22924 | 19811 | 18926 | 18896 | 22498 | 23371 | 24138
3211 | 3211 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 19 | 16969 | 19049 | 19830 | 16824 | 16004 | 18919 | 19973 | 20855 | 21458 | 17624 | 17911 | 20603 | 21837 | 23250 | 20479 | 19664 | 19607 | 23100 | 23922 | 24615
3212 | 3212 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 20 | 16709 | 18983 | 19606 | 16932 | 16016 | 18736 | 19843 | 21011 | 21538 | 17869 | 18327 | 20808 | 22105 | 23770 | 21282 | 20300 | 20327 | 23593 | 24746 | 25296
3213 | 3213 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 21 | 16519 | 18837 | 19453 | 16902 | 15906 | 18683 | 19941 | 21172 | 21730 | 18116 | 18763 | 21162 | 22723 | 24453 | 22123 | 21042 | 21122 | 24488 | 25722 | 26228
3214 | 3214 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 22 | 15369 | 17628 | 18328 | 16267 | 15311 | 17628 | 18840 | 20163 | 20820 | 17769 | 18319 | 20356 | 21922 | 23836 | 22042 | 20995 | 20887 | 23875 | 25212 | 25783
3215 | 3215 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 23 | 14024 | 16114 | 16929 | 15472 | 14392 | 16306 | 17460 | 18726 | 19527 | 16982 | 17512 | 19142 | 20707 | 22645 | 21486 | 20336 | 20196 | 22742 | 24017 | 24675
3216 | 3216 | 134 | 5 | 14 | Spring | 5 | 13 | Spring | 24 | 13040 | 14924 | 15839 | 14852 | 13665 | 15283 | 16354 | 17501 | 18458 | 16301 | 16822 | 18160 | 19690 | 21657 | 20991 | 19758 | 19544 | 21779 | 22900 | 23733
3217 | 3217 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 1 | 12215 | 14223 | 15070 | 13328 | 13069 | 14444 | 15834 | 16819 | 17696 | 15226 | 15757 | 17667 | 19281 | 20915 | 19146 | 18075 | 18412 | 21444 | 22346 | 22999
3218 | 3218 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 2 | 11899 | 13747 | 14684 | 12924 | 12716 | 14052 | 15306 | 16265 | 17193 | 14808 | 15448 | 17162 | 18643 | 20309 | 18524 | 17559 | 18016 | 20735 | 21616 | 22325
3219 | 3219 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 3 | 11721 | 13526 | 14514 | 12705 | 12502 | 13835 | 15051 | 15982 | 16920 | 14518 | 15265 | 16815 | 18239 | 19897 | 18057 | 17145 | 17725 | 20251 | 21104 | 21838
3220 | 3220 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 4 | 11765 | 13506 | 14439 | 12662 | 12416 | 13834 | 14960 | 15802 | 16635 | 14250 | 15159 | 16516 | 17808 | 19258 | 17476 | 16589 | 17381 | 19620 | 20381 | 21019
3221 | 3221 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 5 | 12224 | 13919 | 14656 | 12802 | 12431 | 14219 | 15363 | 16099 | 16664 | 14111 | 15376 | 16567 | 17787 | 18906 | 16975 | 16109 | 17314 | 19360 | 20080 | 20460
3222 | 3222 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 6 | 13229 | 14801 | 15213 | 13057 | 12492 | 15128 | 16227 | 16760 | 16910 | 13957 | 16095 | 17042 | 18200 | 18725 | 16477 | 15618 | 17776 | 19522 | 20069 | 20075
3223 | 3223 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 7 | 14625 | 16134 | 16180 | 13506 | 12720 | 16376 | 17510 | 17891 | 17568 | 13924 | 17172 | 17845 | 19150 | 19060 | 16290 | 15341 | 18632 | 20255 | 20610 | 20267
3224 | 3224 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 8 | 15488 | 17140 | 16668 | 14297 | 13411 | 17130 | 18390 | 18818 | 17964 | 14520 | 17917 | 18390 | 19815 | 19352 | 16857 | 15849 | 19235 | 20832 | 21242 | 20507
3225 | 3225 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 9 | 16045 | 17787 | 16836 | 14930 | 13964 | 17569 | 18835 | 19300 | 18037 | 14977 | 18119 | 18692 | 20105 | 19438 | 17307 | 16363 | 19373 | 21054 | 21575 | 20575
3226 | 3226 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 10 | 16459 | 18257 | 16882 | 15172 | 14381 | 17975 | 19341 | 19825 | 18150 | 15462 | 18451 | 19177 | 20703 | 19625 | 17711 | 16915 | 19777 | 21692 | 22232 | 20803
3227 | 3227 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 11 | 16720 | 18552 | 16756 | 15158 | 14614 | 18283 | 19718 | 20186 | 18115 | 15762 | 18671 | 19577 | 21176 | 19578 | 17870 | 17190 | 20065 | 22205 | 22740 | 20806
3228 | 3228 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 12 | 16931 | 18865 | 16724 | 15122 | 14732 | 18497 | 20018 | 20533 | 18118 | 15901 | 18872 | 19821 | 21525 | 19568 | 17900 | 17296 | 20290 | 22574 | 23156 | 20815
3229 | 3229 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 13 | 17188 | 19149 | 16673 | 14895 | 14733 | 18758 | 20253 | 20837 | 18082 | 15909 | 19071 | 20080 | 21757 | 19505 | 17662 | 17278 | 20478 | 22809 | 23465 | 20760
3230 | 3230 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 14 | 17212 | 19135 | 16438 | 14552 | 14578 | 18786 | 20246 | 20804 | 17834 | 15740 | 18914 | 20075 | 21714 | 19214 | 17272 | 17073 | 20295 | 22744 | 23371 | 20454
3231 | 3231 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 15 | 17463 | 19243 | 16368 | 14502 | 14736 | 19048 | 20372 | 20864 | 17716 | 15878 | 18962 | 20311 | 21811 | 19058 | 17172 | 17189 | 20318 | 22825 | 23364 | 20275
3232 | 3232 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 16 | 17846 | 19487 | 16354 | 14694 | 15042 | 19587 | 20612 | 21027 | 17603 | 16136 | 19137 | 20924 | 21952 | 18845 | 17221 | 17387 | 20429 | 22924 | 23359 | 20008
3233 | 3233 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 17 | 17913 | 19491 | 16395 | 15089 | 15441 | 19698 | 20617 | 21061 | 17653 | 16492 | 19353 | 21049 | 22038 | 18920 | 17705 | 17824 | 20648 | 23031 | 23366 | 20080
3234 | 3234 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 18 | 17745 | 19371 | 16307 | 15486 | 15821 | 19479 | 20464 | 21191 | 17888 | 17050 | 19679 | 21015 | 21980 | 19376 | 18528 | 18514 | 21072 | 23069 | 23846 | 20609
3235 | 3235 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 19 | 17639 | 19095 | 16385 | 15609 | 15971 | 19470 | 20398 | 21021 | 18182 | 17407 | 19905 | 21323 | 22291 | 19949 | 19185 | 19167 | 21601 | 23573 | 24262 | 21329
3236 | 3236 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 20 | 17316 | 18799 | 16436 | 15574 | 16108 | 19292 | 20494 | 20996 | 18418 | 17718 | 20288 | 21501 | 22869 | 20675 | 19755 | 19853 | 22291 | 24382 | 24915 | 22229
3237 | 3237 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 21 | 17178 | 18649 | 16393 | 15450 | 16204 | 19359 | 20613 | 21125 | 18723 | 18099 | 20457 | 22055 | 23539 | 21469 | 20465 | 20630 | 22814 | 25361 | 25859 | 23260
3238 | 3238 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 22 | 15931 | 17480 | 15717 | 14825 | 15512 | 18195 | 19524 | 20160 | 18290 | 17591 | 19617 | 21192 | 22796 | 21320 | 20365 | 20361 | 22197 | 24809 | 25381 | 23284
3239 | 3239 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 23 | 14492 | 16123 | 14961 | 13945 | 14636 | 16828 | 18097 | 18870 | 17620 | 16813 | 18372 | 19973 | 21524 | 20785 | 19731 | 19691 | 21031 | 23645 | 24315 | 22841
3240 | 3240 | 135 | 5 | 15 | Spring | 5 | 14 | Spring | 24 | 13427 | 15052 | 14347 | 13233 | 13902 | 15725 | 16864 | 17792 | 17023 | 16123 | 17384 | 18949 | 20347 | 20281 | 19142 | 19039 | 20074 | 22522 | 23376 | 22377
3241 | 3241 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 1 | 13299 | 14670 | 13236 | 13045 | 13358 | 15554 | 16537 | 17358 | 15740 | 15443 | 17173 | 18893 | 20137 | 18843 | 17904 | 18298 | 20163 | 22356 | 23026 | 20868
3242 | 3242 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 2 | 12919 | 14316 | 12864 | 12710 | 13128 | 15046 | 16004 | 16880 | 15270 | 15157 | 16693 | 18277 | 19488 | 18246 | 17410 | 17915 | 19596 | 21633 | 22365 | 20208
3243 | 3243 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 3 | 12712 | 14149 | 12657 | 12501 | 13042 | 14801 | 15737 | 16626 | 14962 | 14994 | 16435 | 17896 | 19065 | 17797 | 17006 | 17635 | 19221 | 21129 | 21878 | 19684
3244 | 3244 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 4 | 12720 | 14076 | 12630 | 12426 | 13159 | 14746 | 15601 | 16397 | 14730 | 14937 | 16129 | 17523 | 18563 | 17262 | 16481 | 17314 | 18628 | 20416 | 21064 | 18972
3245 | 3245 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 5 | 13190 | 14316 | 12804 | 12467 | 13636 | 15207 | 15962 | 16504 | 14660 | 15230 | 16189 | 17593 | 18538 | 16837 | 16058 | 17299 | 18354 | 20153 | 20544 | 18334
3246 | 3246 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 6 | 14149 | 14879 | 13071 | 12525 | 14642 | 16100 | 16669 | 16812 | 14625 | 15991 | 16687 | 18059 | 18768 | 16374 | 15585 | 17766 | 18508 | 20138 | 20148 | 17664
3247 | 3247 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 7 | 15449 | 15687 | 13386 | 12598 | 15774 | 17253 | 17690 | 17373 | 14688 | 16964 | 17285 | 18872 | 19322 | 16048 | 15148 | 18454 | 18833 | 20495 | 20158 | 17195
3248 | 3248 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 8 | 16261 | 16038 | 14061 | 13166 | 16444 | 18004 | 18496 | 17674 | 15251 | 17591 | 17618 | 19434 | 19891 | 16478 | 15520 | 18912 | 19003 | 20988 | 20240 | 17596
3249 | 3249 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 9 | 16587 | 16028 | 14514 | 13529 | 16583 | 18247 | 18789 | 17564 | 15555 | 17596 | 17430 | 19529 | 20033 | 16722 | 15832 | 18834 | 18671 | 21106 | 20082 | 17817
3250 | 3250 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 10 | 16794 | 15794 | 14496 | 13664 | 16583 | 18478 | 19044 | 17400 | 15618 | 17666 | 17378 | 19846 | 20384 | 16853 | 16108 | 18968 | 18688 | 21500 | 20046 | 18004
3251 | 3251 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 11 | 16997 | 15575 | 14386 | 13790 | 16620 | 18745 | 19300 | 17251 | 15586 | 17782 | 17429 | 20209 | 20733 | 16909 | 16285 | 19151 | 18802 | 21913 | 19954 | 18111
3252 | 3252 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 12 | 17249 | 15573 | 14354 | 13910 | 16800 | 19047 | 19651 | 17257 | 15585 | 17989 | 17455 | 20557 | 21133 | 16944 | 16396 | 19384 | 18854 | 22337 | 19971 | 18161
3253 | 3253 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 13 | 17469 | 15539 | 14128 | 13914 | 16979 | 19278 | 19946 | 17223 | 15338 | 18184 | 17533 | 20793 | 21412 | 16707 | 16380 | 19578 | 18915 | 22641 | 19914 | 17915
3254 | 3254 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 14 | 17586 | 15419 | 13908 | 13882 | 16967 | 19397 | 20040 | 17102 | 15107 | 18154 | 17523 | 20882 | 21466 | 16448 | 16304 | 19522 | 18874 | 22672 | 19733 | 17641
3255 | 3255 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 15 | 17800 | 15382 | 13913 | 14101 | 17090 | 19583 | 20163 | 17047 | 15093 | 18263 | 17616 | 21039 | 21542 | 16405 | 16476 | 19602 | 18940 | 22715 | 19605 | 17583
3256 | 3256 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 16 | 18074 | 15309 | 14062 | 14371 | 17289 | 19784 | 20292 | 16914 | 15188 | 18407 | 18160 | 21154 | 21565 | 16418 | 16632 | 19676 | 19478 | 22662 | 19296 | 17562
3257 | 3257 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 17 | 18441 | 15610 | 14717 | 15035 | 17785 | 20071 | 20599 | 17229 | 15935 | 18887 | 18762 | 21514 | 21862 | 17174 | 17338 | 20186 | 20119 | 22944 | 19642 | 18317
3258 | 3258 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 18 | 18458 | 15708 | 15259 | 15592 | 18130 | 20129 | 20898 | 17616 | 16694 | 19397 | 19222 | 21652 | 22460 | 18196 | 18223 | 20825 | 20706 | 23637 | 20385 | 19405
3259 | 3259 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 19 | 18388 | 15980 | 15560 | 15930 | 18404 | 20243 | 20901 | 18057 | 17191 | 19763 | 19737 | 22106 | 22893 | 19020 | 19056 | 21525 | 21459 | 24266 | 21309 | 20357
3260 | 3260 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 20 | 18347 | 16053 | 15556 | 16118 | 18540 | 20375 | 20900 | 18296 | 17399 | 20124 | 19946 | 22669 | 23377 | 19604 | 19783 | 22235 | 22101 | 24988 | 22284 | 21096
3261 | 3261 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 21 | 18209 | 16014 | 15414 | 16203 | 18369 | 20448 | 20975 | 18524 | 17602 | 20231 | 20376 | 23265 | 24021 | 20260 | 20533 | 22742 | 22951 | 25929 | 23333 | 21990
3262 | 3262 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 22 | 16956 | 15346 | 14761 | 15470 | 17299 | 19300 | 19935 | 18013 | 17175 | 19337 | 19767 | 22443 | 23328 | 20102 | 20224 | 22090 | 22613 | 25419 | 23332 | 21993
3263 | 3263 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 23 | 15457 | 14559 | 13857 | 14586 | 15927 | 17829 | 18604 | 17303 | 16385 | 18065 | 18611 | 21134 | 22136 | 19431 | 19523 | 20903 | 21576 | 24320 | 22862 | 21417
3264 | 3264 | 136 | 5 | 16 | Spring | 5 | 15 | Spring | 24 | 14272 | 13917 | 13118 | 13854 | 14871 | 16571 | 17496 | 16673 | 15670 | 17051 | 17680 | 19926 | 21116 | 18810 | 18842 | 19922 | 20704 | 23357 | 22377 | 20841
3265 | 3265 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 1 | 13705 | 12607 | 12745 | 13065 | 14101 | 15984 | 16817 | 15145 | 14806 | 16528 | 17447 | 19430 | 20497 | 17394 | 17859 | 19718 | 20598 | 22753 | 20608 | 19138
3266 | 3266 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 2 | 13266 | 12251 | 12436 | 12849 | 13741 | 15479 | 16362 | 14700 | 14425 | 16080 | 17058 | 18815 | 19923 | 16925 | 17497 | 19174 | 20092 | 22104 | 19962 | 18619
3267 | 3267 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 3 | 13020 | 12027 | 12217 | 12749 | 13579 | 15205 | 16108 | 14391 | 14130 | 15828 | 16771 | 18398 | 19514 | 16517 | 17210 | 18789 | 19678 | 21610 | 19427 | 18153
3268 | 3268 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 4 | 13034 | 12029 | 12176 | 12902 | 13568 | 15126 | 15949 | 14235 | 13932 | 15604 | 16498 | 17981 | 18961 | 16053 | 16943 | 18250 | 19091 | 20836 | 18748 | 17543
3269 | 3269 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 5 | 13459 | 12192 | 12216 | 13380 | 13916 | 15511 | 16097 | 14213 | 13852 | 15725 | 16592 | 18026 | 18692 | 15667 | 16958 | 18006 | 18850 | 20326 | 18124 | 16985
3270 | 3270 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 6 | 14327 | 12468 | 12302 | 14409 | 14801 | 16258 | 16477 | 14260 | 13732 | 16297 | 17267 | 18345 | 18559 | 15239 | 17463 | 18198 | 19122 | 19948 | 17465 | 16392
3271 | 3271 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 7 | 15557 | 12882 | 12473 | 15635 | 15844 | 17367 | 17164 | 14472 | 13640 | 17026 | 18089 | 19027 | 18833 | 14895 | 18240 | 18608 | 19596 | 20033 | 17056 | 15941
3272 | 3272 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 8 | 16549 | 13700 | 13207 | 16450 | 16465 | 18318 | 17615 | 15215 | 14253 | 17537 | 18645 | 19760 | 19112 | 15408 | 18837 | 18924 | 20053 | 20234 | 17581 | 16442
3273 | 3273 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 9 | 17229 | 14424 | 13842 | 16851 | 16633 | 18859 | 17757 | 15800 | 14767 | 17609 | 18799 | 20167 | 19233 | 15959 | 19000 | 18844 | 20305 | 20304 | 18031 | 16977
3274 | 3274 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 10 | 17646 | 14648 | 14214 | 17077 | 16713 | 19335 | 17825 | 16087 | 15199 | 17783 | 19087 | 20730 | 19374 | 16461 | 19362 | 19087 | 20675 | 20510 | 18450 | 17531
3275 | 3275 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 11 | 18004 | 14678 | 14482 | 17258 | 16815 | 19724 | 17806 | 16195 | 15549 | 17967 | 19367 | 21222 | 19372 | 16775 | 19684 | 19348 | 21021 | 20558 | 18699 | 17887
3276 | 3276 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 12 | 18273 | 14618 | 14566 | 17405 | 16765 | 20038 | 17778 | 16157 | 15648 | 17955 | 19496 | 21582 | 19330 | 16852 | 19882 | 19366 | 21150 | 20544 | 18720 | 17972
3277 | 3277 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 13 | 18555 | 14395 | 14565 | 17595 | 16834 | 20330 | 17735 | 15921 | 15654 | 18029 | 19655 | 21883 | 19267 | 16834 | 20071 | 19441 | 21277 | 20479 | 18472 | 17949
3278 | 3278 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 14 | 18676 | 14170 | 14541 | 17589 | 16858 | 20433 | 17626 | 15696 | 15620 | 18032 | 19682 | 21950 | 19119 | 16769 | 20027 | 19409 | 21194 | 20305 | 18205 | 17869
3279 | 3279 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 15 | 19081 | 14400 | 14986 | 17941 | 17210 | 20790 | 17806 | 15915 | 16050 | 18357 | 19949 | 22260 | 19250 | 17173 | 20336 | 19703 | 21425 | 20408 | 18374 | 18260
3280 | 3280 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 16 | 19231 | 14486 | 15192 | 18076 | 17617 | 20869 | 17620 | 15955 | 16207 | 18833 | 20053 | 22230 | 18935 | 17274 | 20353 | 20178 | 21415 | 20029 | 18288 | 18334
3281 | 3281 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 17 | 19201 | 14849 | 15557 | 18263 | 17916 | 20890 | 17650 | 16388 | 16522 | 19137 | 20130 | 22211 | 18982 | 17694 | 20577 | 20516 | 21532 | 20100 | 18753 | 18757
3282 | 3282 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 18 | 18939 | 15029 | 15718 | 18242 | 17907 | 20835 | 17674 | 16752 | 16935 | 19242 | 19899 | 22428 | 19309 | 18240 | 20881 | 20755 | 21513 | 20528 | 19513 | 19357
3283 | 3283 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 19 | 18582 | 15027 | 15741 | 18221 | 17878 | 20533 | 17781 | 16916 | 17185 | 19395 | 20327 | 22521 | 19757 | 18760 | 21267 | 21198 | 22249 | 21156 | 20182 | 19980
3284 | 3284 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 20 | 18273 | 14918 | 15821 | 18261 | 17750 | 20439 | 17888 | 16991 | 17441 | 19446 | 20855 | 22870 | 20417 | 19367 | 21878 | 21736 | 23092 | 22047 | 20848 | 20699
3285 | 3285 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 21 | 18068 | 14717 | 15827 | 18006 | 17689 | 20411 | 17997 | 17058 | 17717 | 19736 | 21210 | 23363 | 21077 | 20016 | 22285 | 22488 | 23928 | 23027 | 21689 | 21534
3286 | 3286 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 22 | 16897 | 14066 | 15105 | 16936 | 16819 | 19359 | 17470 | 16594 | 17170 | 19103 | 20518 | 22632 | 20899 | 19693 | 21625 | 22147 | 23513 | 23036 | 21710 | 21348
3287 | 3287 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 23 | 15519 | 13192 | 14221 | 15577 | 15526 | 18011 | 16740 | 15783 | 16358 | 17940 | 19374 | 21420 | 20329 | 18985 | 20444 | 21112 | 22454 | 22559 | 21139 | 20719
3288 | 3288 | 137 | 5 | 17 | Spring | 5 | 16 | Spring | 24 | 14462 | 12462 | 13493 | 14550 | 14556 | 16917 | 16114 | 15067 | 15669 | 17010 | 18419 | 20405 | 19826 | 18312 | 19474 | 20248 | 21597 | 22093 | 20582 | 20077
3289 | 3289 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 1 | 13966 | 12254 | 12468 | 13907 | 14342 | 16385 | 14740 | 14449 | 14870 | 16905 | 17694 | 19897 | 18266 | 17076 | 19348 | 20245 | 20975 | 20452 | 19019 | 18801
3290 | 3290 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 2 | 13637 | 11958 | 12202 | 13551 | 14049 | 15945 | 14308 | 14081 | 14612 | 16538 | 17135 | 19346 | 17696 | 16667 | 18808 | 19750 | 20302 | 19810 | 18502 | 18344
3291 | 3291 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 3 | 13484 | 11783 | 12083 | 13426 | 13908 | 15734 | 14044 | 13830 | 14472 | 16306 | 16762 | 18987 | 17273 | 16370 | 18465 | 19371 | 19786 | 19300 | 18063 | 17991
3292 | 3292 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 4 | 13437 | 11720 | 12067 | 13413 | 13909 | 15586 | 13908 | 13646 | 14473 | 16064 | 16388 | 18484 | 16806 | 15970 | 17953 | 18806 | 19096 | 18628 | 17451 | 17448
3293 | 3293 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 5 | 13663 | 11744 | 12122 | 13775 | 14335 | 15767 | 13937 | 13612 | 14796 | 16233 | 16480 | 18284 | 16426 | 15644 | 17744 | 18596 | 18785 | 18011 | 16894 | 16955
3294 | 3294 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 6 | 14269 | 11888 | 12165 | 14740 | 15422 | 16233 | 14102 | 13615 | 15649 | 17036 | 17028 | 18282 | 16063 | 15178 | 18016 | 18947 | 18902 | 17408 | 16343 | 16329
3295 | 3295 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 7 | 15209 | 12163 | 12355 | 15895 | 16586 | 17022 | 14442 | 13655 | 16787 | 17993 | 18000 | 18700 | 15912 | 14890 | 18541 | 19528 | 19585 | 17081 | 15965 | 15943
3296 | 3296 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 8 | 15707 | 12934 | 12951 | 16567 | 17319 | 17522 | 15250 | 14350 | 17602 | 18641 | 18676 | 19038 | 16524 | 15276 | 18889 | 20026 | 20143 | 17623 | 16482 | 16328
3297 | 3297 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 9 | 15719 | 13443 | 13401 | 16598 | 17404 | 17562 | 15751 | 14794 | 17658 | 18740 | 18668 | 18952 | 16804 | 15416 | 18601 | 20068 | 20099 | 17861 | 16802 | 16456
3298 | 3298 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 10 | 15421 | 13505 | 13372 | 16390 | 17300 | 17319 | 15722 | 14929 | 17656 | 18714 | 18584 | 18798 | 16865 | 15515 | 18548 | 20150 | 20117 | 17978 | 17057 | 16607
3299 | 3299 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 11 | 15139 | 13511 | 13236 | 16205 | 17279 | 17001 | 15521 | 14962 | 17702 | 18666 | 18509 | 18559 | 16850 | 15552 | 18583 | 20267 | 20232 | 18005 | 17193 | 16685
3300 | 3300 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 12 | 15354 | 13809 | 13494 | 16369 | 17616 | 17161 | 15667 | 15253 | 18112 | 18968 | 18681 | 18748 | 17093 | 15891 | 18834 | 20636 | 20503 | 18254 | 17512 | 17034
3301 | 3301 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 13 | 15172 | 13649 | 13210 | 16264 | 17621 | 16940 | 15258 | 15080 | 18156 | 18948 | 18597 | 18519 | 16704 | 15623 | 18748 | 20596 | 20409 | 17848 | 17329 | 16762
3302 | 3302 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 14 | 15154 | 13743 | 13186 | 16405 | 17779 | 16951 | 15155 | 15167 | 18244 | 19100 | 18623 | 18492 | 16565 | 15559 | 18838 | 20630 | 20327 | 17698 | 17367 | 16680
3303 | 3303 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 15 | 15136 | 13955 | 13348 | 16549 | 17865 | 16929 | 15170 | 15390 | 18372 | 19164 | 18688 | 18432 | 16542 | 15670 | 18932 | 20653 | 20335 | 17664 | 17554 | 16779
3304 | 3304 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 16 | 15252 | 14414 | 13786 | 17179 | 18291 | 17002 | 15464 | 15803 | 18707 | 19525 | 18939 | 18393 | 16748 | 15976 | 19661 | 20898 | 20459 | 17825 | 17874 | 17055
3305 | 3305 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 17 | 15499 | 15023 | 14396 | 17731 | 18545 | 17271 | 16132 | 16363 | 19121 | 19837 | 19271 | 18684 | 17442 | 16577 | 20232 | 21256 | 20857 | 18530 | 18530 | 17659
3306 | 3306 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 18 | 15380 | 15282 | 14616 | 17845 | 18385 | 17392 | 16569 | 16834 | 19388 | 19695 | 19637 | 19080 | 18230 | 17230 | 20591 | 21343 | 21377 | 19412 | 19245 | 18364
3307 | 3307 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 19 | 15378 | 15274 | 14872 | 17797 | 18552 | 17497 | 16714 | 17049 | 19458 | 20058 | 20010 | 19469 | 18742 | 17906 | 21007 | 22062 | 22048 | 20095 | 19886 | 19133
3308 | 3308 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 20 | 15362 | 15348 | 15150 | 17640 | 18750 | 17592 | 16767 | 17263 | 19714 | 20495 | 20669 | 20060 | 19211 | 18736 | 21510 | 22890 | 23088 | 20784 | 20632 | 20077
3309 | 3309 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 21 | 15259 | 15365 | 15230 | 17555 | 18642 | 17659 | 16774 | 17486 | 19711 | 20763 | 21127 | 20650 | 19749 | 19456 | 22221 | 23697 | 24038 | 21616 | 21475 | 20982
3310 | 3310 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 22 | 14630 | 14635 | 14594 | 16683 | 17648 | 17092 | 16271 | 16909 | 18804 | 20038 | 20414 | 20418 | 19569 | 19186 | 21847 | 23260 | 23589 | 21633 | 21291 | 20836
3311 | 3311 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 23 | 13832 | 13714 | 13731 | 15358 | 16316 | 16312 | 15397 | 16044 | 17499 | 18840 | 19203 | 19784 | 18858 | 18446 | 20772 | 22132 | 22484 | 21001 | 20614 | 20159
3312 | 3312 | 138 | 5 | 18 | Spring | 5 | 17 | Spring | 24 | 13203 | 12971 | 13047 | 14355 | 15289 | 15662 | 14646 | 15301 | 16466 | 17845 | 18211 | 19217 | 18219 | 17794 | 19875 | 21235 | 21552 | 20413 | 19948 | 19532
3313 | 3313 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 1 | 12079 | 11981 | 13686 | 14170 | 14462 | 14334 | 14130 | 14201 | 16051 | 17113 | 17451 | 17721 | 17032 | 18923 | 19875 | 20629 | 20740 | 18899 | 18709 | 20834
3314 | 3314 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 2 | 11749 | 11746 | 13361 | 13898 | 14029 | 13924 | 13784 | 13905 | 15629 | 16596 | 16904 | 17188 | 16589 | 18411 | 19405 | 19986 | 20079 | 18398 | 18267 | 20272
3315 | 3315 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 3 | 11572 | 11645 | 13250 | 13775 | 13797 | 13682 | 13552 | 13741 | 15433 | 16258 | 16572 | 16799 | 16228 | 18092 | 19047 | 19494 | 19615 | 17968 | 17921 | 19888
3316 | 3316 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 4 | 11561 | 11634 | 13253 | 13786 | 13715 | 13590 | 13415 | 13615 | 15229 | 15967 | 16230 | 16386 | 15791 | 17619 | 18516 | 18832 | 18931 | 17368 | 17380 | 19245
3317 | 3317 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 5 | 11730 | 11663 | 13611 | 14230 | 14087 | 13649 | 13409 | 13574 | 15409 | 16131 | 16263 | 16081 | 15444 | 17458 | 18347 | 18561 | 18624 | 16827 | 16893 | 18884
3318 | 3318 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 6 | 12038 | 11705 | 14552 | 15329 | 14991 | 13824 | 13434 | 13433 | 16081 | 16737 | 16644 | 15783 | 15079 | 17758 | 18722 | 18698 | 18650 | 16267 | 16248 | 18986
3319 | 3319 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 7 | 12576 | 11949 | 15762 | 16551 | 16380 | 14221 | 13544 | 13526 | 16969 | 17801 | 17479 | 15744 | 14875 | 18346 | 19364 | 19442 | 19144 | 15916 | 15882 | 19427
3320 | 3320 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 8 | 13437 | 12546 | 16465 | 17298 | 17243 | 15007 | 14232 | 14101 | 17571 | 18484 | 18079 | 16382 | 15440 | 18724 | 19892 | 20013 | 19615 | 16433 | 16266 | 19745
3321 | 3321 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 9 | 14205 | 13166 | 16679 | 17611 | 17516 | 15620 | 14795 | 14570 | 17786 | 18563 | 18233 | 16882 | 15997 | 18658 | 20158 | 20174 | 19835 | 16961 | 16602 | 19638
3322 | 3322 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 10 | 14443 | 13445 | 16769 | 17788 | 17665 | 15879 | 15216 | 14895 | 17956 | 18761 | 18362 | 17231 | 16497 | 18892 | 20527 | 20480 | 20047 | 17505 | 17044 | 19920
3323 | 3323 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 11 | 14389 | 13548 | 16816 | 17929 | 17694 | 15923 | 15505 | 15046 | 17987 | 18950 | 18483 | 17375 | 16754 | 19104 | 20824 | 20761 | 20141 | 17824 | 17307 | 20178
3324 | 3324 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 12 | 14411 | 13687 | 16869 | 18117 | 17698 | 15973 | 15702 | 15217 | 18014 | 19029 | 18552 | 17469 | 16923 | 19215 | 21054 | 20880 | 20191 | 18006 | 17520 | 20304
3325 | 3325 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 13 | 14257 | 13636 | 17006 | 18345 | 17816 | 15811 | 15778 | 15182 | 18128 | 19206 | 18622 | 17305 | 16966 | 19362 | 21246 | 21019 | 20224 | 18057 | 17481 | 20450
3326 | 3326 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 14 | 13856 | 13324 | 16854 | 18224 | 17558 | 15417 | 15575 | 14859 | 17966 | 18948 | 18299 | 16888 | 16733 | 19163 | 20991 | 20654 | 19865 | 17802 | 17106 | 20232
3327 | 3327 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 15 | 14064 | 13661 | 17191 | 18504 | 17843 | 15623 | 15991 | 15182 | 18270 | 19208 | 18438 | 17067 | 17120 | 19450 | 21205 | 20862 | 19956 | 18178 | 17394 | 20503
3328 | 3328 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 16 | 14203 | 13886 | 17547 | 18726 | 18003 | 15716 | 16199 | 15344 | 18791 | 19270 | 18400 | 17078 | 17280 | 19976 | 21246 | 20786 | 19836 | 18284 | 17455 | 21000
3329 | 3329 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 17 | 14562 | 14244 | 17846 | 18742 | 18148 | 16145 | 16508 | 15721 | 19098 | 19350 | 18441 | 17533 | 17692 | 20299 | 21366 | 20958 | 19845 | 18694 | 17813 | 21330
3330 | 3330 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 18 | 14713 | 14297 | 17817 | 18437 | 18124 | 16437 | 16804 | 15995 | 19175 | 19540 | 18547 | 18148 | 18201 | 20510 | 21292 | 21328 | 20131 | 19282 | 18386 | 21602
3331 | 3331 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 19 | 14644 | 14463 | 17684 | 18511 | 18092 | 16493 | 16930 | 16241 | 19219 | 19774 | 18768 | 18534 | 18635 | 20831 | 21915 | 21895 | 20712 | 19870 | 19095 | 22068
3332 | 3332 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 20 | 14455 | 14648 | 17426 | 18602 | 18336 | 16447 | 17047 | 16611 | 19135 | 20274 | 19472 | 18851 | 19142 | 21207 | 22623 | 22832 | 21804 | 20552 | 19972 | 22594
3333 | 3333 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 21 | 14265 | 14716 | 17315 | 18471 | 18340 | 16404 | 17222 | 16900 | 19364 | 20627 | 20059 | 19312 | 19764 | 21870 | 23377 | 23747 | 22880 | 21380 | 20876 | 23481
3334 | 3334 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 22 | 13590 | 14067 | 16405 | 17432 | 17293 | 15844 | 16583 | 16360 | 18672 | 19838 | 19553 | 19060 | 19391 | 21432 | 22878 | 23244 | 22659 | 21165 | 20707 | 23213
3335 | 3335 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 23 | 12722 | 13256 | 15116 | 16129 | 15980 | 14987 | 15734 | 15583 | 17484 | 18643 | 18602 | 18345 | 18658 | 20359 | 21784 | 22150 | 21828 | 20513 | 20067 | 22234
3336 | 3336 | 139 | 5 | 19 | Spring | 5 | 18 | Spring | 24 | 11977 | 12607 | 14136 | 15123 | 14942 | 14251 | 15004 | 14907 | 16529 | 17659 | 17787 | 17701 | 17961 | 19475 | 20900 | 21232 | 21081 | 19865 | 19465 | 21395
3337 | 3337 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 1 | 11745 | 13150 | 13869 | 14190 | 14140 | 13704 | 13806 | 15563 | 16332 | 16777 | 16999 | 16525 | 16680 | 19373 | 20187 | 20351 | 20168 | 18532 | 20661 | 21362
3338 | 3338 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 2 | 11469 | 12844 | 13611 | 13763 | 13697 | 13367 | 13518 | 15158 | 15990 | 16251 | 16488 | 16098 | 16296 | 18914 | 19552 | 19702 | 19556 | 18092 | 20101 | 20847
3339 | 3339 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 3 | 11289 | 12684 | 13477 | 13522 | 13481 | 13124 | 13344 | 14958 | 15771 | 15926 | 16169 | 15738 | 16003 | 18557 | 19053 | 19226 | 19110 | 17729 | 19700 | 20420
3340 | 3340 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 4 | 11242 | 12718 | 13507 | 13476 | 13456 | 13015 | 13252 | 14819 | 15611 | 15649 | 15717 | 15363 | 15650 | 18083 | 18445 | 18589 | 18365 | 17215 | 19079 | 19771
3341 | 3341 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 5 | 11245 | 13032 | 13940 | 13846 | 13795 | 13022 | 13234 | 15029 | 15817 | 15754 | 15373 | 15057 | 15354 | 17952 | 18205 | 18305 | 17661 | 16728 | 18711 | 19427
3342 | 3342 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 6 | 11393 | 14015 | 15063 | 14809 | 14599 | 13104 | 13173 | 15779 | 16676 | 16258 | 15002 | 14780 | 14932 | 18401 | 18411 | 18386 | 16892 | 16117 | 18838 | 19661
3343 | 3343 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 7 | 11709 | 15266 | 16294 | 16240 | 15745 | 13241 | 13319 | 16738 | 17713 | 17175 | 15082 | 14626 | 14698 | 19088 | 19182 | 18898 | 16680 | 15745 | 19269 | 20170
3344 | 3344 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 8 | 12508 | 16027 | 17090 | 17136 | 16503 | 13979 | 13961 | 17416 | 18381 | 17870 | 15740 | 15233 | 15124 | 19655 | 19782 | 19391 | 17166 | 16142 | 19613 | 20663
3345 | 3345 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 9 | 13111 | 16244 | 17400 | 17332 | 16746 | 14559 | 14474 | 17585 | 18499 | 18097 | 16331 | 15720 | 15406 | 19845 | 19872 | 19539 | 17534 | 16390 | 19427 | 20796
3346 | 3346 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 10 | 13309 | 16190 | 17427 | 17310 | 16640 | 14806 | 14627 | 17578 | 18612 | 18050 | 16510 | 16045 | 15635 | 20055 | 20013 | 19580 | 17789 | 16669 | 19543 | 21056
3347 | 3347 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 11 | 13499 | 16148 | 17486 | 17316 | 16632 | 14980 | 14657 | 17589 | 18802 | 18021 | 16650 | 16273 | 15821 | 20306 | 20249 | 19648 | 18113 | 16893 | 19765 | 21351
3348 | 3348 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 12 | 13745 | 16247 | 17704 | 17381 | 16724 | 15194 | 14838 | 17673 | 19086 | 18075 | 16739 | 16500 | 16088 | 20592 | 20419 | 19748 | 18296 | 17163 | 19946 | 21652
3349 | 3349 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 13 | 13936 | 16481 | 18020 | 17612 | 16890 | 15353 | 14884 | 17900 | 19427 | 18230 | 16719 | 16657 | 16164 | 20882 | 20652 | 19894 | 18306 | 17223 | 20192 | 21942
3350 | 3350 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 14 | 13855 | 16439 | 18016 | 17471 | 16718 | 15269 | 14681 | 17856 | 19415 | 18033 | 16556 | 16548 | 15934 | 20754 | 20411 | 19656 | 18116 | 16971 | 20096 | 21796
3351 | 3351 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 15 | 14162 | 16709 | 18224 | 17689 | 16820 | 15615 | 14934 | 18094 | 19591 | 18107 | 16673 | 16868 | 16157 | 20893 | 20544 | 19679 | 18187 | 17179 | 20289 | 21922
3352 | 3352 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 16 | 14438 | 17066 | 18504 | 17898 | 16928 | 15885 | 15159 | 18612 | 19781 | 18152 | 16739 | 17073 | 16286 | 20995 | 20524 | 19602 | 18132 | 17290 | 20835 | 21991
3353 | 3353 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 17 | 14758 | 17298 | 18479 | 17988 | 16914 | 16152 | 15487 | 18853 | 19799 | 18138 | 17022 | 17428 | 16592 | 21072 | 20658 | 19551 | 18428 | 17606 | 21117 | 22083
3354 | 3354 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 18 | 14886 | 17279 | 18197 | 17940 | 16796 | 16454 | 15740 | 18927 | 19530 | 18221 | 17264 | 17915 | 17112 | 21012 | 21031 | 19848 | 18848 | 18200 | 21397 | 22108
3355 | 3355 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 19 | 14790 | 17117 | 18255 | 17895 | 16786 | 16573 | 15969 | 18942 | 19784 | 18371 | 17464 | 18313 | 17692 | 21587 | 21571 | 20412 | 19285 | 18921 | 21861 | 22828
3356 | 3356 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 20 | 14782 | 16861 | 18306 | 18110 | 17085 | 16681 | 16315 | 18812 | 20069 | 18982 | 17976 | 18764 | 18414 | 22228 | 22464 | 21485 | 20235 | 19803 | 22412 | 23648
3357 | 3357 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 21 | 14807 | 16714 | 18142 | 18068 | 17222 | 16820 | 16556 | 18966 | 20261 | 19472 | 18612 | 19306 | 19085 | 22918 | 23328 | 22511 | 21303 | 20708 | 23305 | 24597
3358 | 3358 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 22 | 14054 | 15776 | 17110 | 17007 | 16415 | 16165 | 15993 | 18230 | 19470 | 18924 | 18395 | 18897 | 18776 | 22405 | 22803 | 22270 | 21384 | 20541 | 23028 | 24254
3359 | 3359 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 23 | 13126 | 14490 | 15773 | 15665 | 15292 | 15270 | 15166 | 16989 | 18263 | 17919 | 17843 | 18124 | 18032 | 21254 | 21660 | 21391 | 20951 | 19867 | 22022 | 23200
3360 | 3360 | 140 | 5 | 20 | Spring | 5 | 19 | Spring | 24 | 12425 | 13558 | 14780 | 14655 | 14429 | 14552 | 14494 | 16043 | 17297 | 17092 | 17271 | 17439 | 17418 | 20365 | 20749 | 20668 | 20464 | 19271 | 21195 | 22354
3361 | 3361 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 1 | 11193 | 13155 | 13716 | 13693 | 13660 | 13238 | 14965 | 15659 | 16257 | 16206 | 15836 | 16017 | 18240 | 19483 | 19726 | 19606 | 18573 | 20304 | 21019 | 21561
3362 | 3362 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 2 | 10956 | 12870 | 13300 | 13249 | 13262 | 12949 | 14561 | 15324 | 15746 | 15716 | 15438 | 15640 | 17738 | 18861 | 19081 | 19000 | 18075 | 19734 | 20498 | 20865
3363 | 3363 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 3 | 10846 | 12751 | 13079 | 13050 | 13078 | 12795 | 14387 | 15131 | 15422 | 15433 | 15186 | 15373 | 17425 | 18392 | 18634 | 18578 | 17716 | 19342 | 20086 | 20322
3364 | 3364 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 4 | 10813 | 12763 | 13020 | 13011 | 12898 | 12708 | 14269 | 14988 | 15156 | 15026 | 14869 | 15033 | 16983 | 17795 | 18000 | 17836 | 17160 | 18702 | 19409 | 19547
3365 | 3365 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 5 | 10888 | 13273 | 13463 | 13432 | 12940 | 12778 | 14588 | 15310 | 15449 | 14814 | 14606 | 14859 | 16934 | 17681 | 17832 | 17235 | 16616 | 18423 | 19145 | 19222
3366 | 3366 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 6 | 10951 | 14395 | 14447 | 14269 | 12989 | 12736 | 15385 | 16231 | 16159 | 14509 | 14297 | 14504 | 17303 | 17943 | 17960 | 16501 | 15976 | 18567 | 19386 | 19274
3367 | 3367 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 7 | 11225 | 15672 | 15929 | 15475 | 13448 | 12918 | 16421 | 17353 | 17313 | 14672 | 14277 | 14343 | 17946 | 18777 | 18526 | 16326 | 15663 | 19027 | 19917 | 19959
3368 | 3368 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 8 | 11802 | 16411 | 16774 | 16196 | 14152 | 13476 | 17051 | 18012 | 18032 | 15295 | 14606 | 14742 | 18326 | 19349 | 18983 | 16780 | 15911 | 19321 | 20357 | 20484
3369 | 3369 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 9 | 12394 | 16718 | 16952 | 16468 | 14796 | 13914 | 17153 | 18179 | 18187 | 15798 | 14953 | 15050 | 18210 | 19466 | 19158 | 17170 | 16218 | 19157 | 20513 | 20574
3370 | 3370 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 10 | 12678 | 16889 | 17084 | 16507 | 15034 | 14209 | 17288 | 18434 | 18368 | 16119 | 15330 | 15421 | 18428 | 19744 | 19338 | 17564 | 16657 | 19420 | 20923 | 20893
3371 | 3371 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 11 | 12633 | 16892 | 17048 | 16395 | 15027 | 14213 | 17278 | 18520 | 18325 | 16257 | 15534 | 15506 | 18509 | 19881 | 19310 | 17790 | 16922 | 19551 | 21129 | 21084
3372 | 3372 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 12 | 12946 | 17301 | 17291 | 16628 | 15235 | 14588 | 17560 | 18944 | 18541 | 16545 | 15817 | 15916 | 18814 | 20200 | 19562 | 18114 | 17212 | 19887 | 21587 | 21432
3373 | 3373 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 13 | 12915 | 17552 | 17466 | 16715 | 15148 | 14581 | 17734 | 19204 | 18725 | 16476 | 15844 | 15913 | 18993 | 20365 | 19645 | 18045 | 17234 | 20065 | 21814 | 21612
3374 | 3374 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 14 | 12551 | 17362 | 17156 | 16373 | 14843 | 14211 | 17525 | 19022 | 18415 | 16152 | 15601 | 15518 | 18750 | 19958 | 19242 | 17688 | 16967 | 19801 | 21499 | 21207
3375 | 3375 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 15 | 12913 | 17654 | 17473 | 16576 | 15090 | 14558 | 17857 | 19300 | 18706 | 16365 | 15844 | 15840 | 19059 | 20187 | 19361 | 17856 | 17185 | 20085 | 21716 | 21420
3376 | 3376 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 16 | 13205 | 17925 | 17686 | 16717 | 15251 | 14789 | 18343 | 19527 | 18844 | 16444 | 16028 | 16001 | 19633 | 20184 | 19294 | 17827 | 17313 | 20627 | 21775 | 21368
3377 | 3377 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 17 | 13471 | 17846 | 17725 | 16655 | 15479 | 15074 | 18539 | 19495 | 18833 | 16670 | 16283 | 16260 | 19858 | 20266 | 19196 | 18077 | 17593 | 20865 | 21819 | 21442
3378 | 3378 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 18 | 13552 | 17600 | 17631 | 16526 | 15444 | 15337 | 18627 | 19233 | 19034 | 16886 | 16503 | 16761 | 20091 | 20648 | 19502 | 18503 | 18027 | 21173 | 21866 | 21895
3379 | 3379 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 19 | 13662 | 17581 | 17509 | 16442 | 15334 | 15503 | 18567 | 19389 | 19171 | 16968 | 16857 | 17249 | 20326 | 21103 | 19990 | 18863 | 18630 | 21591 | 22545 | 22495
3380 | 3380 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 20 | 13834 | 17608 | 17687 | 16710 | 15591 | 15840 | 18396 | 19609 | 19598 | 17385 | 17560 | 17914 | 20663 | 21929 | 21006 | 19785 | 19589 | 22135 | 23360 | 23491
3381 | 3381 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 21 | 13879 | 17401 | 17595 | 16794 | 15763 | 16025 | 18467 | 19701 | 19860 | 17903 | 18242 | 18490 | 21233 | 22707 | 21957 | 20808 | 20623 | 22993 | 24281 | 24519
3382 | 3382 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 22 | 13222 | 16343 | 16502 | 15944 | 15232 | 15417 | 17665 | 18837 | 19004 | 17624 | 17957 | 18115 | 20751 | 22119 | 21660 | 20821 | 20560 | 22681 | 23910 | 24109
3383 | 3383 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 23 | 12431 | 15044 | 15199 | 14861 | 14576 | 14623 | 16443 | 17653 | 17797 | 17102 | 17278 | 17398 | 19680 | 21010 | 20812 | 20421 | 19973 | 21711 | 22894 | 23079
3384 | 3384 | 141 | 5 | 21 | Spring | 5 | 20 | Spring | 24 | 11791 | 14028 | 14173 | 13975 | 13899 | 13931 | 15462 | 16639 | 16785 | 16495 | 16683 | 16742 | 18776 | 20068 | 20058 | 19898 | 19436 | 20857 | 22033 | 22171
3385 | 3385 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 1 | 12567 | 13346 | 13599 | 13608 | 13374 | 14723 | 15408 | 15957 | 16142 | 15529 | 15661 | 17874 | 18866 | 19398 | 19374 | 18433 | 18320 | 21022 | 21589 | 21474
3386 | 3386 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 2 | 12276 | 12955 | 13189 | 13226 | 13066 | 14341 | 15098 | 15467 | 15635 | 15158 | 15311 | 17398 | 18426 | 18784 | 18791 | 17958 | 17882 | 20516 | 20903 | 20790
3387 | 3387 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 3 | 12121 | 12743 | 13012 | 13058 | 12916 | 14185 | 14926 | 15173 | 15349 | 14934 | 15071 | 17113 | 18100 | 18360 | 18391 | 17614 | 17535 | 20108 | 20371 | 20295
3388 | 3388 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 4 | 12156 | 12739 | 13018 | 12927 | 12851 | 14127 | 14851 | 14998 | 15141 | 14691 | 14805 | 16747 | 17665 | 17798 | 17714 | 17109 | 17028 | 19474 | 19632 | 19555
3389 | 3389 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 5 | 12482 | 13143 | 13412 | 12933 | 12822 | 14440 | 15180 | 15296 | 15330 | 14445 | 14647 | 16718 | 17616 | 17645 | 17116 | 16548 | 16588 | 19189 | 19276 | 19194
3390 | 3390 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 6 | 13459 | 14151 | 14283 | 13008 | 12826 | 15283 | 16162 | 16086 | 15898 | 14199 | 14352 | 17160 | 18120 | 17829 | 16429 | 15936 | 15994 | 19450 | 19335 | 19175
3391 | 3391 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 7 | 14743 | 15660 | 15518 | 13481 | 13032 | 16344 | 17314 | 17304 | 16889 | 14225 | 14230 | 17856 | 18867 | 18422 | 16274 | 15627 | 15643 | 19980 | 20012 | 19626
3392 | 3392 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 8 | 15472 | 16493 | 16276 | 14197 | 13487 | 17008 | 18024 | 18044 | 17554 | 14611 | 14671 | 18302 | 19439 | 18923 | 16761 | 15902 | 16004 | 20453 | 20537 | 20075
3393 | 3393 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 9 | 15736 | 16768 | 16643 | 14851 | 14029 | 17189 | 18283 | 18176 | 17752 | 15045 | 15056 | 18281 | 19738 | 19164 | 17220 | 16286 | 16337 | 20684 | 20693 | 20299
3394 | 3394 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 10 | 15813 | 16857 | 16651 | 15055 | 14298 | 17279 | 18487 | 18331 | 17821 | 15385 | 15387 | 18457 | 20059 | 19310 | 17577 | 16689 | 16736 | 21053 | 20989 | 20483
3395 | 3395 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 11 | 15815 | 16925 | 16636 | 15201 | 14529 | 17356 | 18663 | 18468 | 17894 | 15682 | 15563 | 18633 | 20323 | 19374 | 17898 | 17053 | 16978 | 21361 | 21279 | 20597
3396 | 3396 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 12 | 15817 | 16882 | 16589 | 15173 | 14510 | 17357 | 18804 | 18465 | 17882 | 15683 | 15690 | 18670 | 20488 | 19349 | 17941 | 17078 | 17132 | 21538 | 21350 | 20592
3397 | 3397 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 13 | 15876 | 16965 | 16570 | 14989 | 14422 | 17422 | 18957 | 18555 | 17874 | 15603 | 15580 | 18742 | 20599 | 19320 | 17767 | 16993 | 17012 | 21653 | 21411 | 20574
3398 | 3398 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 14 | 15866 | 16858 | 16445 | 14901 | 14405 | 17429 | 18991 | 18462 | 17724 | 15577 | 15403 | 18719 | 20514 | 19136 | 17626 | 16943 | 16801 | 21552 | 21214 | 20375
3399 | 3399 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 15 | 15968 | 16877 | 16365 | 14860 | 14389 | 17479 | 18988 | 18466 | 17617 | 15539 | 15446 | 18744 | 20470 | 18977 | 17515 | 16873 | 16822 | 21485 | 21142 | 20191
3400 | 3400 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 16 | 16418 | 17190 | 16613 | 15125 | 14732 | 18058 | 19322 | 18715 | 17780 | 15832 | 15718 | 19398 | 20681 | 19023 | 17596 | 17102 | 17034 | 21646 | 21190 | 20176
3401 | 3401 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 17 | 16758 | 17389 | 16710 | 15517 | 15072 | 18429 | 19456 | 18863 | 17874 | 16245 | 16141 | 19788 | 20860 | 19093 | 18013 | 17549 | 17464 | 21854 | 21441 | 20251
3402 | 3402 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 18 | 16706 | 17216 | 16445 | 15379 | 15072 | 18452 | 19109 | 18939 | 17885 | 16361 | 16543 | 19934 | 20737 | 19317 | 18361 | 17908 | 18020 | 21825 | 21839 | 20546
3403 | 3403 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 19 | 16539 | 17142 | 16401 | 15310 | 15281 | 18436 | 19302 | 19092 | 18004 | 16722 | 17048 | 20183 | 21285 | 19828 | 18755 | 18549 | 18771 | 22566 | 22503 | 21201
3404 | 3404 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 20 | 16301 | 17306 | 16663 | 15570 | 15759 | 18270 | 19530 | 19473 | 18568 | 17373 | 17675 | 20477 | 21909 | 20815 | 19662 | 19511 | 19702 | 23426 | 23529 | 22360
3405 | 3405 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 21 | 16136 | 17206 | 16737 | 15728 | 16109 | 18312 | 19580 | 19673 | 18982 | 18009 | 18212 | 21002 | 22533 | 21720 | 20655 | 20541 | 20592 | 24352 | 24572 | 23513
3406 | 3406 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 22 | 15148 | 16090 | 15861 | 15172 | 15586 | 17460 | 18651 | 18756 | 18338 | 17673 | 17784 | 20447 | 21937 | 21369 | 20622 | 20447 | 20371 | 23946 | 24147 | 23341
3407 | 3407 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 23 | 13889 | 14759 | 14752 | 14501 | 14764 | 16192 | 17403 | 17500 | 17327 | 16957 | 17031 | 19322 | 20783 | 20488 | 20185 | 19824 | 19692 | 22900 | 23085 | 22535
3408 | 3408 | 142 | 5 | 22 | Spring | 5 | 21 | Spring | 24 | 12964 | 13744 | 13864 | 13831 | 14146 | 15207 | 16376 | 16469 | 16469 | 16353 | 16369 | 18401 | 19870 | 19716 | 19663 | 19280 | 19073 | 22028 | 22182 | 21810
3409 | 3409 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 1 | 12742 | 12987 | 13336 | 13162 | 13030 | 14939 | 15480 | 15622 | 15792 | 15159 | 17198 | 18268 | 19152 | 18863 | 18059 | 17997 | 20250 | 21380 | 21295 | 20871
3410 | 3410 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 2 | 12476 | 12631 | 12976 | 12869 | 12760 | 14645 | 15010 | 15139 | 15332 | 14828 | 16798 | 17853 | 18554 | 18302 | 17597 | 17569 | 19752 | 20711 | 20619 | 20251
3411 | 3411 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 3 | 12358 | 12455 | 12813 | 12720 | 12614 | 14482 | 14730 | 14870 | 15074 | 14606 | 16548 | 17547 | 18111 | 17916 | 17259 | 17230 | 19381 | 20173 | 20116 | 19792
3412 | 3412 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 4 | 12403 | 12477 | 12695 | 12663 | 12571 | 14434 | 14589 | 14710 | 14750 | 14376 | 16251 | 17177 | 17594 | 17284 | 16784 | 16753 | 18809 | 19451 | 19390 | 18978
3413 | 3413 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 5 | 12872 | 12878 | 12720 | 12655 | 12609 | 14815 | 14950 | 14978 | 14555 | 14293 | 16321 | 17202 | 17500 | 16741 | 16259 | 16347 | 18558 | 19113 | 19038 | 18222
3414 | 3414 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 6 | 13993 | 13800 | 12835 | 12693 | 12587 | 15856 | 15821 | 15646 | 14332 | 14072 | 16813 | 17792 | 17837 | 16117 | 15691 | 15792 | 18747 | 19197 | 19034 | 17383
3415 | 3415 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 7 | 15262 | 15069 | 13360 | 12927 | 12760 | 17065 | 17118 | 16721 | 14541 | 14031 | 17649 | 18601 | 18711 | 16015 | 15413 | 15466 | 19220 | 19894 | 19496 | 17140
3416 | 3416 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 8 | 16013 | 15827 | 14099 | 13389 | 13292 | 17784 | 17886 | 17429 | 15200 | 14510 | 18089 | 19178 | 19304 | 16490 | 15678 | 15795 | 19426 | 20401 | 19907 | 17585
3417 | 3417 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 9 | 16310 | 16156 | 14767 | 13951 | 13695 | 18082 | 18077 | 17710 | 15698 | 14981 | 18192 | 19410 | 19397 | 16867 | 15988 | 16037 | 19274 | 20462 | 20043 | 17959
3418 | 3418 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 10 | 16280 | 16002 | 14821 | 14055 | 13789 | 18125 | 18081 | 17627 | 15818 | 15172 | 18345 | 19555 | 19482 | 17052 | 16216 | 16272 | 19471 | 20592 | 20068 | 18200
3419 | 3419 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 11 | 16225 | 15801 | 14789 | 14101 | 13721 | 18108 | 18024 | 17504 | 15881 | 15158 | 18460 | 19634 | 19544 | 17193 | 16407 | 16334 | 19678 | 20709 | 20010 | 18396
3420 | 3420 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 12 | 16360 | 15763 | 14748 | 14060 | 13827 | 18232 | 18000 | 17459 | 15896 | 15263 | 18575 | 19788 | 19592 | 17232 | 16427 | 16482 | 19856 | 20777 | 20003 | 18453
3421 | 3421 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 13 | 16548 | 15762 | 14585 | 13996 | 13757 | 18396 | 18093 | 17462 | 15766 | 15152 | 18675 | 19944 | 19688 | 17097 | 16384 | 16407 | 20003 | 20873 | 20022 | 18317
3422 | 3422 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 14 | 16616 | 15661 | 14510 | 13992 | 13652 | 18426 | 17984 | 17301 | 15710 | 14947 | 18599 | 19919 | 19549 | 17010 | 16385 | 16251 | 19982 | 20720 | 19868 | 18210
3423 | 3423 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 15 | 16933 | 15882 | 14780 | 14281 | 14033 | 18732 | 18296 | 17496 | 15955 | 15295 | 18841 | 20193 | 19807 | 17222 | 16636 | 16586 | 20194 | 20966 | 20003 | 18399
3424 | 3424 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 16 | 17232 | 16079 | 14983 | 14553 | 14318 | 19001 | 18480 | 17589 | 16086 | 15492 | 19370 | 20367 | 19854 | 17269 | 16821 | 16751 | 20735 | 20965 | 19941 | 18392
3425 | 3425 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 17 | 17296 | 16146 | 15339 | 14876 | 14754 | 19123 | 18619 | 17679 | 16445 | 15901 | 19617 | 20518 | 20076 | 17650 | 17227 | 17145 | 20925 | 21186 | 19980 | 18768
3426 | 3426 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 18 | 17032 | 15904 | 15185 | 14888 | 14999 | 18824 | 18705 | 17685 | 16609 | 16335 | 19670 | 20420 | 20417 | 18028 | 17607 | 17745 | 21085 | 21625 | 20318 | 19209
3427 | 3427 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 19 | 17086 | 15844 | 15091 | 15082 | 15248 | 18991 | 18817 | 17743 | 16714 | 16769 | 20190 | 20910 | 20893 | 18400 | 18233 | 18477 | 21966 | 22293 | 20981 | 19708
3428 | 3428 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 20 | 17182 | 16113 | 15339 | 15567 | 15657 | 19204 | 19167 | 18252 | 17127 | 17318 | 20609 | 21487 | 21725 | 19282 | 19191 | 19397 | 22769 | 23353 | 22185 | 20742
3429 | 3429 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 21 | 16969 | 16156 | 15452 | 15882 | 15821 | 19190 | 19295 | 18587 | 17581 | 17783 | 20790 | 21999 | 22433 | 20188 | 20165 | 20232 | 23349 | 24357 | 23310 | 21890
3430 | 3430 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 22 | 15893 | 15271 | 14892 | 15351 | 15203 | 18225 | 18337 | 17895 | 17248 | 17323 | 20135 | 21363 | 21813 | 20129 | 20065 | 20019 | 22971 | 23929 | 23144 | 21997
3431 | 3431 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 23 | 14572 | 14148 | 14198 | 14518 | 14372 | 16926 | 17012 | 16816 | 16676 | 16515 | 19050 | 20187 | 20661 | 19675 | 19429 | 19346 | 22047 | 22856 | 22338 | 21633
3432 | 3432 | 143 | 5 | 23 | Spring | 5 | 22 | Spring | 24 | 13568 | 13286 | 13538 | 13916 | 13692 | 15907 | 15985 | 15943 | 16063 | 15860 | 18168 | 19263 | 19712 | 19143 | 18897 | 18730 | 21214 | 21967 | 21615 | 21153
3433 | 3433 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 1 | 12739 | 12803 | 12969 | 12852 | 14243 | 15040 | 15200 | 15335 | 15021 | 16676 | 17454 | 18531 | 18883 | 17646 | 17652 | 19880 | 20625 | 21117 | 20718 | 19387
3434 | 3434 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 2 | 12362 | 12460 | 12683 | 12579 | 13920 | 14579 | 14719 | 14881 | 14665 | 16289 | 16999 | 17949 | 18274 | 17189 | 17227 | 19382 | 20075 | 20439 | 20094 | 18881
3435 | 3435 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 3 | 12151 | 12292 | 12550 | 12446 | 13787 | 14322 | 14478 | 14652 | 14459 | 16073 | 16707 | 17536 | 17874 | 16874 | 16907 | 19030 | 19653 | 19953 | 19647 | 18508
3436 | 3436 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 4 | 12161 | 12203 | 12507 | 12412 | 13771 | 14217 | 14365 | 14372 | 14252 | 15835 | 16398 | 17088 | 17377 | 16438 | 16462 | 18495 | 19013 | 19244 | 18850 | 17926
3437 | 3437 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 5 | 12572 | 12223 | 12501 | 12469 | 14130 | 14609 | 14679 | 14253 | 14070 | 15974 | 16377 | 17071 | 17289 | 15953 | 16088 | 18278 | 18512 | 18907 | 18102 | 17267
3438 | 3438 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 6 | 13555 | 12318 | 12524 | 12432 | 14932 | 15486 | 15375 | 14077 | 13847 | 16496 | 16959 | 17455 | 17510 | 15384 | 15525 | 18461 | 18665 | 18876 | 17229 | 16537
3439 | 3439 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 7 | 14949 | 12724 | 12649 | 12503 | 15939 | 16674 | 16369 | 14231 | 13796 | 17253 | 17782 | 18272 | 18033 | 14999 | 15087 | 18834 | 19216 | 19213 | 16849 | 16053
3440 | 3440 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 8 | 15543 | 13273 | 12926 | 12827 | 16334 | 17239 | 16873 | 14728 | 14008 | 17520 | 18241 | 18675 | 18304 | 15061 | 15209 | 18827 | 19529 | 19405 | 17073 | 16099
3441 | 3441 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 9 | 15666 | 13806 | 13386 | 13212 | 16433 | 17315 | 17038 | 15280 | 14405 | 17529 | 18293 | 18674 | 18337 | 15256 | 15335 | 18566 | 19446 | 19412 | 17320 | 16272
3442 | 3442 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 10 | 15658 | 13949 | 13559 | 13381 | 16556 | 17369 | 17016 | 15478 | 14667 | 17738 | 18416 | 18815 | 18393 | 15544 | 15632 | 18827 | 19650 | 19511 | 17626 | 16610
3443 | 3443 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 11 | 15622 | 13948 | 13659 | 13351 | 16636 | 17359 | 16937 | 15572 | 14842 | 17899 | 18489 | 18917 | 18340 | 15785 | 15746 | 19079 | 19824 | 19507 | 17876 | 16890
3444 | 3444 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 12 | 15597 | 13962 | 13662 | 13479 | 16754 | 17375 | 16936 | 15599 | 14855 | 18053 | 18696 | 18988 | 18347 | 15848 | 15938 | 19288 | 20093 | 19547 | 17978 | 16963
3445 | 3445 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 13 | 15740 | 13848 | 13633 | 13414 | 16890 | 17498 | 16971 | 15460 | 14805 | 18186 | 18820 | 19113 | 18385 | 15840 | 15897 | 19461 | 20252 | 19594 | 17875 | 16950
3446 | 3446 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 14 | 15682 | 13803 | 13664 | 13297 | 16904 | 17427 | 16852 | 15370 | 14789 | 18148 | 18771 | 19004 | 18289 | 15874 | 15773 | 19469 | 20272 | 19471 | 17798 | 16969
3447 | 3447 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 15 | 15891 | 13937 | 13827 | 13553 | 17055 | 17615 | 16929 | 15486 | 14931 | 18266 | 18887 | 19154 | 18328 | 16005 | 15989 | 19570 | 20374 | 19484 | 17865 | 17088
3448 | 3448 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 16 | 16224 | 14221 | 14178 | 13913 | 17603 | 17888 | 17117 | 15687 | 15222 | 18858 | 19064 | 19311 | 18420 | 16276 | 16239 | 20208 | 20510 | 19503 | 17938 | 17336
3449 | 3449 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 17 | 16585 | 14765 | 14667 | 14537 | 18023 | 18207 | 17392 | 16244 | 15799 | 19282 | 19552 | 19708 | 18641 | 16862 | 16826 | 20567 | 20985 | 19721 | 18493 | 17924
3450 | 3450 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 18 | 16573 | 14699 | 14744 | 14891 | 18118 | 18394 | 17490 | 16492 | 16076 | 19442 | 19706 | 20121 | 19020 | 17369 | 17543 | 20849 | 21265 | 20201 | 19064 | 18478
3451 | 3451 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 19 | 16523 | 14608 | 14932 | 15132 | 18469 | 18508 | 17523 | 16552 | 16417 | 19916 | 20263 | 20565 | 19506 | 17990 | 18263 | 21729 | 22092 | 20879 | 19593 | 19203
3452 | 3452 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 20 | 16687 | 14817 | 15375 | 15496 | 18516 | 18825 | 17966 | 16876 | 17019 | 20239 | 20659 | 21305 | 20451 | 18903 | 19136 | 22501 | 22960 | 22058 | 20620 | 20225
3453 | 3453 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 21 | 16557 | 14931 | 15669 | 15645 | 18262 | 18904 | 18233 | 17269 | 17593 | 20337 | 21025 | 21923 | 21246 | 19823 | 19936 | 23040 | 23735 | 23173 | 21768 | 21340
3454 | 3454 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 22 | 15413 | 14339 | 15109 | 14984 | 17303 | 17878 | 17476 | 16848 | 17193 | 19606 | 20453 | 21226 | 20857 | 19656 | 19683 | 22598 | 23458 | 22972 | 21847 | 21313
3455 | 3455 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 23 | 14057 | 13642 | 14280 | 14132 | 16084 | 16538 | 16371 | 16203 | 16418 | 18501 | 19317 | 20037 | 19949 | 19006 | 18992 | 21652 | 22482 | 22157 | 21477 | 20732
3456 | 3456 | 144 | 5 | 24 | Spring | 5 | 23 | Spring | 24 | 13061 | 12977 | 13673 | 13471 | 15139 | 15506 | 15484 | 15573 | 15810 | 17604 | 18393 | 19073 | 19164 | 18471 | 18366 | 20831 | 21606 | 21434 | 20987 | 20222
3457 | 3457 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 1 | 12286 | 12359 | 12908 | 13918 | 14147 | 14624 | 14786 | 14537 | 14581 | 16742 | 17595 | 18144 | 18265 | 17496 | 19367 | 20103 | 20911 | 20443 | 19123 | 19214
3458 | 3458 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 2 | 11954 | 12089 | 12722 | 13599 | 13809 | 14156 | 14343 | 14193 | 14262 | 16312 | 17170 | 17556 | 17713 | 17155 | 18899 | 19567 | 20356 | 19816 | 18626 | 18817
3459 | 3459 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 3 | 11803 | 11951 | 12647 | 13479 | 13639 | 13932 | 14133 | 14005 | 14065 | 16044 | 16906 | 17183 | 17350 | 16898 | 18566 | 19165 | 19943 | 19366 | 18255 | 18503
3460 | 3460 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 4 | 11848 | 11912 | 12790 | 13486 | 13632 | 13859 | 13904 | 13843 | 13886 | 15800 | 16582 | 16754 | 16779 | 16656 | 18072 | 18562 | 19271 | 18587 | 17685 | 18118
3461 | 3461 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 5 | 12252 | 11888 | 13252 | 13845 | 13917 | 14187 | 13816 | 13687 | 13842 | 15834 | 16542 | 16733 | 16288 | 16689 | 17891 | 18091 | 18747 | 17853 | 17035 | 17980
3462 | 3462 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 6 | 13205 | 11980 | 14340 | 14733 | 14961 | 14979 | 13767 | 13593 | 13687 | 16562 | 16922 | 17091 | 15738 | 17262 | 18165 | 18340 | 18629 | 17049 | 16358 | 18396
3463 | 3463 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 7 | 14528 | 12283 | 15729 | 15931 | 16291 | 16159 | 14132 | 13750 | 13711 | 17600 | 17644 | 17842 | 15718 | 18168 | 18733 | 19067 | 19039 | 16832 | 16027 | 19198
3464 | 3464 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 8 | 15280 | 12816 | 16590 | 16558 | 17051 | 16893 | 14871 | 14211 | 14218 | 18311 | 18027 | 18374 | 16222 | 18780 | 18951 | 19599 | 19342 | 17274 | 16292 | 19801
3465 | 3465 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 9 | 15588 | 13382 | 16939 | 16752 | 17250 | 17142 | 15517 | 14718 | 14703 | 18461 | 18039 | 18533 | 16604 | 18830 | 18795 | 19630 | 19381 | 17615 | 16562 | 19838
3466 | 3466 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 10 | 15434 | 13475 | 16992 | 16791 | 17197 | 17035 | 15622 | 14882 | 14875 | 18495 | 17964 | 18514 | 16779 | 19010 | 19001 | 19768 | 19392 | 17860 | 16843 | 20068
3467 | 3467 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 11 | 15217 | 13485 | 16929 | 16753 | 17112 | 16831 | 15584 | 14915 | 14848 | 18419 | 17931 | 18387 | 16903 | 19126 | 19192 | 19879 | 19535 | 18053 | 17069 | 20225
3468 | 3468 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 12 | 15099 | 13352 | 17003 | 16737 | 17122 | 16679 | 15451 | 14776 | 14859 | 18456 | 17825 | 18266 | 16850 | 19276 | 19275 | 20026 | 19521 | 18028 | 17017 | 20385
3469 | 3469 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 13 | 14953 | 13181 | 17082 | 16718 | 17075 | 16551 | 15157 | 14580 | 14610 | 18424 | 17792 | 18139 | 16575 | 19370 | 19275 | 20030 | 19522 | 17752 | 16838 | 20468
3470 | 3470 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 14 | 14673 | 13014 | 16926 | 16565 | 16855 | 16280 | 14923 | 14426 | 14233 | 18249 | 17541 | 17831 | 16307 | 19178 | 19072 | 19835 | 19234 | 17462 | 16643 | 20262
3471 | 3471 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 15 | 14579 | 12997 | 16988 | 16535 | 16814 | 16185 | 14867 | 14391 | 14270 | 18191 | 17536 | 17689 | 16214 | 19204 | 18985 | 19748 | 19198 | 17339 | 16571 | 20277
3472 | 3472 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 16 | 14823 | 13310 | 17272 | 17031 | 17058 | 16370 | 15068 | 14677 | 14510 | 18376 | 17652 | 17748 | 16312 | 19380 | 19582 | 19849 | 19216 | 17367 | 16767 | 20427
3473 | 3473 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 17 | 15048 | 13759 | 17630 | 17420 | 17510 | 16606 | 15579 | 15201 | 15068 | 18802 | 18068 | 17946 | 16845 | 19779 | 19919 | 20285 | 19641 | 17907 | 17322 | 20833
3474 | 3474 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 18 | 15049 | 13921 | 17835 | 17645 | 17604 | 16804 | 15900 | 15538 | 15721 | 19039 | 18754 | 18416 | 17452 | 20365 | 20332 | 20686 | 20571 | 18615 | 18019 | 21468
3475 | 3475 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 19 | 15178 | 14290 | 17971 | 18166 | 18063 | 17014 | 16130 | 16036 | 16320 | 19717 | 19525 | 19032 | 17982 | 20958 | 21365 | 21664 | 21644 | 19324 | 18928 | 22172
3476 | 3476 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 20 | 15453 | 14730 | 18108 | 18209 | 18236 | 17469 | 16454 | 16626 | 16849 | 20089 | 20026 | 19912 | 18821 | 21602 | 22109 | 22546 | 22485 | 20389 | 19991 | 22925
3477 | 3477 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 21 | 15445 | 14968 | 17831 | 17855 | 18075 | 17615 | 16707 | 17067 | 17214 | 20273 | 20286 | 20585 | 19621 | 21964 | 22549 | 23234 | 23216 | 21473 | 21062 | 23469
3478 | 3478 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 22 | 14575 | 14441 | 16764 | 16931 | 17250 | 16869 | 16293 | 16684 | 16735 | 19705 | 19903 | 20181 | 19552 | 21287 | 22123 | 22963 | 23095 | 21578 | 21066 | 22923
3479 | 3479 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 23 | 13433 | 13608 | 15373 | 15720 | 15990 | 15758 | 15638 | 15910 | 15893 | 18573 | 18968 | 19213 | 19053 | 20058 | 21135 | 21939 | 22258 | 21171 | 20452 | 21761
3480 | 3480 | 145 | 5 | 25 | Spring | 5 | 24 | Spring | 24 | 12574 | 13013 | 14340 | 14786 | 15013 | 14868 | 14993 | 15295 | 15224 | 17642 | 18222 | 18410 | 18499 | 19076 | 20302 | 21070 | 21598 | 20677 | 19937 | 20808
3481 | 3481 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 1 | 12130 | 12396 | 13646 | 13900 | 14291 | 14325 | 14160 | 14554 | 15996 | 16955 | 17518 | 17676 | 17106 | 18909 | 19675 | 20489 | 20828 | 18960 | 19047 | 20823
3482 | 3482 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 2 | 11819 | 12246 | 13368 | 13593 | 13993 | 13917 | 13849 | 14332 | 15644 | 16580 | 17078 | 17163 | 16689 | 18463 | 19175 | 19967 | 20256 | 18487 | 18690 | 20316
3483 | 3483 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 3 | 11648 | 12174 | 13252 | 13429 | 13851 | 13720 | 13672 | 14199 | 15450 | 16345 | 16783 | 16824 | 16387 | 18144 | 18782 | 19576 | 19813 | 18119 | 18375 | 19929
3484 | 3484 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 4 | 11577 | 12309 | 13277 | 13450 | 13832 | 13540 | 13559 | 14234 | 15269 | 16103 | 16468 | 16312 | 15996 | 17691 | 18214 | 18934 | 19138 | 17568 | 17995 | 19307
3485 | 3485 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 5 | 11595 | 12796 | 13643 | 13746 | 14148 | 13491 | 13441 | 14628 | 15450 | 16141 | 16513 | 15900 | 15557 | 17568 | 17797 | 18454 | 18622 | 16935 | 17874 | 18982
3486 | 3486 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 6 | 11737 | 13851 | 14518 | 14806 | 14905 | 13464 | 13380 | 15572 | 16083 | 16586 | 16971 | 15423 | 15068 | 17881 | 18079 | 18359 | 18632 | 16260 | 18282 | 19098
3487 | 3487 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 7 | 12108 | 15056 | 15539 | 15937 | 15710 | 13651 | 13372 | 16562 | 16850 | 17164 | 17597 | 15256 | 14666 | 18280 | 18638 | 18570 | 18995 | 15722 | 18879 | 19352
3488 | 3488 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 8 | 12610 | 15641 | 15907 | 16408 | 15917 | 14077 | 13534 | 17055 | 17086 | 17260 | 17842 | 15504 | 14687 | 18246 | 18906 | 18598 | 19156 | 15695 | 19185 | 19260
3489 | 3489 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 9 | 13091 | 15832 | 15939 | 16374 | 15865 | 14491 | 13817 | 17107 | 17053 | 17027 | 17542 | 15744 | 14860 | 17967 | 18815 | 18496 | 18957 | 15832 | 19088 | 18943
3490 | 3490 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 10 | 13314 | 16011 | 16112 | 16443 | 15819 | 14719 | 14102 | 17349 | 17303 | 17078 | 17511 | 16056 | 15214 | 18293 | 19075 | 18645 | 19026 | 16236 | 19450 | 19321
3491 | 3491 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 11 | 13328 | 16100 | 16227 | 16469 | 15813 | 14844 | 14312 | 17498 | 17423 | 17231 | 17458 | 16282 | 15502 | 18581 | 19284 | 18894 | 19058 | 16565 | 19710 | 19657
3492 | 3492 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 12 | 13469 | 16443 | 16495 | 16750 | 15922 | 15009 | 14472 | 17875 | 17674 | 17423 | 17492 | 16493 | 15699 | 18917 | 19686 | 19135 | 19142 | 16771 | 20129 | 20013
3493 | 3493 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 13 | 13162 | 16499 | 16449 | 16691 | 15848 | 14692 | 14256 | 17929 | 17623 | 17375 | 17392 | 16184 | 15489 | 18881 | 19640 | 19103 | 19057 | 16550 | 20177 | 19977
3494 | 3494 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 14 | 13039 | 16456 | 16405 | 16630 | 15740 | 14573 | 14216 | 17876 | 17568 | 17238 | 17144 | 16034 | 15426 | 18794 | 19572 | 18926 | 18772 | 16466 | 20082 | 19872
3495 | 3495 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 15 | 13025 | 16549 | 16415 | 16635 | 15822 | 14560 | 14223 | 17963 | 17559 | 17279 | 17037 | 15982 | 15412 | 18750 | 19526 | 18929 | 18632 | 16432 | 20135 | 19811
3496 | 3496 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 16 | 13338 | 16901 | 16916 | 16967 | 16113 | 14842 | 14581 | 18273 | 18208 | 17472 | 17071 | 16157 | 15704 | 19408 | 19701 | 19010 | 18564 | 16694 | 20340 | 20455
3497 | 3497 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 17 | 13875 | 17262 | 17315 | 17422 | 16483 | 15375 | 15117 | 18604 | 18595 | 17902 | 17423 | 16713 | 16284 | 19767 | 20164 | 19467 | 18979 | 17279 | 20763 | 20812
3498 | 3498 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 18 | 13857 | 17349 | 17461 | 17445 | 16898 | 15617 | 15346 | 18934 | 18794 | 18478 | 18181 | 17225 | 16840 | 20094 | 20467 | 20324 | 19862 | 17900 | 21338 | 21202
3499 | 3499 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 19 | 13943 | 17462 | 17960 | 17896 | 17412 | 15822 | 15818 | 19224 | 19416 | 19188 | 18782 | 17703 | 17604 | 21079 | 21407 | 21389 | 20800 | 18819 | 22046 | 22337
3500 | 3500 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 20 | 14156 | 17595 | 17970 | 18037 | 17572 | 16114 | 16381 | 19470 | 19704 | 19595 | 19487 | 18463 | 18497 | 21779 | 22244 | 22188 | 21885 | 19888 | 22806 | 23180
3501 | 3501 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 21 | 14259 | 17354 | 17652 | 17872 | 17433 | 16371 | 16829 | 19459 | 19701 | 19822 | 19766 | 19225 | 19378 | 22215 | 22934 | 22926 | 22632 | 21005 | 23404 | 23846
3502 | 3502 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 22 | 13658 | 16236 | 16680 | 16993 | 16697 | 15895 | 16378 | 18497 | 18930 | 19347 | 19391 | 19058 | 19178 | 21723 | 22594 | 22753 | 22531 | 20966 | 22824 | 23504
3503 | 3503 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 23 | 12970 | 14863 | 15491 | 15790 | 15655 | 15244 | 15608 | 17177 | 17843 | 18408 | 18460 | 18550 | 18505 | 20741 | 21592 | 21930 | 21726 | 20374 | 21674 | 22615
3504 | 3504 | 146 | 5 | 26 | Spring | 5 | 25 | Spring | 24 | 12306 | 13834 | 14541 | 14811 | 14871 | 14577 | 14969 | 16133 | 16937 | 17630 | 17667 | 17971 | 17949 | 19872 | 20697 | 21239 | 20998 | 19840 | 20717 | 21791
3505 | 3505 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 1 | 11845 | 13133 | 13659 | 14062 | 14245 | 13807 | 14231 | 15574 | 16160 | 16930 | 16847 | 16651 | 17106 | 19226 | 20080 | 20477 | 20009 | 18942 | 20701 | 21236
3506 | 3506 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 2 | 11598 | 12851 | 13356 | 13766 | 13898 | 13493 | 14006 | 15230 | 15758 | 16497 | 16324 | 16235 | 16788 | 18735 | 19575 | 19921 | 19369 | 18567 | 20202 | 20687
3507 | 3507 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 3 | 11469 | 12745 | 13218 | 13645 | 13741 | 13340 | 13899 | 15068 | 15526 | 16247 | 16004 | 15967 | 16556 | 18371 | 19203 | 19505 | 18912 | 18272 | 19829 | 20250
3508 | 3508 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 4 | 11444 | 12800 | 13262 | 13664 | 13745 | 13262 | 13977 | 14961 | 15362 | 16010 | 15611 | 15632 | 16360 | 17857 | 18611 | 18858 | 18166 | 17915 | 19225 | 19565
3509 | 3509 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 5 | 11440 | 13182 | 13577 | 14012 | 14101 | 13185 | 14422 | 15204 | 15471 | 16149 | 15268 | 15269 | 16462 | 17508 | 18193 | 18399 | 17345 | 17825 | 18923 | 19000
3510 | 3510 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 6 | 11495 | 14031 | 14604 | 14779 | 14896 | 13121 | 15386 | 15860 | 16218 | 16663 | 15024 | 14820 | 17042 | 17812 | 18122 | 18418 | 16729 | 18212 | 19011 | 19090
3511 | 3511 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 7 | 11647 | 15117 | 15786 | 15659 | 15945 | 13180 | 16466 | 16738 | 17154 | 17406 | 14958 | 14523 | 17819 | 18467 | 18405 | 18854 | 16335 | 18848 | 19293 | 19574
3512 | 3512 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 8 | 11878 | 15504 | 16243 | 15814 | 16337 | 13319 | 16951 | 16975 | 17541 | 17665 | 15313 | 14546 | 18136 | 18735 | 18406 | 19003 | 16561 | 19130 | 19184 | 19777
3513 | 3513 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 9 | 12157 | 15473 | 16120 | 15581 | 16050 | 13500 | 16913 | 16748 | 17326 | 17273 | 15436 | 14620 | 17954 | 18537 | 18191 | 18696 | 16764 | 18918 | 18760 | 19538
3514 | 3514 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 10 | 12295 | 15551 | 16107 | 15447 | 15830 | 13685 | 17057 | 16901 | 17404 | 17147 | 15592 | 14879 | 18171 | 18707 | 18249 | 18659 | 17027 | 19182 | 19041 | 19762
3515 | 3515 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 11 | 12570 | 15766 | 16246 | 15607 | 15793 | 13999 | 17312 | 17218 | 17643 | 17198 | 15722 | 15274 | 18514 | 19023 | 18610 | 18800 | 17245 | 19558 | 19494 | 20123
3516 | 3516 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 12 | 12561 | 15864 | 16374 | 15586 | 15617 | 13998 | 17526 | 17353 | 17834 | 17061 | 15764 | 15308 | 18771 | 19260 | 18689 | 18735 | 17339 | 19819 | 19689 | 20388
3517 | 3517 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 13 | 12517 | 15967 | 16456 | 15661 | 15649 | 13928 | 17727 | 17461 | 17933 | 17105 | 15610 | 15240 | 18974 | 19358 | 18804 | 18789 | 17187 | 20012 | 19800 | 20489
3518 | 3518 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 14 | 12511 | 15993 | 16463 | 15626 | 15487 | 13959 | 17745 | 17478 | 17930 | 16932 | 15405 | 15250 | 18957 | 19349 | 18705 | 18575 | 16937 | 19982 | 19766 | 20470
3519 | 3519 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 15 | 12486 | 15975 | 16435 | 15666 | 15379 | 13931 | 17797 | 17428 | 17868 | 16791 | 15365 | 15200 | 18979 | 19269 | 18671 | 18396 | 16863 | 19997 | 19668 | 20379
3520 | 3520 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 16 | 12843 | 16400 | 16764 | 15957 | 15505 | 14282 | 18099 | 18025 | 18117 | 16833 | 15601 | 15490 | 19203 | 19441 | 18747 | 18314 | 17023 | 20194 | 20283 | 20514
3521 | 3521 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 17 | 13438 | 16916 | 17360 | 16456 | 16032 | 14959 | 18565 | 18536 | 18695 | 17320 | 16262 | 16200 | 19754 | 20033 | 19335 | 18864 | 17638 | 20754 | 20777 | 21115
3522 | 3522 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 18 | 13561 | 17093 | 17429 | 16869 | 16594 | 15217 | 18899 | 18752 | 18903 | 18079 | 17081 | 16755 | 20308 | 20378 | 20216 | 19796 | 18655 | 21372 | 21209 | 21554
3523 | 3523 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 19 | 13836 | 17506 | 17776 | 17282 | 16767 | 15601 | 19098 | 19259 | 19439 | 18541 | 17472 | 17410 | 20788 | 21207 | 21159 | 20619 | 19395 | 22005 | 22276 | 22526
3524 | 3524 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 20 | 14217 | 17470 | 17828 | 17379 | 17080 | 16108 | 19279 | 19459 | 19687 | 19097 | 18035 | 18203 | 21348 | 21933 | 21888 | 21637 | 20319 | 22737 | 23089 | 23425
3525 | 3525 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 21 | 14450 | 17064 | 17575 | 17148 | 16836 | 16458 | 19151 | 19331 | 19787 | 19218 | 18382 | 18960 | 21652 | 22497 | 22518 | 22284 | 21115 | 23267 | 23693 | 24238
3526 | 3526 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 22 | 13890 | 16091 | 16685 | 16397 | 16174 | 15976 | 18146 | 18526 | 19139 | 18788 | 18115 | 18720 | 20913 | 22117 | 22291 | 22170 | 21146 | 22667 | 23338 | 24032
3527 | 3527 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 23 | 13094 | 14909 | 15483 | 15375 | 15156 | 15195 | 16806 | 17418 | 18019 | 17841 | 17399 | 18034 | 19694 | 21091 | 21460 | 21352 | 20518 | 21520 | 22445 | 23088
3528 | 3528 | 147 | 5 | 27 | Spring | 5 | 26 | Spring | 24 | 12493 | 13993 | 14510 | 14597 | 14307 | 14563 | 15765 | 16487 | 17069 | 17029 | 16801 | 17460 | 18700 | 20196 | 20770 | 20615 | 19982 | 20558 | 21626 | 22236
3529 | 3529 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 1 | 11561 | 12795 | 13446 | 13662 | 13376 | 13524 | 14834 | 15366 | 16004 | 15941 | 15734 | 16306 | 18132 | 19256 | 19709 | 19333 | 18416 | 20205 | 20747 | 21339
3530 | 3530 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 2 | 11433 | 12517 | 13192 | 13345 | 12977 | 13331 | 14524 | 15001 | 15665 | 15463 | 15305 | 16022 | 17712 | 18775 | 19180 | 18727 | 17901 | 19725 | 20222 | 20802
3531 | 3531 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 3 | 11368 | 12365 | 13072 | 13193 | 12771 | 13224 | 14368 | 14781 | 15456 | 15157 | 15056 | 15802 | 17412 | 18415 | 18775 | 18272 | 17542 | 19346 | 19777 | 20367
3532 | 3532 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 4 | 11513 | 12421 | 13110 | 13222 | 12674 | 13332 | 14306 | 14675 | 15286 | 14831 | 14718 | 15658 | 17019 | 17875 | 18172 | 17564 | 16907 | 18762 | 19100 | 19642
3533 | 3533 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 5 | 11993 | 12712 | 13434 | 13564 | 12619 | 13770 | 14562 | 14807 | 15373 | 14527 | 14418 | 15785 | 16934 | 17480 | 17726 | 16748 | 16174 | 18448 | 18512 | 19029
3534 | 3534 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 6 | 13064 | 13765 | 14281 | 14441 | 12822 | 14815 | 15328 | 15666 | 15929 | 14415 | 14142 | 16478 | 17323 | 17515 | 17845 | 16214 | 15566 | 18606 | 18662 | 18863
3535 | 3535 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 7 | 14420 | 15062 | 15287 | 15615 | 13150 | 16007 | 16359 | 16746 | 16694 | 14514 | 14035 | 17401 | 17897 | 17927 | 18409 | 15935 | 15253 | 19003 | 19245 | 19139
3536 | 3536 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 8 | 15323 | 15912 | 15846 | 16400 | 13972 | 16869 | 17010 | 17554 | 17106 | 15232 | 14474 | 18127 | 18204 | 18327 | 18951 | 16496 | 15659 | 19271 | 19827 | 19501
3537 | 3537 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 9 | 15712 | 16110 | 15941 | 16433 | 14553 | 17138 | 17106 | 17668 | 17071 | 15666 | 14837 | 18257 | 18131 | 18414 | 18953 | 16993 | 16080 | 19143 | 19882 | 19579
3538 | 3538 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 10 | 15888 | 16165 | 15889 | 16279 | 14695 | 17346 | 17323 | 17813 | 17109 | 15895 | 15130 | 18541 | 18437 | 18541 | 18998 | 17331 | 16465 | 19498 | 20183 | 19763
3539 | 3539 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 11 | 16020 | 16228 | 15979 | 16151 | 14653 | 17522 | 17559 | 17962 | 17290 | 15949 | 15333 | 18798 | 18757 | 18826 | 19061 | 17470 | 16720 | 19878 | 20481 | 20111
3540 | 3540 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 12 | 16219 | 16292 | 15912 | 15924 | 14607 | 17694 | 17649 | 18101 | 17335 | 15945 | 15460 | 19005 | 18950 | 18859 | 18939 | 17515 | 16877 | 20032 | 20704 | 20180
3541 | 3541 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 13 | 16416 | 16365 | 15987 | 15958 | 14431 | 17898 | 17760 | 18199 | 17419 | 15791 | 15435 | 19210 | 19055 | 18971 | 18993 | 17360 | 16836 | 20147 | 20808 | 20305
3542 | 3542 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 14 | 16386 | 16329 | 15902 | 15754 | 14190 | 17868 | 17731 | 18158 | 17305 | 15546 | 15385 | 19159 | 18985 | 18827 | 18730 | 17076 | 16750 | 20064 | 20743 | 20137
3543 | 3543 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 15 | 16669 | 16544 | 16175 | 15886 | 14396 | 18149 | 17908 | 18334 | 17541 | 15733 | 15609 | 19420 | 19137 | 19026 | 18784 | 17235 | 16956 | 20192 | 20878 | 20311
3544 | 3544 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 16 | 16833 | 16688 | 16287 | 15830 | 14543 | 18271 | 18288 | 18408 | 17575 | 15799 | 15849 | 19476 | 19617 | 18934 | 18533 | 17220 | 17165 | 20620 | 20823 | 20160
3545 | 3545 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 17 | 17007 | 16949 | 16456 | 16038 | 14862 | 18427 | 18488 | 18669 | 17821 | 16133 | 16394 | 19716 | 19789 | 19208 | 18770 | 17517 | 17729 | 20800 | 21112 | 20438
3546 | 3546 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 18 | 16897 | 16809 | 16584 | 16342 | 15218 | 18535 | 18487 | 18639 | 18182 | 16700 | 16932 | 20002 | 19929 | 19853 | 19469 | 18299 | 18434 | 21013 | 21331 | 21170
3547 | 3547 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 19 | 16792 | 16995 | 16834 | 16369 | 15257 | 18587 | 18826 | 19004 | 18636 | 16882 | 17482 | 20316 | 20669 | 20624 | 20125 | 18892 | 19178 | 21942 | 22172 | 22085
3548 | 3548 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 20 | 16848 | 17012 | 16871 | 16626 | 15419 | 18727 | 18960 | 19158 | 18904 | 17321 | 17908 | 20784 | 21245 | 21263 | 21056 | 19766 | 19956 | 22734 | 23036 | 22879
3549 | 3549 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 21 | 16552 | 16748 | 16617 | 16353 | 15338 | 18569 | 18778 | 19188 | 18995 | 17589 | 18374 | 21027 | 21572 | 21833 | 21670 | 20529 | 20788 | 23333 | 23856 | 23694
3550 | 3550 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 22 | 15398 | 15817 | 15823 | 15632 | 14766 | 17506 | 17893 | 18452 | 18438 | 17237 | 18099 | 20208 | 21005 | 21539 | 21493 | 20476 | 20744 | 22935 | 23613 | 23572
3551 | 3551 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 23 | 14043 | 14640 | 14825 | 14644 | 13968 | 16181 | 16786 | 17330 | 17515 | 16529 | 17286 | 18992 | 20030 | 20718 | 20683 | 19863 | 19999 | 22055 | 22691 | 22818
3552 | 3552 | 148 | 5 | 28 | Spring | 5 | 27 | Spring | 24 | 12956 | 13608 | 13987 | 13742 | 13311 | 15078 | 15781 | 16303 | 16662 | 15920 | 16604 | 17928 | 19098 | 19963 | 19882 | 19333 | 19355 | 21174 | 21771 | 22090
3553 | 3553 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 1 | 12295 | 12933 | 13420 | 13209 | 13114 | 14461 | 14980 | 15585 | 16018 | 15291 | 15926 | 17648 | 18465 | 19242 | 18974 | 18159 | 18630 | 20621 | 21224 | 21320
3554 | 3554 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 2 | 12034 | 12688 | 13123 | 12810 | 12779 | 14158 | 14626 | 15251 | 15625 | 14874 | 15589 | 17240 | 18006 | 18724 | 18378 | 17645 | 18176 | 20096 | 20681 | 20737
3555 | 3555 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 3 | 11929 | 12595 | 12996 | 12633 | 12648 | 14036 | 14443 | 15088 | 15405 | 14671 | 15387 | 16984 | 17665 | 18356 | 17958 | 17320 | 17858 | 19675 | 20278 | 20301
3556 | 3556 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 4 | 11967 | 12608 | 13014 | 12528 | 12513 | 13980 | 14353 | 14945 | 15207 | 14352 | 15228 | 16621 | 17181 | 17773 | 17260 | 16682 | 17413 | 18987 | 19534 | 19538
3557 | 3557 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 5 | 12366 | 12993 | 13417 | 12537 | 12507 | 14322 | 14585 | 15140 | 15431 | 14160 | 15353 | 16652 | 16909 | 17437 | 16541 | 16028 | 17111 | 18472 | 18984 | 18983
3558 | 3558 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 6 | 13234 | 13835 | 14305 | 12737 | 12540 | 15107 | 15477 | 15751 | 16055 | 13921 | 15993 | 17078 | 17289 | 17597 | 16025 | 15413 | 17396 | 18615 | 18796 | 18932
3559 | 3559 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 7 | 14461 | 14934 | 15563 | 13156 | 12783 | 16230 | 16654 | 16653 | 16988 | 13929 | 17003 | 17776 | 18119 | 18250 | 15833 | 15177 | 18148 | 19253 | 19130 | 19438
3560 | 3560 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 8 | 15135 | 15400 | 16266 | 13887 | 13175 | 16805 | 17398 | 17057 | 17527 | 14311 | 17598 | 18086 | 18681 | 18699 | 16317 | 15483 | 18709 | 19753 | 19390 | 19829
3561 | 3561 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 9 | 15307 | 15406 | 16229 | 14389 | 13528 | 16816 | 17442 | 16949 | 17354 | 14606 | 17796 | 17936 | 18697 | 18605 | 16724 | 15816 | 19041 | 19717 | 19358 | 19720
3562 | 3562 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 10 | 15337 | 15233 | 15934 | 14378 | 13606 | 16872 | 17422 | 16838 | 17164 | 14743 | 18020 | 18085 | 18804 | 18499 | 16910 | 16046 | 19369 | 19862 | 19404 | 19673
3563 | 3563 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 11 | 15354 | 15169 | 15681 | 14214 | 13597 | 16964 | 17431 | 16890 | 17007 | 14808 | 18188 | 18280 | 18918 | 18429 | 16916 | 16179 | 19603 | 20031 | 19620 | 19663
3564 | 3564 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 12 | 15383 | 15091 | 15423 | 14141 | 13669 | 17022 | 17534 | 16840 | 16803 | 14901 | 18303 | 18380 | 19088 | 18284 | 16931 | 16313 | 19770 | 20222 | 19660 | 19538
3565 | 3565 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 13 | 15503 | 15161 | 15470 | 13991 | 13654 | 17148 | 17648 | 16947 | 16862 | 14896 | 18443 | 18512 | 19206 | 18357 | 16794 | 16303 | 19907 | 20343 | 19798 | 19620
3566 | 3566 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 14 | 15468 | 15071 | 15239 | 13728 | 13602 | 17092 | 17577 | 16815 | 16635 | 14816 | 18406 | 18426 | 19141 | 18073 | 16485 | 16193 | 19860 | 20246 | 19598 | 19317
3567 | 3567 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 15 | 15537 | 15166 | 15217 | 13774 | 13692 | 17114 | 17595 | 16895 | 16577 | 14887 | 18531 | 18422 | 19139 | 17972 | 16488 | 16242 | 19966 | 20221 | 19619 | 19192
3568 | 3568 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 16 | 15968 | 15507 | 15411 | 14145 | 14194 | 17726 | 17918 | 17166 | 16662 | 15369 | 18837 | 19103 | 19347 | 17978 | 16718 | 16667 | 20200 | 20402 | 19709 | 19147
3569 | 3569 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 17 | 16314 | 15815 | 15751 | 14599 | 14859 | 18070 | 18321 | 17549 | 16971 | 16049 | 19215 | 19405 | 19772 | 18349 | 17157 | 17370 | 20605 | 20829 | 20134 | 19529
3570 | 3570 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 18 | 16439 | 16072 | 16130 | 15073 | 15266 | 18220 | 18421 | 18005 | 17634 | 16700 | 19457 | 19678 | 20030 | 19165 | 18067 | 18205 | 21072 | 21190 | 21022 | 20425
3571 | 3571 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 19 | 16754 | 16301 | 16157 | 15115 | 15648 | 18569 | 18787 | 18424 | 17947 | 17223 | 19900 | 20398 | 20730 | 19814 | 18660 | 18966 | 21772 | 22060 | 21972 | 21225
3572 | 3572 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 20 | 16699 | 16330 | 16404 | 15269 | 15908 | 18696 | 18926 | 18637 | 18430 | 17588 | 20355 | 20929 | 21397 | 20720 | 19514 | 19746 | 22450 | 22962 | 22780 | 22300
3573 | 3573 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 21 | 16318 | 16096 | 16142 | 15191 | 16048 | 18505 | 18928 | 18682 | 18505 | 18022 | 20515 | 21215 | 21919 | 21296 | 20266 | 20583 | 22956 | 23808 | 23628 | 23122
3574 | 3574 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 22 | 15306 | 15298 | 15400 | 14594 | 15539 | 17590 | 18141 | 18077 | 17980 | 17713 | 19796 | 20588 | 21465 | 21078 | 20182 | 20515 | 22430 | 23544 | 23502 | 23070
3575 | 3575 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 23 | 14128 | 14295 | 14388 | 13778 | 14623 | 16433 | 16972 | 17101 | 17023 | 16861 | 18624 | 19558 | 20423 | 20228 | 19526 | 19733 | 21325 | 22580 | 22721 | 22295
3576 | 3576 | 149 | 5 | 29 | Spring | 5 | 28 | Spring | 24 | 13170 | 13449 | 13482 | 13127 | 13896 | 15415 | 15924 | 16232 | 16136 | 16160 | 17526 | 18608 | 19467 | 19408 | 18977 | 19078 | 20252 | 21653 | 21979 | 21504
3577 | 3577 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 1 | 12409 | 12986 | 13087 | 13076 | 13432 | 14683 | 15282 | 15663 | 15550 | 15602 | 17169 | 18032 | 18950 | 18622 | 17968 | 18456 | 20165 | 21194 | 21306 | 20632
3578 | 3578 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 2 | 12138 | 12717 | 12709 | 12751 | 13175 | 14340 | 14961 | 15288 | 15084 | 15279 | 16757 | 17590 | 18477 | 18044 | 17467 | 18020 | 19638 | 20654 | 20739 | 19988
3579 | 3579 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 3 | 12005 | 12610 | 12548 | 12629 | 13066 | 14169 | 14813 | 15096 | 14823 | 15098 | 16465 | 17278 | 18165 | 17646 | 17150 | 17717 | 19215 | 20247 | 20298 | 19526
3580 | 3580 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 4 | 12065 | 12650 | 12462 | 12507 | 13156 | 14108 | 14705 | 14937 | 14553 | 14964 | 16178 | 16877 | 17680 | 17017 | 16570 | 17320 | 18646 | 19555 | 19572 | 18716
3581 | 3581 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 5 | 12389 | 12989 | 12416 | 12434 | 13528 | 14286 | 14849 | 15112 | 14342 | 15021 | 16147 | 16655 | 17379 | 16331 | 15931 | 17026 | 18209 | 19006 | 19007 | 17816
3582 | 3582 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 6 | 13418 | 13900 | 12638 | 12480 | 14494 | 15201 | 15496 | 15791 | 14296 | 15677 | 16622 | 17134 | 17473 | 15888 | 15372 | 17359 | 18375 | 18853 | 18982 | 17166
3583 | 3583 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 7 | 14716 | 15135 | 13054 | 12720 | 15665 | 16374 | 16417 | 16773 | 14460 | 16706 | 17397 | 17988 | 17939 | 15691 | 15112 | 18092 | 18900 | 19148 | 19440 | 16831
3584 | 3584 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 8 | 15539 | 15893 | 13886 | 13215 | 16389 | 17205 | 16921 | 17456 | 15173 | 17421 | 17716 | 18661 | 18308 | 16239 | 15480 | 18733 | 19070 | 19447 | 19872 | 17348
3585 | 3585 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 9 | 15647 | 15923 | 14488 | 13653 | 16675 | 17357 | 16944 | 17443 | 15541 | 17782 | 17774 | 18688 | 18299 | 16653 | 15801 | 19066 | 19057 | 19402 | 19748 | 17736
3586 | 3586 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 10 | 15465 | 15564 | 14420 | 13661 | 16732 | 17272 | 16768 | 17181 | 15532 | 17955 | 17913 | 18704 | 18204 | 16760 | 15966 | 19309 | 19267 | 19377 | 19636 | 17904
3587 | 3587 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 11 | 15423 | 15331 | 14269 | 13671 | 16833 | 17287 | 16823 | 17034 | 15467 | 18136 | 18040 | 18825 | 18374 | 16771 | 16115 | 19562 | 19487 | 19607 | 19651 | 17965
3588 | 3588 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 12 | 15453 | 15124 | 14232 | 13770 | 16945 | 17416 | 16801 | 16850 | 15458 | 18283 | 18187 | 19016 | 18406 | 16823 | 16288 | 19757 | 19670 | 19682 | 19560 | 18036
3589 | 3589 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 13 | 15551 | 15150 | 14085 | 13755 | 17092 | 17530 | 16906 | 16911 | 15339 | 18424 | 18337 | 19138 | 18557 | 16693 | 16279 | 19886 | 19838 | 19821 | 19646 | 17905
3590 | 3590 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 14 | 15493 | 14946 | 13844 | 13710 | 17082 | 17484 | 16804 | 16693 | 15074 | 18417 | 18323 | 19082 | 18401 | 16410 | 16201 | 19845 | 19780 | 19654 | 19369 | 17607
3591 | 3591 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 15 | 15545 | 14913 | 13876 | 13778 | 17214 | 17490 | 16874 | 16619 | 15089 | 18530 | 18467 | 19064 | 18427 | 16407 | 16235 | 19934 | 19896 | 19661 | 19232 | 17591
3592 | 3592 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 16 | 15911 | 15097 | 14217 | 14284 | 17556 | 17798 | 17136 | 16717 | 15368 | 18827 | 19139 | 19284 | 18560 | 16617 | 16646 | 20174 | 20557 | 19731 | 19162 | 17769
3593 | 3593 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 17 | 16346 | 15445 | 14679 | 14958 | 17885 | 18226 | 17535 | 17037 | 15869 | 19215 | 19513 | 19717 | 18996 | 17077 | 17368 | 20588 | 21016 | 20177 | 19566 | 18227
3594 | 3594 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 18 | 16309 | 15736 | 15032 | 15282 | 17913 | 18271 | 17892 | 17585 | 16506 | 19378 | 19678 | 19907 | 19725 | 17935 | 18159 | 20991 | 21279 | 21005 | 20410 | 19149
3595 | 3595 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 19 | 16517 | 15759 | 15055 | 15635 | 18162 | 18621 | 18292 | 17837 | 16674 | 19767 | 20153 | 20536 | 20494 | 18483 | 18887 | 21675 | 22025 | 21966 | 21223 | 19849
3596 | 3596 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 20 | 16561 | 15988 | 15188 | 15883 | 18391 | 18734 | 18473 | 18257 | 17070 | 20148 | 20739 | 21141 | 21087 | 19290 | 19639 | 22343 | 22970 | 22788 | 22312 | 20805
3597 | 3597 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 21 | 16294 | 15654 | 15035 | 15961 | 18170 | 18640 | 18409 | 18216 | 17264 | 20192 | 20787 | 21546 | 21597 | 19941 | 20390 | 22782 | 23438 | 23582 | 23089 | 21688
3598 | 3598 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 22 | 15410 | 14961 | 14478 | 15497 | 17308 | 17868 | 17802 | 17701 | 16930 | 19485 | 20207 | 21096 | 21325 | 19871 | 20342 | 22299 | 23117 | 23491 | 23082 | 21779
3599 | 3599 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 23 | 14193 | 13954 | 13656 | 14584 | 16044 | 16675 | 16801 | 16709 | 16167 | 18299 | 19111 | 20021 | 20443 | 19193 | 19545 | 21172 | 22122 | 22693 | 22296 | 21176
3600 | 3600 | 150 | 5 | 30 | Spring | 5 | 29 | Spring | 24 | 13176 | 13067 | 13004 | 13861 | 14963 | 15626 | 15925 | 15792 | 15535 | 17196 | 18219 | 19033 | 19662 | 18623 | 18890 | 20090 | 21261 | 21944 | 21496 | 20640
3601 | 3601 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 1 | 12423 | 12480 | 12819 | 13187 | 14126 | 14769 | 15170 | 15018 | 14920 | 16582 | 17543 | 18292 | 18834 | 17503 | 18051 | 19755 | 20686 | 21087 | 20432 | 19236
3602 | 3602 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 2 | 12179 | 12107 | 12490 | 12918 | 13798 | 14444 | 14785 | 14554 | 14505 | 16169 | 17151 | 17828 | 18321 | 16995 | 17601 | 19237 | 20177 | 20496 | 19775 | 18688
3603 | 3603 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 3 | 12092 | 11934 | 12376 | 12819 | 13630 | 14305 | 14608 | 14309 | 14322 | 15898 | 16835 | 17541 | 17980 | 16697 | 17317 | 18823 | 19723 | 20059 | 19301 | 18329
3604 | 3604 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 4 | 12106 | 11862 | 12269 | 12893 | 13621 | 14237 | 14503 | 14049 | 14018 | 15670 | 16510 | 17116 | 17466 | 16155 | 16949 | 18282 | 19095 | 19349 | 18502 | 17639
3605 | 3605 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 5 | 12457 | 11862 | 12224 | 13233 | 13903 | 14440 | 14753 | 13821 | 13770 | 15722 | 16350 | 16904 | 17189 | 15573 | 16705 | 17894 | 18568 | 18820 | 17629 | 16890
3606 | 3606 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 6 | 13303 | 12112 | 12310 | 14196 | 14717 | 15139 | 15516 | 13819 | 13549 | 16276 | 16721 | 17089 | 17441 | 15064 | 17079 | 18100 | 18645 | 18821 | 17006 | 16219
3607 | 3607 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 7 | 14372 | 12523 | 12579 | 15398 | 15865 | 16083 | 16560 | 14059 | 13571 | 17113 | 17470 | 17618 | 18107 | 14829 | 17830 | 18647 | 19089 | 19288 | 16659 | 15881
3608 | 3608 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 8 | 14819 | 13273 | 13004 | 16038 | 16317 | 16498 | 17159 | 14722 | 13976 | 17382 | 17871 | 17926 | 18544 | 15107 | 18383 | 18737 | 19324 | 19638 | 17055 | 16146
3609 | 3609 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 9 | 14811 | 13801 | 13400 | 16351 | 16392 | 16463 | 17087 | 15184 | 14359 | 17395 | 17895 | 17858 | 18381 | 15371 | 18669 | 18648 | 19280 | 19441 | 17378 | 16393
3610 | 3610 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 10 | 14580 | 13734 | 13409 | 16419 | 16421 | 16260 | 16813 | 15199 | 14449 | 17527 | 17884 | 17757 | 18210 | 15527 | 18902 | 18869 | 19353 | 19325 | 17541 | 16600
3611 | 3611 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 11 | 14501 | 13572 | 13384 | 16474 | 16408 | 16265 | 16613 | 15092 | 14503 | 17614 | 17950 | 17878 | 18121 | 15637 | 19110 | 19048 | 19507 | 19290 | 17572 | 16751
3612 | 3612 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 12 | 14456 | 13517 | 13476 | 16585 | 16501 | 16229 | 16419 | 15080 | 14623 | 17751 | 18176 | 17906 | 18006 | 15804 | 19300 | 19232 | 19812 | 19197 | 17640 | 16930
3613 | 3613 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 13 | 14467 | 13326 | 13414 | 16674 | 16581 | 16288 | 16432 | 14897 | 14565 | 17852 | 18230 | 17994 | 18030 | 15752 | 19401 | 19337 | 19878 | 19233 | 17462 | 16874
3614 | 3614 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 14 | 14459 | 13148 | 13419 | 16727 | 16632 | 16241 | 16268 | 14704 | 14565 | 17898 | 18199 | 17910 | 17825 | 15729 | 19412 | 19349 | 19820 | 19008 | 17219 | 16840
3615 | 3615 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 15 | 14422 | 13067 | 13371 | 16755 | 16673 | 16202 | 16084 | 14609 | 14497 | 17930 | 18236 | 17834 | 17595 | 15653 | 19392 | 19359 | 19834 | 18760 | 17086 | 16755
3616 | 3616 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 16 | 14694 | 13348 | 13820 | 17041 | 17222 | 16421 | 16140 | 14853 | 14916 | 18551 | 18436 | 17933 | 17541 | 16014 | 19566 | 19989 | 19976 | 18636 | 17210 | 17097
3617 | 3617 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 17 | 15032 | 13818 | 14501 | 17383 | 17653 | 16841 | 16481 | 15359 | 15622 | 18939 | 18872 | 18382 | 17944 | 16757 | 20005 | 20462 | 20362 | 19067 | 17694 | 17851
3618 | 3618 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 18 | 15352 | 14260 | 14893 | 17519 | 17871 | 17305 | 17124 | 16058 | 16333 | 19238 | 19363 | 19190 | 18835 | 17666 | 20542 | 20849 | 20997 | 20060 | 18752 | 18827
3619 | 3619 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 19 | 15704 | 14419 | 15385 | 17922 | 18158 | 17855 | 17501 | 16340 | 16958 | 19798 | 20023 | 20075 | 19579 | 18544 | 21361 | 21747 | 21982 | 21027 | 19617 | 19806
3620 | 3620 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 20 | 15782 | 14580 | 15650 | 18179 | 18472 | 18068 | 17922 | 16731 | 17318 | 20337 | 20483 | 20657 | 20475 | 19301 | 22053 | 22702 | 22820 | 22161 | 20640 | 20670
3621 | 3621 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 21 | 15496 | 14436 | 15709 | 17928 | 18104 | 17958 | 17814 | 16843 | 17646 | 20300 | 20634 | 21071 | 20936 | 20013 | 22455 | 23128 | 23421 | 22923 | 21526 | 21570
3622 | 3622 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 22 | 14690 | 13847 | 15193 | 17006 | 17214 | 17269 | 17218 | 16403 | 17301 | 19631 | 20202 | 20691 | 20673 | 19895 | 21914 | 22730 | 23258 | 22865 | 21562 | 21583
3623 | 3623 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 23 | 13686 | 13007 | 14264 | 15748 | 16018 | 16244 | 16187 | 15608 | 16425 | 18506 | 19203 | 19777 | 19792 | 19072 | 20765 | 21714 | 22345 | 22057 | 20951 | 20816
3624 | 3624 | 151 | 5 | 31 | Spring | 5 | 30 | Spring | 24 | 12865 | 12358 | 13548 | 14687 | 15121 | 15382 | 15274 | 14978 | 15742 | 17625 | 18304 | 18994 | 18964 | 18424 | 19681 | 20868 | 21480 | 21275 | 20434 | 20194
3625 | 3625 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 1 | 12349 | 12323 | 13014 | 13943 | 14429 | 14748 | 14626 | 14564 | 15088 | 17021 | 17788 | 18270 | 18090 | 17704 | 19432 | 20363 | 20994 | 20279 | 19148 | 19428
3626 | 3626 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 2 | 12081 | 12017 | 12764 | 13620 | 14126 | 14377 | 14176 | 14157 | 14766 | 16642 | 17306 | 17774 | 17515 | 17271 | 18917 | 19872 | 20411 | 19640 | 18600 | 18949
3627 | 3627 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 3 | 11977 | 11882 | 12657 | 13444 | 13925 | 14202 | 13937 | 13974 | 14596 | 16335 | 16968 | 17445 | 17124 | 16984 | 18512 | 19420 | 19941 | 19167 | 18240 | 18611
3628 | 3628 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 4 | 12036 | 11799 | 12749 | 13476 | 13917 | 14143 | 13731 | 13734 | 14520 | 16077 | 16612 | 17016 | 16557 | 16661 | 18014 | 18831 | 19273 | 18396 | 17562 | 18143
3629 | 3629 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 5 | 12389 | 11743 | 13083 | 13760 | 14106 | 14410 | 13529 | 13502 | 14644 | 15946 | 16420 | 16816 | 15948 | 16458 | 17669 | 18343 | 18708 | 17546 | 16816 | 17774
3630 | 3630 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 6 | 13312 | 11862 | 14085 | 14627 | 14863 | 15242 | 13623 | 13385 | 15365 | 16423 | 16731 | 17157 | 15586 | 16869 | 17914 | 18457 | 18627 | 16939 | 16148 | 18038
3631 | 3631 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 7 | 14602 | 12206 | 15364 | 15852 | 15924 | 16370 | 13972 | 13511 | 16481 | 17289 | 17463 | 17931 | 15477 | 17692 | 18537 | 18963 | 19098 | 16645 | 15856 | 18774
3632 | 3632 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 8 | 15206 | 12627 | 15996 | 16284 | 16408 | 16949 | 14628 | 13906 | 17078 | 17712 | 17997 | 18352 | 15895 | 18224 | 18605 | 19178 | 19518 | 17002 | 16079 | 19296
3633 | 3633 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 9 | 15263 | 13138 | 16417 | 16447 | 16624 | 16966 | 15190 | 14403 | 17480 | 17848 | 18387 | 18291 | 16352 | 18588 | 18611 | 19222 | 19865 | 17409 | 16418 | 19644
3634 | 3634 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 10 | 15265 | 13507 | 16856 | 16830 | 16866 | 17037 | 15553 | 14845 | 18003 | 18194 | 18758 | 18469 | 16813 | 19182 | 19190 | 19651 | 20317 | 17926 | 16981 | 20285
3635 | 3635 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 11 | 15158 | 13641 | 17065 | 16953 | 16983 | 16973 | 15585 | 15035 | 18297 | 18401 | 19026 | 18517 | 16944 | 19542 | 19520 | 19951 | 20679 | 18109 | 17285 | 20691
3636 | 3636 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 12 | 14941 | 13715 | 17169 | 17039 | 17109 | 16773 | 15568 | 15153 | 18424 | 18623 | 19236 | 18381 | 16979 | 19717 | 19688 | 20234 | 20947 | 18167 | 17452 | 20883
3637 | 3637 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 13 | 14919 | 13668 | 17266 | 17137 | 17158 | 16795 | 15394 | 15116 | 18529 | 18690 | 19421 | 18422 | 16813 | 19826 | 19804 | 20304 | 21142 | 18001 | 17412 | 20996
3638 | 3638 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 14 | 14867 | 13756 | 17421 | 17290 | 17236 | 16733 | 15300 | 15213 | 18677 | 18760 | 19502 | 18328 | 16692 | 19943 | 19920 | 20351 | 21189 | 17858 | 17476 | 21102
3639 | 3639 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 15 | 14875 | 13839 | 17594 | 17480 | 17435 | 16696 | 15349 | 15300 | 18814 | 18937 | 19641 | 18253 | 16717 | 20065 | 20075 | 20512 | 21298 | 17866 | 17534 | 21217
3640 | 3640 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 16 | 14991 | 14263 | 17871 | 17975 | 17687 | 16745 | 15584 | 15694 | 19037 | 19131 | 19811 | 18187 | 16861 | 20240 | 20686 | 20629 | 21359 | 17963 | 17846 | 21371
3641 | 3641 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 17 | 15228 | 14805 | 18053 | 18271 | 17977 | 16938 | 15935 | 16253 | 19307 | 19409 | 20069 | 18460 | 17199 | 20528 | 21014 | 20883 | 21642 | 18309 | 18454 | 21673
3642 | 3642 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 18 | 15319 | 14810 | 17793 | 18160 | 18025 | 17231 | 16259 | 16578 | 19252 | 19550 | 20281 | 18977 | 17825 | 20724 | 21061 | 21178 | 22047 | 19037 | 19100 | 21933
3643 | 3643 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 19 | 15229 | 14974 | 17864 | 18152 | 18198 | 17277 | 16201 | 16889 | 19506 | 19835 | 20538 | 19382 | 18236 | 21208 | 21617 | 21867 | 22579 | 19595 | 19778 | 22517
3644 | 3644 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 20 | 15379 | 15088 | 17962 | 18310 | 18160 | 17546 | 16428 | 17078 | 19775 | 20069 | 20976 | 20083 | 18942 | 21738 | 22406 | 22549 | 23471 | 20501 | 20526 | 23132
3645 | 3645 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 21 | 15001 | 15114 | 17662 | 17883 | 17835 | 17360 | 16447 | 17319 | 19734 | 20099 | 21426 | 20422 | 19499 | 22054 | 22757 | 23080 | 24373 | 21339 | 21392 | 23640
3646 | 3646 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 22 | 14273 | 14574 | 16720 | 16976 | 17112 | 16718 | 15957 | 16940 | 18959 | 19610 | 20874 | 20104 | 19342 | 21478 | 22319 | 22896 | 24101 | 21354 | 21404 | 23175
3647 | 3647 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 23 | 13282 | 13676 | 15483 | 15800 | 16031 | 15695 | 15159 | 16053 | 17772 | 18613 | 19763 | 19216 | 18656 | 20342 | 21316 | 21987 | 23089 | 20750 | 20660 | 22085
3648 | 3648 | 152 | 6 | 1 | Summer | 5 | 31 | Spring | 24 | 12422 | 12973 | 14416 | 14900 | 15105 | 14775 | 14513 | 15343 | 16667 | 17698 | 18761 | 18357 | 18084 | 19258 | 20451 | 21113 | 22122 | 20224 | 20028 | 21016
3649 | 3649 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 1 | 11807 | 12305 | 13481 | 14044 | 14401 | 13994 | 13999 | 14546 | 15922 | 16993 | 17803 | 17352 | 16977 | 18766 | 19779 | 20460 | 21173 | 18798 | 19113 | 20697
3650 | 3650 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 2 | 11482 | 12108 | 13205 | 13773 | 14075 | 13581 | 13635 | 14260 | 15552 | 16561 | 17298 | 16823 | 16517 | 18297 | 19328 | 19915 | 20540 | 18280 | 18663 | 20168
3651 | 3651 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 3 | 11316 | 12034 | 13065 | 13594 | 13877 | 13378 | 13481 | 14120 | 15303 | 16271 | 16955 | 16475 | 16228 | 17928 | 18906 | 19480 | 20048 | 17933 | 18340 | 19732
3652 | 3652 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 4 | 11275 | 12144 | 13118 | 13613 | 13848 | 13219 | 13288 | 14091 | 15151 | 15990 | 16558 | 15973 | 15747 | 17479 | 18364 | 18844 | 19327 | 17277 | 17887 | 19114
3653 | 3653 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 5 | 11253 | 12461 | 13372 | 13766 | 13990 | 13024 | 13064 | 14189 | 15198 | 15836 | 16365 | 15397 | 15187 | 17141 | 17878 | 18277 | 18767 | 16508 | 17482 | 18575
3654 | 3654 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 6 | 11524 | 13500 | 14252 | 14580 | 14733 | 13170 | 13022 | 15018 | 15853 | 16246 | 16722 | 15127 | 14740 | 17443 | 18044 | 18239 | 18689 | 15871 | 17755 | 18684
3655 | 3655 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 7 | 12009 | 14821 | 15532 | 15690 | 15829 | 13575 | 13210 | 16220 | 16813 | 17072 | 17457 | 15114 | 14598 | 18132 | 18610 | 18754 | 19083 | 15598 | 18512 | 19233
3656 | 3656 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 8 | 12885 | 15603 | 16141 | 16340 | 16576 | 14369 | 13746 | 17002 | 17233 | 17783 | 18025 | 15705 | 14984 | 18365 | 18984 | 19333 | 19563 | 15944 | 19166 | 19407
3657 | 3657 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 9 | 13563 | 16100 | 16416 | 16617 | 17006 | 15001 | 14329 | 17496 | 17429 | 18266 | 18340 | 16239 | 15421 | 18467 | 19108 | 19743 | 19857 | 16355 | 19588 | 19478
3658 | 3658 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 10 | 13922 | 16577 | 16852 | 16914 | 17339 | 15408 | 14814 | 18070 | 17966 | 18677 | 18780 | 16751 | 15987 | 19086 | 19591 | 20246 | 20392 | 16971 | 20284 | 20152
3659 | 3659 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 11 | 13878 | 16722 | 16929 | 16978 | 17457 | 15379 | 14950 | 18306 | 18143 | 18884 | 18973 | 16825 | 16204 | 19357 | 19841 | 20556 | 20681 | 17230 | 20643 | 20475
3660 | 3660 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 12 | 13717 | 16726 | 16916 | 17007 | 17506 | 15259 | 14965 | 18344 | 18179 | 18985 | 19056 | 16758 | 16262 | 19422 | 20022 | 20718 | 20802 | 17299 | 20736 | 20563
3661 | 3661 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 13 | 13422 | 16710 | 16901 | 16940 | 17542 | 14968 | 14809 | 18335 | 18179 | 19056 | 19071 | 16479 | 16111 | 19424 | 19975 | 20799 | 20829 | 17143 | 20734 | 20573
3662 | 3662 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 14 | 13260 | 16778 | 16962 | 16929 | 17558 | 14787 | 14823 | 18384 | 18227 | 19057 | 19054 | 16276 | 16106 | 19448 | 19940 | 20760 | 20775 | 17121 | 20750 | 20590
3663 | 3663 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 15 | 13205 | 16839 | 17039 | 17009 | 17626 | 14720 | 14791 | 18412 | 18288 | 19091 | 19015 | 16188 | 16057 | 19491 | 19985 | 20754 | 20704 | 17058 | 20745 | 20621
3664 | 3664 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 16 | 13391 | 17038 | 17399 | 17215 | 17839 | 14903 | 15134 | 18584 | 18806 | 19214 | 19091 | 16290 | 16333 | 20047 | 20050 | 20763 | 20685 | 17311 | 20835 | 21149
3665 | 3665 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 17 | 13738 | 17247 | 17724 | 17526 | 18109 | 15290 | 15715 | 18866 | 19066 | 19497 | 19345 | 16654 | 16956 | 20400 | 20331 | 21067 | 20973 | 17946 | 21171 | 21514
3666 | 3666 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 18 | 13936 | 17034 | 17702 | 17669 | 18104 | 15699 | 16086 | 18854 | 19114 | 19767 | 19623 | 17337 | 17600 | 20531 | 20711 | 21560 | 21483 | 18680 | 21523 | 21720
3667 | 3667 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 19 | 13826 | 17154 | 17730 | 17844 | 18140 | 15678 | 16431 | 19095 | 19375 | 20015 | 19999 | 17713 | 18188 | 21109 | 21425 | 22099 | 22167 | 19425 | 22177 | 22444
3668 | 3668 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 20 | 13860 | 17261 | 17901 | 17784 | 18325 | 15915 | 16642 | 19330 | 19744 | 20394 | 20354 | 18355 | 18807 | 21889 | 22098 | 22980 | 22831 | 20225 | 22840 | 23368
3669 | 3669 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 21 | 13709 | 16986 | 17481 | 17451 | 18361 | 15912 | 16865 | 19258 | 19632 | 20777 | 20656 | 18854 | 19462 | 22215 | 22606 | 23870 | 23598 | 21119 | 23378 | 23917
3670 | 3670 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 22 | 13109 | 16037 | 16553 | 16686 | 17512 | 15381 | 16434 | 18426 | 18910 | 20163 | 20247 | 18625 | 19290 | 21735 | 22373 | 23551 | 23471 | 21095 | 22902 | 23588
3671 | 3671 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 23 | 12284 | 14770 | 15373 | 15608 | 16298 | 14571 | 15536 | 17221 | 17776 | 19030 | 19251 | 17912 | 18474 | 20714 | 21454 | 22529 | 22562 | 20349 | 21820 | 22637
3672 | 3672 | 153 | 6 | 2 | Summer | 6 | 1 | Summer | 24 | 11624 | 13762 | 14467 | 14692 | 15266 | 13918 | 14820 | 16101 | 16876 | 18007 | 18394 | 17321 | 17808 | 19834 | 20568 | 21558 | 21782 | 19716 | 20746 | 21779
3673 | 3673 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 1 | 11403 | 12784 | 13601 | 13939 | 14278 | 13442 | 14008 | 15268 | 16070 | 17007 | 17094 | 16269 | 16918 | 19116 | 19863 | 20578 | 20265 | 18776 | 20394 | 21132
3674 | 3674 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 2 | 11119 | 12501 | 13324 | 13596 | 13876 | 13063 | 13706 | 14890 | 15717 | 16498 | 16576 | 15801 | 16502 | 18653 | 19310 | 19925 | 19636 | 18297 | 19840 | 20615
3675 | 3675 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 3 | 11001 | 12356 | 13154 | 13414 | 13681 | 12915 | 13577 | 14665 | 15456 | 16179 | 16153 | 15538 | 16256 | 18246 | 18885 | 19453 | 19083 | 17979 | 19396 | 20131
3676 | 3676 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 4 | 10905 | 12383 | 13159 | 13373 | 13579 | 12725 | 13556 | 14530 | 15238 | 15824 | 15686 | 15070 | 15949 | 17721 | 18261 | 18731 | 18313 | 17511 | 18759 | 19429
3677 | 3677 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 5 | 10859 | 12708 | 13382 | 13587 | 13836 | 12596 | 13759 | 14683 | 15181 | 15771 | 15182 | 14610 | 15795 | 17345 | 17797 | 18252 | 17408 | 17180 | 18288 | 18839
3678 | 3678 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 6 | 10986 | 13589 | 14178 | 14350 | 14582 | 12567 | 14625 | 15389 | 15716 | 16201 | 14981 | 14215 | 16240 | 17546 | 17786 | 18195 | 16833 | 17444 | 18383 | 18828
3679 | 3679 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 7 | 11268 | 14784 | 15178 | 15382 | 15499 | 12668 | 15765 | 16323 | 16557 | 16901 | 14951 | 14034 | 17018 | 18048 | 18226 | 18508 | 16555 | 18088 | 18824 | 19165
3680 | 3680 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 8 | 11638 | 15183 | 15569 | 15869 | 15976 | 13000 | 16288 | 16528 | 16954 | 17237 | 15466 | 14247 | 17505 | 18183 | 18553 | 18737 | 16949 | 18473 | 18733 | 19238
3681 | 3681 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 9 | 12096 | 15298 | 15718 | 16165 | 16193 | 13442 | 16659 | 16613 | 17030 | 17430 | 15895 | 14568 | 17827 | 18179 | 18825 | 18907 | 17305 | 18763 | 18655 | 19200
3682 | 3682 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 10 | 12421 | 15615 | 15901 | 16379 | 16432 | 13803 | 17106 | 17036 | 17318 | 17750 | 16364 | 15016 | 18361 | 18545 | 19212 | 19328 | 17860 | 19341 | 19223 | 19622
3683 | 3683 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 11 | 12603 | 15782 | 16056 | 16578 | 16604 | 14021 | 17419 | 17299 | 17552 | 18018 | 16713 | 15318 | 18751 | 18879 | 19607 | 19703 | 18289 | 19787 | 19641 | 20011
3684 | 3684 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 12 | 12657 | 15849 | 16182 | 16711 | 16647 | 14122 | 17543 | 17419 | 17677 | 18182 | 16780 | 15463 | 18843 | 19141 | 19855 | 19910 | 18363 | 19970 | 19819 | 20309
3685 | 3685 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 13 | 12665 | 16003 | 16278 | 16910 | 16805 | 14130 | 17701 | 17578 | 17797 | 18366 | 16735 | 15477 | 19012 | 19257 | 20099 | 20099 | 18329 | 20135 | 19989 | 20433
3686 | 3686 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 14 | 12684 | 16086 | 16286 | 16947 | 16832 | 14165 | 17778 | 17653 | 17801 | 18379 | 16733 | 15497 | 19065 | 19247 | 20086 | 20075 | 18305 | 20168 | 20031 | 20416
3687 | 3687 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 15 | 12707 | 16219 | 16434 | 17080 | 16902 | 14198 | 17871 | 17770 | 17931 | 18404 | 16797 | 15514 | 19143 | 19357 | 20146 | 20067 | 18353 | 20226 | 20121 | 20518
3688 | 3688 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 16 | 13228 | 16698 | 16808 | 17469 | 17233 | 14707 | 18203 | 18424 | 18234 | 18660 | 17095 | 15968 | 19410 | 19598 | 20331 | 20224 | 18579 | 20467 | 20817 | 20727
3689 | 3689 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 17 | 13794 | 16998 | 17118 | 17735 | 17416 | 15285 | 18478 | 18677 | 18535 | 18908 | 17453 | 16585 | 19727 | 19874 | 20635 | 20505 | 19014 | 20799 | 21176 | 21018
3690 | 3690 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 18 | 13814 | 16916 | 17215 | 17652 | 17450 | 15592 | 18369 | 18663 | 18708 | 19097 | 17935 | 17148 | 19950 | 20186 | 21058 | 20959 | 19630 | 21104 | 21334 | 21419
3691 | 3691 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 19 | 14027 | 16964 | 17375 | 17682 | 17533 | 15931 | 18595 | 18896 | 19010 | 19408 | 18348 | 17708 | 20475 | 20863 | 21572 | 21632 | 20342 | 21772 | 22065 | 22249
3692 | 3692 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 20 | 14194 | 17108 | 17306 | 17875 | 17578 | 16156 | 18831 | 19241 | 19232 | 19686 | 18752 | 18304 | 21028 | 21502 | 22431 | 22304 | 21119 | 22475 | 23011 | 23050
3693 | 3693 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 21 | 14241 | 16663 | 16942 | 17874 | 17423 | 16332 | 18703 | 19052 | 19213 | 19884 | 19162 | 18885 | 21330 | 21947 | 23262 | 23023 | 21961 | 22999 | 23548 | 23734
3694 | 3694 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 22 | 13653 | 15705 | 16156 | 16997 | 16710 | 15865 | 17834 | 18270 | 18648 | 19414 | 18975 | 18658 | 20699 | 21663 | 22902 | 22858 | 22031 | 22509 | 23203 | 23624
3695 | 3695 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 23 | 12760 | 14528 | 15078 | 15797 | 15613 | 14960 | 16613 | 17119 | 17632 | 18394 | 18183 | 17828 | 19547 | 20723 | 21873 | 21946 | 21350 | 21407 | 22249 | 22753
3696 | 3696 | 154 | 6 | 3 | Summer | 6 | 2 | Summer | 24 | 12070 | 13701 | 14229 | 14843 | 14810 | 14249 | 15555 | 16279 | 16790 | 17591 | 17493 | 17152 | 18526 | 19899 | 20955 | 21228 | 20702 | 20394 | 21468 | 21950
3697 | 3697 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 1 | 11635 | 13099 | 13759 | 14121 | 13982 | 13697 | 14942 | 15688 | 16310 | 16591 | 16165 | 16518 | 18221 | 19460 | 20231 | 19994 | 18906 | 20300 | 21054 | 21509
3698 | 3698 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 2 | 11423 | 12819 | 13436 | 13724 | 13579 | 13408 | 14574 | 15344 | 15872 | 16093 | 15705 | 16117 | 17739 | 18920 | 19594 | 19371 | 18345 | 19750 | 20536 | 20901
3699 | 3699 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 3 | 11337 | 12676 | 13257 | 13527 | 13288 | 13282 | 14362 | 15094 | 15595 | 15693 | 15414 | 15874 | 17380 | 18505 | 19127 | 18818 | 17940 | 19308 | 20054 | 20413
3700 | 3700 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 4 | 11436 | 12700 | 13250 | 13466 | 13149 | 13307 | 14289 | 14946 | 15368 | 15303 | 15033 | 15630 | 16967 | 17946 | 18462 | 18093 | 17308 | 18704 | 19375 | 19673
3701 | 3701 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 5 | 11810 | 12957 | 13479 | 13759 | 12978 | 13544 | 14494 | 14962 | 15339 | 14865 | 14561 | 15540 | 16735 | 17532 | 18025 | 17234 | 16577 | 18248 | 18790 | 19054
3702 | 3702 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 6 | 12849 | 13753 | 14280 | 14549 | 13136 | 14461 | 15267 | 15570 | 15810 | 14751 | 14281 | 16067 | 17074 | 17583 | 18024 | 16700 | 16027 | 18368 | 18794 | 18907
3703 | 3703 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 7 | 14021 | 14728 | 15306 | 15453 | 13419 | 15576 | 16222 | 16421 | 16548 | 14755 | 14008 | 16849 | 17663 | 18022 | 18337 | 16402 | 15490 | 18779 | 19099 | 19219
3704 | 3704 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 8 | 14370 | 14972 | 15645 | 15704 | 13931 | 15909 | 16292 | 16613 | 16866 | 15148 | 14234 | 17113 | 17506 | 18204 | 18415 | 16639 | 15601 | 18523 | 19007 | 19367
3705 | 3705 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 9 | 14631 | 15043 | 15881 | 15846 | 14347 | 16191 | 16313 | 16639 | 17122 | 15522 | 14537 | 17369 | 17397 | 18391 | 18506 | 16921 | 15851 | 18366 | 18894 | 19560
3706 | 3706 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 10 | 14933 | 15168 | 16039 | 16015 | 14649 | 16564 | 16662 | 16850 | 17358 | 15923 | 14983 | 17835 | 17848 | 18709 | 18860 | 17411 | 16377 | 18870 | 19249 | 19931
3707 | 3707 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 11 | 15115 | 15259 | 16195 | 16145 | 14846 | 16824 | 16867 | 17037 | 17597 | 16217 | 15311 | 18188 | 18159 | 19054 | 19185 | 17803 | 16774 | 19239 | 19590 | 20336
3708 | 3708 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 12 | 15157 | 15274 | 16256 | 16193 | 14809 | 16881 | 16918 | 17167 | 17720 | 16215 | 15529 | 18288 | 18256 | 19232 | 19324 | 17819 | 17014 | 19352 | 19822 | 20549
3709 | 3709 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 13 | 15278 | 15363 | 16428 | 16320 | 14726 | 17014 | 17053 | 17257 | 17921 | 16148 | 15601 | 18430 | 18392 | 19451 | 19490 | 17755 | 17084 | 19501 | 19927 | 20790
3710 | 3710 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 14 | 15326 | 15341 | 16430 | 16308 | 14696 | 17058 | 17098 | 17218 | 17902 | 16114 | 15687 | 18448 | 18400 | 19408 | 19433 | 17692 | 17143 | 19505 | 19868 | 20733
3711 | 3711 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 15 | 15362 | 15393 | 16467 | 16278 | 14676 | 17054 | 17118 | 17248 | 17898 | 16082 | 15827 | 18423 | 18404 | 19372 | 19331 | 17638 | 17273 | 19495 | 19866 | 20680
3712 | 3712 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 16 | 15613 | 15627 | 16746 | 16497 | 14939 | 17268 | 17610 | 17436 | 18100 | 16269 | 16152 | 18583 | 19015 | 19452 | 19373 | 17750 | 17563 | 20057 | 19945 | 20698
3713 | 3713 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 17 | 15932 | 16033 | 17122 | 16792 | 15448 | 17656 | 17976 | 17850 | 18489 | 16735 | 16871 | 19007 | 19477 | 19866 | 19768 | 18298 | 18262 | 20533 | 20351 | 21125
3714 | 3714 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 18 | 15979 | 16478 | 17311 | 17135 | 16025 | 17866 | 18291 | 18350 | 19022 | 17525 | 17818 | 19521 | 19890 | 20623 | 20552 | 19247 | 19346 | 21038 | 21095 | 21969
3715 | 3715 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 19 | 16310 | 16833 | 17535 | 17413 | 16317 | 18297 | 18710 | 18822 | 19438 | 18079 | 18406 | 20215 | 20641 | 21313 | 21406 | 20150 | 20222 | 21986 | 22144 | 22794
3716 | 3716 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 20 | 16477 | 16783 | 17740 | 17471 | 16451 | 18578 | 19066 | 19028 | 19804 | 18432 | 18638 | 20766 | 21429 | 22163 | 22078 | 20932 | 20736 | 22985 | 22997 | 23792
3717 | 3717 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 21 | 16192 | 16407 | 17715 | 17277 | 16424 | 18422 | 18821 | 18934 | 20098 | 18756 | 18768 | 21005 | 21684 | 22934 | 22758 | 21752 | 21202 | 23515 | 23681 | 24795
3718 | 3718 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 22 | 15219 | 15619 | 16809 | 16538 | 15959 | 17517 | 17994 | 18325 | 19419 | 18511 | 18525 | 20317 | 21143 | 22527 | 22547 | 21789 | 21167 | 23146 | 23557 | 24539
3719 | 3719 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 23 | 13974 | 14553 | 15620 | 15463 | 15107 | 16302 | 16832 | 17295 | 18293 | 17714 | 17759 | 19164 | 20123 | 21486 | 21632 | 21111 | 20477 | 22189 | 22696 | 23562
3720 | 3720 | 155 | 6 | 4 | Summer | 6 | 3 | Summer | 24 | 13086 | 13740 | 14658 | 14658 | 14379 | 15253 | 15977 | 16419 | 17333 | 17007 | 17115 | 18134 | 19315 | 20566 | 20899 | 20451 | 19879 | 21404 | 21890 | 22668
3721 | 3721 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 1 | 12460 | 13365 | 14005 | 13917 | 13631 | 14665 | 15427 | 15986 | 16650 | 15815 | 16449 | 17852 | 18902 | 19899 | 19760 | 18762 | 19180 | 21066 | 21541 | 22020
3722 | 3722 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 2 | 12183 | 13049 | 13626 | 13519 | 13252 | 14306 | 15094 | 15562 | 16158 | 15369 | 16032 | 17382 | 18449 | 19278 | 19147 | 18207 | 18672 | 20550 | 20939 | 21320
3723 | 3723 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 3 | 12064 | 12900 | 13458 | 13252 | 13086 | 14124 | 14873 | 15322 | 15881 | 15118 | 15827 | 17062 | 18077 | 18847 | 18626 | 17831 | 18361 | 20085 | 20465 | 20806
3724 | 3724 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 4 | 12117 | 12918 | 13429 | 13148 | 12968 | 14101 | 14789 | 15165 | 15619 | 14798 | 15570 | 16717 | 17627 | 18245 | 17956 | 17236 | 17854 | 19439 | 19749 | 20024
3725 | 3725 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 5 | 12419 | 13140 | 13730 | 12993 | 12784 | 14341 | 14853 | 15195 | 15624 | 14371 | 15440 | 16540 | 17292 | 17854 | 17127 | 16524 | 17440 | 18865 | 19127 | 19420
3726 | 3726 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 6 | 13305 | 13973 | 14550 | 13188 | 12829 | 15161 | 15525 | 15758 | 16141 | 14156 | 15907 | 16953 | 17558 | 17908 | 16637 | 16005 | 17624 | 18889 | 18985 | 19272
3727 | 3727 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 7 | 14460 | 15013 | 15484 | 13500 | 12779 | 16153 | 16418 | 16571 | 16853 | 13946 | 16635 | 17602 | 18060 | 18258 | 16365 | 15479 | 18164 | 19198 | 19286 | 19487
3728 | 3728 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 8 | 14808 | 15436 | 15841 | 14099 | 13168 | 16328 | 16722 | 17004 | 17136 | 14300 | 17243 | 17565 | 18142 | 18445 | 16708 | 15672 | 18693 | 19202 | 19521 | 19627
3729 | 3729 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 9 | 15001 | 15792 | 16152 | 14678 | 13724 | 16509 | 16902 | 17436 | 17414 | 14786 | 17640 | 17639 | 18228 | 18692 | 17153 | 16088 | 19022 | 19235 | 19855 | 19874
3730 | 3730 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 10 | 14995 | 15715 | 16080 | 14736 | 13819 | 16598 | 16865 | 17426 | 17414 | 14985 | 17828 | 17835 | 18284 | 18796 | 17398 | 16365 | 19269 | 19349 | 19987 | 20031
3731 | 3731 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 11 | 15012 | 15753 | 16106 | 14831 | 13961 | 16681 | 16942 | 17560 | 17529 | 15203 | 18030 | 18033 | 18474 | 19004 | 17679 | 16657 | 19542 | 19583 | 20282 | 20293
3732 | 3732 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 12 | 15207 | 16000 | 16347 | 14981 | 14336 | 16919 | 17258 | 17860 | 17822 | 15606 | 18304 | 18321 | 18869 | 19341 | 17898 | 17093 | 19851 | 20015 | 20696 | 20660
3733 | 3733 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 13 | 15361 | 16189 | 16488 | 14919 | 14405 | 17069 | 17357 | 18078 | 17993 | 15694 | 18526 | 18477 | 18978 | 19524 | 17848 | 17189 | 20073 | 20128 | 20951 | 20864
3734 | 3734 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 14 | 15407 | 16208 | 16494 | 14913 | 14509 | 17128 | 17345 | 18088 | 17981 | 15796 | 18601 | 18516 | 18947 | 19488 | 17805 | 17270 | 20122 | 20083 | 20910 | 20817
3735 | 3735 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 15 | 15474 | 16267 | 16499 | 14926 | 14680 | 17182 | 17402 | 18122 | 17940 | 15972 | 18759 | 18556 | 18980 | 19418 | 17780 | 17433 | 20260 | 20110 | 20885 | 20731
3736 | 3736 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 16 | 15831 | 16574 | 16762 | 15213 | 15089 | 17703 | 17634 | 18361 | 18119 | 16338 | 19061 | 19161 | 19141 | 19506 | 17933 | 17737 | 20508 | 20226 | 20943 | 20770
3737 | 3737 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 17 | 16269 | 16974 | 17067 | 15736 | 15794 | 18087 | 18068 | 18764 | 18494 | 17070 | 19610 | 19635 | 19545 | 19914 | 18497 | 18450 | 21085 | 20644 | 21379 | 21186
3738 | 3738 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 18 | 16395 | 17005 | 17208 | 16146 | 16395 | 18262 | 18420 | 19101 | 18861 | 17846 | 20199 | 19896 | 20046 | 20557 | 19298 | 19402 | 21808 | 21254 | 22089 | 21906
3739 | 3739 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 19 | 16597 | 17149 | 17378 | 16345 | 16758 | 18583 | 18776 | 19391 | 19265 | 18296 | 20572 | 20529 | 20832 | 21288 | 20097 | 20191 | 22377 | 22229 | 22845 | 22801
3740 | 3740 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 20 | 16737 | 17274 | 17364 | 16418 | 16693 | 18881 | 18902 | 19658 | 19487 | 18420 | 20659 | 21217 | 21428 | 21869 | 20804 | 20653 | 22803 | 23045 | 23811 | 23535
3741 | 3741 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 21 | 16264 | 17201 | 17114 | 16334 | 16453 | 18561 | 18710 | 19847 | 19572 | 18450 | 20699 | 21372 | 21770 | 22441 | 21535 | 21070 | 23178 | 23681 | 24780 | 24351
3742 | 3742 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 22 | 15314 | 16339 | 16386 | 15876 | 16013 | 17725 | 18076 | 19133 | 19064 | 18190 | 20077 | 20810 | 21457 | 22222 | 21565 | 21041 | 22753 | 23561 | 24545 | 24291
3743 | 3743 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 23 | 14133 | 15147 | 15297 | 15003 | 15159 | 16534 | 17012 | 17953 | 18027 | 17398 | 18928 | 19736 | 20498 | 21274 | 20857 | 20313 | 21662 | 22672 | 23551 | 23400
3744 | 3744 | 156 | 6 | 5 | Summer | 6 | 4 | Summer | 24 | 13301 | 14219 | 14493 | 14273 | 14466 | 15672 | 16128 | 16976 | 17199 | 16736 | 17930 | 18903 | 19650 | 20530 | 20182 | 19703 | 20670 | 21866 | 22661 | 22678
3745 | 3745 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 1 | 12641 | 13449 | 13635 | 13401 | 13727 | 14961 | 15518 | 16112 | 16122 | 15947 | 17385 | 18303 | 19101 | 19247 | 18385 | 18847 | 20460 | 21330 | 21854 | 21290
3746 | 3746 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 2 | 12387 | 13107 | 13278 | 13048 | 13437 | 14657 | 15125 | 15658 | 15659 | 15565 | 16924 | 17885 | 18593 | 18670 | 17859 | 18369 | 19884 | 20742 | 21178 | 20647
3747 | 3747 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 3 | 12259 | 12916 | 13011 | 12869 | 13322 | 14436 | 14890 | 15382 | 15285 | 15365 | 16597 | 17520 | 18202 | 18156 | 17480 | 18049 | 19436 | 20259 | 20648 | 20052
3748 | 3748 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 4 | 12301 | 12903 | 12927 | 12770 | 13313 | 14391 | 14780 | 15184 | 14971 | 15157 | 16236 | 17135 | 17711 | 17528 | 16916 | 17571 | 18791 | 19564 | 19877 | 19248
3749 | 3749 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 5 | 12560 | 13210 | 12798 | 12613 | 13484 | 14509 | 14870 | 15266 | 14598 | 15086 | 16087 | 16875 | 17354 | 16756 | 16243 | 17191 | 18315 | 18962 | 19286 | 18272
3750 | 3750 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 6 | 13351 | 14074 | 13029 | 12688 | 14303 | 15234 | 15504 | 15875 | 14561 | 15620 | 16590 | 17217 | 17475 | 16321 | 15762 | 17402 | 18450 | 18837 | 19147 | 17638
3751 | 3751 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 7 | 14328 | 15024 | 13381 | 12676 | 15322 | 16169 | 16379 | 16675 | 14637 | 16411 | 17217 | 17784 | 17967 | 16094 | 15267 | 17964 | 18742 | 19149 | 19364 | 17280
3752 | 3752 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 8 | 14596 | 15292 | 13937 | 13004 | 15871 | 16404 | 16753 | 16923 | 15077 | 16976 | 17463 | 17829 | 18181 | 16379 | 15396 | 18422 | 18855 | 19300 | 19417 | 17539
3753 | 3753 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 9 | 14643 | 15443 | 14376 | 13400 | 16081 | 16421 | 17041 | 17048 | 15458 | 17232 | 17578 | 17763 | 18373 | 16672 | 15657 | 18585 | 18921 | 19480 | 19492 | 17812
3754 | 3754 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 10 | 14782 | 15627 | 14687 | 13752 | 16421 | 16622 | 17271 | 17307 | 15863 | 17669 | 17962 | 18070 | 18696 | 17162 | 16183 | 19090 | 19370 | 19860 | 19907 | 18362
3755 | 3755 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 11 | 14849 | 15729 | 14865 | 13969 | 16614 | 16770 | 17474 | 17496 | 16127 | 17948 | 18299 | 18328 | 19006 | 17520 | 16556 | 19439 | 19775 | 20238 | 20261 | 18776
3756 | 3756 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 12 | 14843 | 15803 | 14845 | 14166 | 16679 | 16903 | 17599 | 17601 | 16140 | 18050 | 18545 | 18541 | 19214 | 17570 | 16823 | 19577 | 20080 | 20482 | 20458 | 18842
3757 | 3757 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 13 | 14911 | 15919 | 14742 | 14197 | 16853 | 16960 | 17772 | 17727 | 16049 | 18231 | 18753 | 18610 | 19416 | 17480 | 16879 | 19766 | 20298 | 20693 | 20616 | 18758
3758 | 3758 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 14 | 14988 | 15996 | 14814 | 14379 | 17025 | 17025 | 17864 | 17802 | 16115 | 18387 | 18909 | 18663 | 19471 | 17519 | 17040 | 19895 | 20433 | 20726 | 20648 | 18782
3759 | 3759 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 15 | 15210 | 16155 | 14957 | 14689 | 17333 | 17216 | 18036 | 17903 | 16248 | 18680 | 19125 | 18841 | 19604 | 17631 | 17337 | 20171 | 20620 | 20834 | 20692 | 18885
3760 | 3760 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 16 | 15515 | 16471 | 15284 | 15144 | 17727 | 17499 | 18327 | 18147 | 16508 | 19034 | 19780 | 19053 | 19753 | 17834 | 17687 | 20462 | 21241 | 20929 | 20781 | 19058
3761 | 3761 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 17 | 15904 | 16734 | 15762 | 15813 | 18220 | 17900 | 18690 | 18482 | 16955 | 19541 | 20212 | 19419 | 20145 | 18366 | 18363 | 20998 | 21680 | 21330 | 21162 | 19595
3762 | 3762 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 18 | 16148 | 16741 | 16016 | 16296 | 18465 | 18153 | 18889 | 18703 | 17493 | 20003 | 20399 | 19823 | 20658 | 19066 | 19219 | 21635 | 22056 | 21947 | 21794 | 20366
3763 | 3763 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 19 | 16387 | 16848 | 16156 | 16600 | 18615 | 18460 | 19107 | 19008 | 17891 | 20294 | 20866 | 20518 | 21202 | 19792 | 19958 | 22153 | 22832 | 22678 | 22658 | 21232
3764 | 3764 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 20 | 16267 | 16788 | 16180 | 16491 | 18516 | 18538 | 19319 | 19136 | 18123 | 20284 | 21103 | 21016 | 21948 | 20433 | 20375 | 22538 | 23368 | 23638 | 23377 | 22016
3765 | 3765 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 21 | 15847 | 16516 | 16054 | 16215 | 18224 | 18289 | 19435 | 19130 | 18334 | 20245 | 21218 | 21263 | 22611 | 21087 | 20734 | 22875 | 23904 | 24598 | 24189 | 22899
3766 | 3766 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 22 | 15088 | 15770 | 15583 | 15764 | 17406 | 17607 | 18686 | 18570 | 18076 | 19584 | 20593 | 20890 | 22197 | 21077 | 20679 | 22434 | 23541 | 24352 | 24119 | 23039
3767 | 3767 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 23 | 14008 | 14676 | 14711 | 14922 | 16190 | 16531 | 17488 | 17514 | 17243 | 18430 | 19431 | 19906 | 21123 | 20358 | 19944 | 21345 | 22466 | 23349 | 23230 | 22384
3768 | 3768 | 157 | 6 | 6 | Summer | 6 | 5 | Summer | 24 | 13238 | 13891 | 13981 | 14246 | 15170 | 15650 | 16490 | 16681 | 16521 | 17419 | 18488 | 19063 | 20181 | 19675 | 19321 | 20358 | 21588 | 22448 | 22506 | 21725
3769 | 3769 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 1 | 12640 | 12989 | 13087 | 13439 | 14285 | 14982 | 15559 | 15570 | 15184 | 16760 | 17580 | 18418 | 19267 | 17848 | 18366 | 20027 | 20728 | 21555 | 21030 | 19649
3770 | 3770 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 2 | 12352 | 12632 | 12748 | 13153 | 13924 | 14602 | 15120 | 15122 | 14772 | 16318 | 17129 | 17926 | 18675 | 17334 | 17897 | 19458 | 20172 | 20883 | 20394 | 19075
3771 | 3771 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 3 | 12206 | 12402 | 12595 | 13062 | 13729 | 14397 | 14881 | 14784 | 14538 | 16031 | 16743 | 17571 | 18260 | 16987 | 17609 | 19032 | 19653 | 20379 | 19819 | 18666
3772 | 3772 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 4 | 12233 | 12322 | 12519 | 13072 | 13669 | 14333 | 14740 | 14531 | 14275 | 15736 | 16366 | 17149 | 17724 | 16468 | 17166 | 18420 | 18976 | 19624 | 19026 | 17995
3773 | 3773 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 5 | 12463 | 12217 | 12381 | 13263 | 13906 | 14468 | 14885 | 14223 | 13914 | 15656 | 16215 | 16865 | 17406 | 15840 | 16824 | 17978 | 18444 | 19053 | 18054 | 17193
3774 | 3774 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 6 | 13309 | 12463 | 12484 | 14109 | 14776 | 15142 | 15563 | 14269 | 13763 | 16230 | 16755 | 17071 | 17530 | 15401 | 17068 | 18144 | 18615 | 18929 | 17427 | 16593
3775 | 3775 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 7 | 14377 | 12856 | 12523 | 15164 | 15721 | 16058 | 16433 | 14425 | 13625 | 16938 | 17491 | 17645 | 17953 | 14958 | 17675 | 18474 | 19093 | 19169 | 17088 | 16051
3776 | 3776 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 8 | 14702 | 13438 | 12878 | 15708 | 16133 | 16431 | 16698 | 14897 | 13917 | 17230 | 17928 | 17887 | 18075 | 15096 | 18139 | 18602 | 19373 | 19237 | 17339 | 16181
3777 | 3777 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 9 | 14816 | 13855 | 13258 | 15888 | 16277 | 16665 | 16793 | 15267 | 14217 | 17325 | 18094 | 18044 | 18132 | 15327 | 18283 | 18631 | 19462 | 19272 | 17575 | 16403
3778 | 3778 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 10 | 14956 | 14154 | 13582 | 16191 | 16520 | 16859 | 17010 | 15637 | 14626 | 17677 | 18451 | 18339 | 18456 | 15818 | 18752 | 19061 | 19888 | 19660 | 18099 | 16953
3779 | 3779 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 11 | 15127 | 14337 | 13839 | 16417 | 16802 | 17089 | 17223 | 15931 | 14974 | 18043 | 18804 | 18687 | 18801 | 16227 | 19137 | 19511 | 20331 | 20054 | 18554 | 17408
3780 | 3780 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 12 | 15164 | 14305 | 14009 | 16458 | 16962 | 17189 | 17302 | 15923 | 15172 | 18268 | 19110 | 18858 | 18936 | 16464 | 19243 | 19783 | 20682 | 20221 | 18590 | 17662
3781 | 3781 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 13 | 15329 | 14222 | 14056 | 16648 | 17175 | 17371 | 17439 | 15845 | 15234 | 18493 | 19367 | 19068 | 19094 | 16536 | 19451 | 20011 | 20943 | 20389 | 18520 | 17742
3782 | 3782 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 14 | 15386 | 14229 | 14207 | 16784 | 17312 | 17435 | 17491 | 15879 | 15379 | 18626 | 19542 | 19101 | 19108 | 16670 | 19551 | 20117 | 21093 | 20389 | 18514 | 17866
3783 | 3783 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 15 | 15508 | 14318 | 14450 | 17030 | 17469 | 17545 | 17530 | 15947 | 15608 | 18778 | 19755 | 19174 | 19098 | 16907 | 19768 | 20240 | 21275 | 20369 | 18553 | 18102
3784 | 3784 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 16 | 15800 | 14568 | 14836 | 17369 | 17993 | 17785 | 17715 | 16164 | 15959 | 19363 | 20046 | 19297 | 19183 | 17198 | 19992 | 20824 | 21497 | 20390 | 18657 | 18373
3785 | 3785 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 17 | 16204 | 15080 | 15505 | 17876 | 18394 | 18161 | 18060 | 16617 | 16673 | 19802 | 20427 | 19704 | 19567 | 17891 | 20548 | 21287 | 21963 | 20790 | 19213 | 19078
3786 | 3786 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 18 | 16216 | 15391 | 16011 | 18174 | 18633 | 18429 | 18324 | 17180 | 17423 | 20056 | 20750 | 20252 | 20184 | 18824 | 21268 | 21732 | 22358 | 21506 | 20073 | 20063
3787 | 3787 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 19 | 16369 | 15533 | 16319 | 18341 | 18870 | 18666 | 18624 | 17560 | 17838 | 20487 | 21141 | 20769 | 20880 | 19560 | 21781 | 22502 | 23066 | 22394 | 20967 | 20897
3788 | 3788 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 20 | 16472 | 15536 | 16198 | 18237 | 18804 | 18867 | 18727 | 17741 | 17906 | 20644 | 21427 | 21448 | 21392 | 19953 | 22156 | 23027 | 23734 | 23136 | 21774 | 21380
3789 | 3789 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 21 | 16363 | 15378 | 15881 | 17901 | 18485 | 18922 | 18640 | 17851 | 17847 | 20658 | 21445 | 22001 | 21862 | 20254 | 22444 | 23504 | 24200 | 23912 | 22636 | 21856
3790 | 3790 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 22 | 15505 | 14895 | 15426 | 17069 | 17596 | 18129 | 18037 | 17539 | 17552 | 19987 | 20849 | 21522 | 21586 | 20171 | 21989 | 23105 | 23888 | 23830 | 22777 | 21898
3791 | 3791 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 23 | 14333 | 14041 | 14587 | 15873 | 16333 | 16928 | 16964 | 16688 | 16762 | 18817 | 19621 | 20426 | 20639 | 19423 | 20890 | 22034 | 22787 | 22949 | 22133 | 21209
3792 | 3792 | 158 | 6 | 7 | Summer | 6 | 6 | Summer | 24 | 13463 | 13312 | 13911 | 14859 | 15370 | 15938 | 16121 | 15952 | 16101 | 17859 | 18617 | 19481 | 19896 | 18794 | 19890 | 21147 | 21826 | 22222 | 21481 | 20605
3793 | 3793 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 1 | 12652 | 12476 | 13131 | 13980 | 14355 | 14980 | 15036 | 14711 | 15270 | 16894 | 17706 | 18560 | 18571 | 17873 | 19556 | 20288 | 20942 | 20786 | 19434 | 19661
3794 | 3794 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 2 | 12332 | 12180 | 12874 | 13637 | 14016 | 14566 | 14614 | 14323 | 14910 | 16475 | 17205 | 17998 | 18018 | 17427 | 19008 | 19750 | 20334 | 20159 | 18874 | 19159
3795 | 3795 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 3 | 12165 | 12022 | 12788 | 13452 | 13760 | 14346 | 14289 | 14107 | 14753 | 16113 | 16866 | 17614 | 17535 | 17152 | 18596 | 19241 | 19866 | 19584 | 18464 | 18822
3796 | 3796 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 4 | 12155 | 11934 | 12802 | 13406 | 13680 | 14235 | 14079 | 13882 | 14590 | 15790 | 16479 | 17133 | 16958 | 16739 | 18013 | 18587 | 19158 | 18803 | 17794 | 18260
3797 | 3797 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 5 | 12468 | 11819 | 13015 | 13674 | 13872 | 14432 | 13841 | 13581 | 14586 | 15718 | 16240 | 16896 | 16257 | 16446 | 17620 | 18097 | 18578 | 17862 | 17010 | 17799
3798 | 3798 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 6 | 13341 | 11905 | 13885 | 14573 | 14755 | 15149 | 13954 | 13498 | 15176 | 16331 | 16560 | 17106 | 15884 | 16726 | 17826 | 18302 | 18539 | 17249 | 16411 | 17933
3799 | 3799 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 7 | 14432 | 12106 | 15110 | 15686 | 15938 | 16187 | 14301 | 13555 | 16144 | 17273 | 17305 | 17732 | 15844 | 17490 | 18320 | 18942 | 18940 | 17046 | 15997 | 18618
3800 | 3800 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 8 | 14776 | 12604 | 15746 | 16202 | 16628 | 16530 | 14867 | 13959 | 16815 | 17822 | 17784 | 17965 | 16241 | 18040 | 18542 | 19319 | 19276 | 17367 | 16196 | 19172
3801 | 3801 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 9 | 15073 | 13192 | 16153 | 16551 | 17032 | 16832 | 15441 | 14482 | 17225 | 18216 | 18106 | 18247 | 16683 | 18386 | 18781 | 19618 | 19539 | 17792 | 16615 | 19507
3802 | 3802 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 10 | 15328 | 13584 | 16536 | 16869 | 17390 | 17110 | 15876 | 14966 | 17727 | 18643 | 18505 | 18637 | 17252 | 18924 | 19282 | 20124 | 20046 | 18391 | 17238 | 20097
3803 | 3803 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 11 | 15381 | 13740 | 16677 | 17043 | 17559 | 17225 | 16077 | 15207 | 17945 | 18904 | 18813 | 18869 | 17563 | 19215 | 19641 | 20462 | 20444 | 18758 | 17605 | 20432
3804 | 3804 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 12 | 15466 | 13935 | 16744 | 17234 | 17822 | 17326 | 16087 | 15438 | 18063 | 19226 | 19038 | 19034 | 17621 | 19356 | 19949 | 20848 | 20717 | 18832 | 17896 | 20596
3805 | 3805 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 13 | 15572 | 13985 | 16908 | 17422 | 18035 | 17435 | 15980 | 15474 | 18229 | 19458 | 19257 | 19170 | 17512 | 19542 | 20155 | 21083 | 20929 | 18735 | 17953 | 20788
3806 | 3806 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 14 | 15607 | 14106 | 17040 | 17560 | 18216 | 17480 | 16015 | 15621 | 18350 | 19632 | 19355 | 19188 | 17526 | 19642 | 20260 | 21235 | 20990 | 18729 | 18073 | 20877
3807 | 3807 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 15 | 15618 | 14243 | 17183 | 17622 | 18342 | 17419 | 15975 | 15756 | 18472 | 19746 | 19474 | 19093 | 17468 | 19753 | 20279 | 21319 | 21080 | 18654 | 18198 | 20984
3808 | 3808 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 16 | 15836 | 14617 | 17502 | 18084 | 18682 | 17583 | 16180 | 16082 | 18722 | 20025 | 19636 | 19156 | 17586 | 19954 | 20837 | 21511 | 21132 | 18733 | 18435 | 21165
3809 | 3809 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 17 | 16114 | 15267 | 18002 | 18482 | 19113 | 17930 | 16633 | 16780 | 19228 | 20406 | 20029 | 19533 | 18124 | 20507 | 21298 | 21970 | 21482 | 19287 | 19138 | 21730
3810 | 3810 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 18 | 16060 | 15627 | 18114 | 18608 | 19196 | 18048 | 17028 | 17360 | 19641 | 20583 | 20544 | 19984 | 18767 | 21098 | 21616 | 22248 | 22175 | 20029 | 20007 | 22366
3811 | 3811 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 19 | 16050 | 15755 | 18123 | 18686 | 19115 | 18191 | 17235 | 17597 | 19795 | 20765 | 20926 | 20483 | 19342 | 21454 | 22227 | 22791 | 22907 | 20795 | 20717 | 22822
3812 | 3812 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 20 | 15972 | 15590 | 17958 | 18561 | 19036 | 18243 | 17347 | 17591 | 19729 | 20923 | 21267 | 20898 | 19915 | 21759 | 22670 | 23400 | 23638 | 21574 | 21179 | 23212
3813 | 3813 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 21 | 15672 | 15249 | 17594 | 18205 | 18593 | 18099 | 17388 | 17469 | 19612 | 20841 | 21406 | 21277 | 20484 | 21990 | 23089 | 23821 | 24232 | 22422 | 21647 | 23613
3814 | 3814 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 22 | 14931 | 14801 | 16763 | 17312 | 17705 | 17472 | 17042 | 17151 | 18929 | 20203 | 20843 | 20960 | 20436 | 21517 | 22673 | 23492 | 23949 | 22558 | 21696 | 23253
3815 | 3815 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 23 | 13838 | 13954 | 15559 | 16038 | 16372 | 16381 | 16162 | 16321 | 17754 | 18948 | 19721 | 19964 | 19688 | 20396 | 21570 | 22358 | 22929 | 21886 | 20996 | 22179
3816 | 3816 | 159 | 6 | 8 | Summer | 6 | 7 | Summer | 24 | 13069 | 13287 | 14545 | 15081 | 15331 | 15545 | 15430 | 15644 | 16734 | 17942 | 18703 | 19201 | 18997 | 19403 | 20687 | 21392 | 21957 | 21236 | 20398 | 21192
3817 | 3817 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 1 | 12367 | 12659 | 13800 | 14187 | 14559 | 14651 | 14409 | 14933 | 16121 | 17169 | 17785 | 18057 | 17391 | 19145 | 19954 | 20645 | 21053 | 19339 | 19587 | 21105
3818 | 3818 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 2 | 12045 | 12421 | 13465 | 13849 | 14166 | 14234 | 14024 | 14580 | 15713 | 16682 | 17226 | 17517 | 16909 | 18602 | 19422 | 20041 | 20405 | 18775 | 19079 | 20503
3819 | 3819 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 3 | 11835 | 12334 | 13299 | 13606 | 13961 | 13932 | 13830 | 14444 | 15452 | 16378 | 16880 | 17064 | 16579 | 18218 | 18933 | 19591 | 19918 | 18377 | 18753 | 20050
3820 | 3820 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 4 | 11773 | 12393 | 13280 | 13565 | 13902 | 13776 | 13659 | 14340 | 15225 | 16073 | 16464 | 16564 | 16112 | 17691 | 18333 | 18931 | 19178 | 17737 | 18213 | 19350
3821 | 3821 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 5 | 11683 | 12633 | 13557 | 13780 | 14025 | 13580 | 13403 | 14385 | 15210 | 15910 | 16202 | 15929 | 15533 | 17342 | 17881 | 18384 | 18530 | 16964 | 17754 | 18803
3822 | 3822 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 6 | 11944 | 13544 | 14478 | 14707 | 14764 | 13748 | 13391 | 15057 | 15861 | 16334 | 16570 | 15650 | 15154 | 17610 | 18144 | 18393 | 18494 | 16392 | 17903 | 18879
3823 | 3823 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 7 | 12366 | 14689 | 15514 | 15817 | 15683 | 14008 | 13379 | 15992 | 16653 | 17037 | 17264 | 15577 | 14764 | 18031 | 18709 | 18719 | 18910 | 15866 | 18467 | 19159
3824 | 3824 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 8 | 12967 | 15258 | 15998 | 16435 | 16197 | 14507 | 13727 | 16606 | 16980 | 17485 | 17856 | 15923 | 14920 | 18205 | 19040 | 18979 | 19376 | 15989 | 18946 | 19286
3825 | 3825 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 9 | 13407 | 15444 | 16176 | 16648 | 16406 | 14873 | 14051 | 16854 | 17128 | 17618 | 18227 | 16196 | 15187 | 18256 | 19135 | 19058 | 19700 | 16198 | 19071 | 19308
3826 | 3826 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 10 | 13616 | 15658 | 16327 | 16806 | 16536 | 15125 | 14353 | 17152 | 17362 | 17836 | 18610 | 16556 | 15569 | 18578 | 19472 | 19362 | 20150 | 16650 | 19493 | 19683
3827 | 3827 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 11 | 13728 | 15841 | 16536 | 17007 | 16766 | 15346 | 14618 | 17401 | 17657 | 18165 | 19029 | 16889 | 15911 | 18959 | 19847 | 19789 | 20647 | 17050 | 19864 | 20113
3828 | 3828 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 12 | 13764 | 15929 | 16761 | 17289 | 16975 | 15386 | 14876 | 17534 | 17928 | 18414 | 19309 | 16976 | 16213 | 19296 | 20264 | 20091 | 20972 | 17374 | 20060 | 20473
3829 | 3829 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 13 | 13711 | 16144 | 16994 | 17552 | 17224 | 15321 | 14951 | 17753 | 18182 | 18680 | 19581 | 16924 | 16317 | 19549 | 20541 | 20358 | 21255 | 17472 | 20295 | 20730
3830 | 3830 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 14 | 13752 | 16327 | 17180 | 17789 | 17402 | 15409 | 15150 | 17929 | 18360 | 18841 | 19743 | 16993 | 16498 | 19707 | 20750 | 20475 | 21382 | 17643 | 20436 | 20877
3831 | 3831 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 15 | 13913 | 16623 | 17416 | 18086 | 17737 | 15542 | 15454 | 18225 | 18588 | 19139 | 19883 | 17111 | 16804 | 19904 | 21011 | 20730 | 21492 | 17936 | 20712 | 21057
3832 | 3832 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 16 | 14177 | 16962 | 17845 | 18476 | 18057 | 15788 | 15819 | 18524 | 19182 | 19353 | 19995 | 17280 | 17117 | 20499 | 21243 | 20828 | 21526 | 18204 | 20923 | 21624
3833 | 3833 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 17 | 14682 | 17451 | 18231 | 18909 | 18419 | 16234 | 16503 | 19028 | 19611 | 19726 | 20415 | 17815 | 17791 | 20951 | 21692 | 21177 | 21955 | 18898 | 21479 | 22076
3834 | 3834 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 18 | 14885 | 17557 | 18375 | 19017 | 18708 | 16635 | 17070 | 19412 | 19760 | 20227 | 20983 | 18440 | 18619 | 21273 | 21980 | 21890 | 22704 | 19796 | 22147 | 22470
3835 | 3835 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 19 | 14962 | 17645 | 18524 | 19005 | 18946 | 16912 | 17373 | 19616 | 20080 | 20628 | 21411 | 19055 | 19272 | 21937 | 22566 | 22690 | 23380 | 20602 | 22690 | 23271
3836 | 3836 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 20 | 14936 | 17480 | 18394 | 18901 | 18919 | 17029 | 17371 | 19509 | 20166 | 20894 | 21603 | 19570 | 19614 | 22356 | 23149 | 23403 | 24008 | 21091 | 23108 | 23832
3837 | 3837 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 21 | 14770 | 17101 | 18015 | 18424 | 18622 | 17025 | 17207 | 19336 | 20107 | 20939 | 21622 | 20058 | 19867 | 22723 | 23519 | 23959 | 24498 | 21563 | 23522 | 24424
3838 | 3838 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 22 | 14273 | 16243 | 17092 | 17502 | 17757 | 16628 | 16839 | 18613 | 19401 | 20307 | 21096 | 19946 | 19750 | 22253 | 23146 | 23636 | 24260 | 21593 | 23149 | 24106
3839 | 3839 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 23 | 13429 | 15042 | 15831 | 16190 | 16535 | 15752 | 16011 | 17434 | 18203 | 19176 | 19937 | 19185 | 18985 | 21158 | 22008 | 22615 | 23194 | 20892 | 22090 | 23080
3840 | 3840 | 160 | 6 | 9 | Summer | 6 | 8 | Summer | 24 | 12720 | 14051 | 14865 | 15166 | 15493 | 15017 | 15326 | 16406 | 17243 | 18145 | 18866 | 18482 | 18352 | 20261 | 21040 | 21648 | 22181 | 20289 | 21106 | 22207
3841 | 3841 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 1 | 12083 | 13310 | 13995 | 14409 | 14570 | 14085 | 14630 | 15769 | 16447 | 17225 | 18151 | 16995 | 17590 | 19524 | 20282 | 20752 | 21334 | 19484 | 21012 | 21538
3842 | 3842 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 2 | 11775 | 12983 | 13671 | 14003 | 14121 | 13709 | 14284 | 15355 | 16018 | 16683 | 17575 | 16511 | 17128 | 19002 | 19684 | 20105 | 20615 | 18975 | 20408 | 20962
3843 | 3843 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 3 | 11625 | 12821 | 13435 | 13810 | 13914 | 13521 | 14159 | 15116 | 15688 | 16362 | 17137 | 16201 | 16878 | 18529 | 19246 | 19636 | 20061 | 18650 | 19955 | 20421
3844 | 3844 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 4 | 11546 | 12817 | 13401 | 13763 | 13811 | 13374 | 14085 | 14927 | 15430 | 16008 | 16601 | 15771 | 16510 | 17964 | 18618 | 18917 | 19221 | 18115 | 19255 | 19682
3845 | 3845 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 5 | 11439 | 13099 | 13639 | 13928 | 13934 | 13165 | 14187 | 14987 | 15429 | 15837 | 16052 | 15261 | 16264 | 17575 | 18126 | 18319 | 18311 | 17683 | 18726 | 19081
3846 | 3846 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 6 | 11508 | 14025 | 14556 | 14691 | 14728 | 13171 | 14900 | 15691 | 16103 | 16284 | 15810 | 14936 | 16580 | 17877 | 18168 | 18306 | 17655 | 17828 | 18793 | 19171
3847 | 3847 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 7 | 11590 | 15069 | 15643 | 15618 | 15759 | 13151 | 15852 | 16529 | 16959 | 17025 | 15783 | 14578 | 17238 | 18461 | 18500 | 18723 | 17287 | 18365 | 19049 | 19588
3848 | 3848 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 8 | 12003 | 15503 | 16199 | 16071 | 16369 | 13424 | 16401 | 16838 | 17412 | 17581 | 16292 | 14694 | 17669 | 18746 | 18706 | 19133 | 17713 | 18764 | 19101 | 19813
3849 | 3849 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 9 | 12469 | 15790 | 16531 | 16352 | 16819 | 13842 | 16761 | 17086 | 17696 | 18076 | 17016 | 15040 | 17908 | 18958 | 18897 | 19536 | 18412 | 18992 | 19228 | 19985
3850 | 3850 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 10 | 12675 | 15925 | 16666 | 16463 | 17088 | 14110 | 17023 | 17304 | 17930 | 18422 | 17606 | 15408 | 18256 | 19269 | 19176 | 19974 | 19089 | 19387 | 19579 | 20351
3851 | 3851 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 11 | 12927 | 16187 | 16923 | 16753 | 17464 | 14425 | 17319 | 17661 | 18280 | 18884 | 18125 | 15816 | 18641 | 19696 | 19655 | 20536 | 19693 | 19814 | 20067 | 20825
3852 | 3852 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 12 | 13138 | 16372 | 17197 | 16944 | 17683 | 14662 | 17431 | 17913 | 18612 | 19138 | 18437 | 16102 | 18801 | 20084 | 19936 | 20844 | 20042 | 19992 | 20410 | 21246
3853 | 3853 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 13 | 13210 | 16591 | 17435 | 17159 | 17904 | 14706 | 17621 | 18131 | 18855 | 19387 | 18565 | 16168 | 19002 | 20335 | 20178 | 21092 | 20165 | 20200 | 20641 | 21502
3854 | 3854 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 14 | 13327 | 16725 | 17618 | 17291 | 18038 | 14856 | 17747 | 18262 | 19035 | 19510 | 18685 | 16309 | 19107 | 20497 | 20248 | 21174 | 20259 | 20288 | 20736 | 21655
3855 | 3855 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 15 | 13623 | 16959 | 17911 | 17617 | 18213 | 15154 | 18037 | 18479 | 19313 | 19655 | 18885 | 16603 | 19384 | 20756 | 20510 | 21276 | 20434 | 20557 | 20912 | 21899
3856 | 3856 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 16 | 14173 | 17475 | 18449 | 18071 | 18573 | 15670 | 18483 | 19161 | 19778 | 19934 | 19159 | 17060 | 19761 | 21144 | 20760 | 21447 | 20637 | 20904 | 21616 | 22256
3857 | 3857 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 17 | 14791 | 17833 | 18869 | 18418 | 18966 | 16337 | 18966 | 19575 | 20130 | 20335 | 19661 | 17717 | 20288 | 21573 | 21085 | 21861 | 21169 | 21442 | 22054 | 22694
3858 | 3858 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 18 | 15148 | 17951 | 18954 | 18649 | 19211 | 16872 | 19292 | 19686 | 20302 | 20829 | 20293 | 18484 | 20876 | 21821 | 21763 | 22566 | 22039 | 22083 | 22429 | 23030
3859 | 3859 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 19 | 15325 | 18039 | 18881 | 18844 | 19329 | 17131 | 19441 | 19939 | 20493 | 21140 | 20821 | 19069 | 21271 | 22329 | 22493 | 23198 | 22869 | 22599 | 23194 | 23701
3860 | 3860 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 20 | 15167 | 17880 | 18736 | 18783 | 19234 | 17113 | 19311 | 19961 | 20590 | 21242 | 20956 | 19348 | 21551 | 22850 | 23156 | 23795 | 23317 | 23047 | 23753 | 24386
3861 | 3861 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 21 | 14810 | 17469 | 18236 | 18446 | 18790 | 16911 | 19091 | 19824 | 20423 | 21156 | 21056 | 19531 | 21729 | 23153 | 23657 | 24231 | 23828 | 23448 | 24340 | 24941
3862 | 3862 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 22 | 14330 | 16555 | 17293 | 17547 | 17965 | 16501 | 18319 | 19055 | 19714 | 20566 | 20852 | 19350 | 21202 | 22722 | 23294 | 23948 | 23900 | 23050 | 24006 | 24675
3863 | 3863 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 23 | 13487 | 15280 | 15972 | 16332 | 16683 | 15658 | 17120 | 17833 | 18443 | 19377 | 20037 | 18564 | 20071 | 21572 | 22246 | 22881 | 23176 | 21977 | 22969 | 23586
3864 | 3864 | 161 | 6 | 10 | Summer | 6 | 9 | Summer | 24 | 12844 | 14350 | 14970 | 15324 | 15578 | 15008 | 16115 | 16885 | 17444 | 18317 | 19076 | 17950 | 19083 | 20621 | 21298 | 21888 | 22238 | 21021 | 22125 | 22655
3865 | 3865 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 1 | 12110 | 13373 | 14116 | 14277 | 14954 | 14196 | 15313 | 15924 | 16570 | 17523 | 17712 | 17054 | 18667 | 19749 | 20284 | 20936 | 20402 | 20788 | 21330 | 21785
3866 | 3866 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 2 | 11897 | 13061 | 13737 | 13861 | 14498 | 13869 | 14919 | 15534 | 16107 | 16976 | 17116 | 16633 | 18144 | 19178 | 19654 | 20251 | 19714 | 20199 | 20757 | 21146
3867 | 3867 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 3 | 11794 | 12853 | 13544 | 13652 | 14181 | 13748 | 14688 | 15215 | 15816 | 16557 | 16643 | 16390 | 17767 | 18745 | 19189 | 19687 | 19134 | 19741 | 20213 | 20644
3868 | 3868 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 4 | 11855 | 12845 | 13516 | 13577 | 13960 | 13710 | 14550 | 15015 | 15570 | 16086 | 16130 | 16074 | 17283 | 18169 | 18515 | 18881 | 18371 | 19062 | 19485 | 19889
3869 | 3869 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 5 | 12120 | 13095 | 13708 | 13741 | 13825 | 13856 | 14673 | 15088 | 15499 | 15614 | 15586 | 15893 | 17006 | 17739 | 17971 | 18017 | 17509 | 18559 | 18899 | 19253
3870 | 3870 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 6 | 13046 | 14047 | 14528 | 14607 | 14011 | 14626 | 15462 | 15863 | 16012 | 15476 | 15343 | 16305 | 17336 | 17861 | 18031 | 17428 | 16952 | 18668 | 19022 | 19173
3871 | 3871 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 7 | 14188 | 15169 | 15502 | 15681 | 14282 | 15604 | 16368 | 16782 | 16756 | 15533 | 15366 | 17025 | 17788 | 18241 | 18491 | 17095 | 16770 | 18942 | 19455 | 19423
3872 | 3872 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 8 | 14687 | 15723 | 15986 | 16301 | 14913 | 16153 | 16719 | 17268 | 17168 | 16098 | 15934 | 17485 | 17926 | 18476 | 18928 | 17536 | 17241 | 19007 | 19690 | 19625
3873 | 3873 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 9 | 14850 | 15924 | 16176 | 16656 | 15573 | 16392 | 16871 | 17484 | 17305 | 16737 | 16562 | 17640 | 18000 | 18552 | 19229 | 18143 | 17814 | 19023 | 19763 | 19694
3874 | 3874 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 10 | 15121 | 16141 | 16370 | 16995 | 16131 | 16719 | 17156 | 17783 | 17576 | 17400 | 17331 | 18061 | 18376 | 18908 | 19742 | 18894 | 18647 | 19451 | 20204 | 20094
3875 | 3875 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 11 | 15315 | 16336 | 16609 | 17305 | 16492 | 16950 | 17447 | 18065 | 17900 | 17856 | 18036 | 18384 | 18759 | 19328 | 20244 | 19438 | 19412 | 19885 | 20622 | 20570
3876 | 3876 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 12 | 15395 | 16604 | 16826 | 17546 | 16778 | 17088 | 17724 | 18419 | 18142 | 18193 | 18519 | 18567 | 19092 | 19635 | 20579 | 19812 | 19906 | 20257 | 21072 | 20903
3877 | 3877 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 13 | 15555 | 16832 | 17024 | 17754 | 16866 | 17260 | 17924 | 18652 | 18350 | 18304 | 18859 | 18755 | 19293 | 19858 | 20811 | 19923 | 20231 | 20470 | 21315 | 21156
3878 | 3878 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 14 | 15661 | 16973 | 17133 | 17858 | 16973 | 17356 | 18025 | 18794 | 18442 | 18398 | 19126 | 18832 | 19375 | 19900 | 20866 | 19987 | 20479 | 20533 | 21428 | 21188
3879 | 3879 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 15 | 15855 | 17149 | 17351 | 17925 | 17090 | 17536 | 18130 | 18966 | 18641 | 18491 | 19437 | 19002 | 19468 | 20053 | 20862 | 20053 | 20782 | 20597 | 21568 | 21322
3880 | 3880 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 16 | 16247 | 17597 | 17735 | 18209 | 17338 | 17900 | 18694 | 19352 | 18925 | 18689 | 19900 | 19305 | 20109 | 20234 | 20955 | 20175 | 21187 | 21211 | 21829 | 21448
3881 | 3881 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 17 | 16762 | 18042 | 18095 | 18615 | 17790 | 18405 | 19129 | 19731 | 19319 | 19204 | 20534 | 19844 | 20576 | 20584 | 21397 | 20723 | 21911 | 21662 | 22291 | 21802
3882 | 3882 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 18 | 16933 | 18228 | 18359 | 18914 | 18323 | 18818 | 19330 | 19971 | 19862 | 19890 | 21410 | 20486 | 20962 | 21335 | 22194 | 21678 | 22888 | 22145 | 22721 | 22637
3883 | 3883 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 19 | 17092 | 18241 | 18623 | 19099 | 18692 | 19056 | 19655 | 20209 | 20284 | 20451 | 21743 | 20931 | 21658 | 22135 | 22875 | 22580 | 23476 | 23008 | 23493 | 23572
3884 | 3884 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 20 | 16906 | 18066 | 18521 | 18973 | 18523 | 18917 | 19639 | 20245 | 20465 | 20487 | 21797 | 21151 | 22016 | 22740 | 23426 | 22986 | 23837 | 23573 | 24182 | 24329
3885 | 3885 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 21 | 16512 | 17537 | 18145 | 18490 | 18177 | 18651 | 19429 | 19995 | 20417 | 20486 | 21676 | 21261 | 22309 | 23164 | 23809 | 23470 | 24081 | 24135 | 24717 | 24988
3886 | 3886 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 22 | 15624 | 16599 | 17228 | 17644 | 17687 | 17854 | 18611 | 19231 | 19711 | 20230 | 21243 | 20691 | 21785 | 22759 | 23492 | 23508 | 23854 | 23787 | 24449 | 24734
3887 | 3887 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 23 | 14420 | 15283 | 16018 | 16383 | 16776 | 16656 | 17376 | 17950 | 18569 | 19405 | 20164 | 19551 | 20671 | 21704 | 22414 | 22799 | 22877 | 22743 | 23366 | 23750
3888 | 3888 | 162 | 6 | 11 | Summer | 6 | 10 | Summer | 24 | 13463 | 14272 | 14979 | 15278 | 15787 | 15635 | 16395 | 16922 | 17532 | 18406 | 19220 | 18549 | 19765 | 20732 | 21383 | 21851 | 21963 | 21872 | 22408 | 22788
3889 | 3889 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 1 | 12574 | 13444 | 13920 | 14654 | 14931 | 14788 | 15404 | 16028 | 16441 | 17132 | 18377 | 18026 | 18851 | 19668 | 20414 | 19993 | 21018 | 21036 | 21530 | 21748
3890 | 3890 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 2 | 12280 | 13089 | 13534 | 14216 | 14439 | 14420 | 15040 | 15593 | 15943 | 16565 | 17780 | 17533 | 18367 | 19061 | 19755 | 19324 | 20333 | 20487 | 20907 | 21073
3891 | 3891 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 3 | 12127 | 12910 | 13356 | 13928 | 14085 | 14223 | 14760 | 15343 | 15652 | 16139 | 17383 | 17197 | 17921 | 18636 | 19223 | 18775 | 19821 | 19962 | 20426 | 20577
3892 | 3892 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 4 | 12147 | 12921 | 13318 | 13747 | 13837 | 14141 | 14626 | 15173 | 15380 | 15692 | 17082 | 16788 | 17423 | 18029 | 18474 | 18054 | 19276 | 19267 | 19697 | 19785
3893 | 3893 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 5 | 12428 | 13126 | 13489 | 13622 | 13560 | 14296 | 14745 | 15155 | 15288 | 15190 | 16962 | 16560 | 17094 | 17528 | 17640 | 17204 | 18917 | 18689 | 19055 | 19071
3894 | 3894 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 6 | 13397 | 14000 | 14401 | 13854 | 13625 | 15144 | 15595 | 15770 | 15857 | 15023 | 17571 | 16974 | 17497 | 17657 | 17108 | 16689 | 19283 | 18844 | 18994 | 18996
3895 | 3895 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 7 | 14522 | 15033 | 15560 | 14208 | 13994 | 16135 | 16606 | 16635 | 16721 | 15154 | 18638 | 17547 | 18190 | 18212 | 16862 | 16581 | 20103 | 19344 | 19295 | 19415
3896 | 3896 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 8 | 15007 | 15553 | 16226 | 14877 | 14707 | 16524 | 17137 | 17111 | 17342 | 15783 | 19612 | 17758 | 18540 | 18694 | 17345 | 17088 | 20956 | 19613 | 19520 | 19862
3897 | 3897 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 9 | 15171 | 15724 | 16610 | 15531 | 15394 | 16673 | 17359 | 17258 | 17722 | 16440 | 20107 | 17843 | 18656 | 18996 | 17960 | 17663 | 21372 | 19679 | 19583 | 20156
3898 | 3898 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 10 | 15370 | 15887 | 16923 | 16051 | 16050 | 16911 | 17613 | 17492 | 18120 | 17169 | 20800 | 18182 | 19021 | 19474 | 18679 | 18462 | 22140 | 20088 | 19957 | 20682
3899 | 3899 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 11 | 15535 | 16064 | 17183 | 16359 | 16629 | 17137 | 17834 | 17757 | 18479 | 17813 | 21332 | 18512 | 19343 | 19923 | 19174 | 19181 | 22744 | 20461 | 20388 | 21186
3900 | 3900 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 12 | 15707 | 16228 | 17392 | 16627 | 17053 | 17382 | 18159 | 17983 | 18730 | 18271 | 21711 | 18817 | 19732 | 20218 | 19511 | 19652 | 23144 | 20874 | 20686 | 21509
3901 | 3901 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 13 | 15917 | 16417 | 17599 | 16724 | 17393 | 17581 | 18391 | 18202 | 18967 | 18615 | 22009 | 19028 | 19977 | 20449 | 19622 | 19991 | 23450 | 21114 | 20923 | 21754
3902 | 3902 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 14 | 16068 | 16587 | 17756 | 16881 | 17716 | 17735 | 18593 | 18347 | 19112 | 18935 | 22198 | 19165 | 20150 | 20563 | 19743 | 20286 | 23609 | 21284 | 21008 | 21854
3903 | 3903 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 15 | 16204 | 16803 | 17835 | 16997 | 18038 | 17849 | 18770 | 18547 | 19151 | 19257 | 22394 | 19261 | 20303 | 20572 | 19820 | 20592 | 23779 | 21431 | 21152 | 21842
3904 | 3904 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 16 | 16676 | 17253 | 18187 | 17311 | 18608 | 18462 | 19221 | 18909 | 19417 | 19779 | 22749 | 19949 | 20668 | 20738 | 20008 | 21057 | 24083 | 21750 | 21339 | 21958
3905 | 3905 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 17 | 17081 | 17650 | 18630 | 17788 | 19297 | 18945 | 19637 | 19324 | 19859 | 20447 | 23218 | 20448 | 21141 | 21221 | 20602 | 21810 | 24499 | 22252 | 21738 | 22446
3906 | 3906 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 18 | 17270 | 17833 | 18823 | 18247 | 19905 | 19102 | 19829 | 19765 | 20394 | 21245 | 23751 | 20786 | 21438 | 21964 | 21501 | 22734 | 25201 | 22637 | 22536 | 23268
3907 | 3907 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 19 | 17326 | 17995 | 18871 | 18476 | 19851 | 19293 | 19921 | 20020 | 20645 | 21412 | 23917 | 21302 | 21893 | 22503 | 22253 | 23193 | 25651 | 23296 | 23360 | 23949
3908 | 3908 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 20 | 17140 | 17870 | 18712 | 18285 | 19663 | 19258 | 19917 | 20135 | 20658 | 21391 | 24000 | 21598 | 22360 | 22991 | 22626 | 23535 | 26020 | 23994 | 24128 | 24605
3909 | 3909 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 21 | 16702 | 17448 | 18171 | 17882 | 19180 | 18981 | 19583 | 19982 | 20470 | 21180 | 23600 | 21787 | 22579 | 23286 | 23034 | 23720 | 25993 | 24482 | 24752 | 25116
3910 | 3910 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 22 | 15803 | 16545 | 17307 | 17385 | 18524 | 18128 | 18774 | 19242 | 19838 | 20705 | 22758 | 21216 | 22102 | 22927 | 23041 | 23487 | 25356 | 24195 | 24492 | 24923
3911 | 3911 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 23 | 14530 | 15316 | 16047 | 16475 | 17370 | 16880 | 17466 | 18060 | 18621 | 19612 | 21177 | 20072 | 20921 | 21822 | 22313 | 22490 | 23817 | 23096 | 23506 | 23887
3912 | 3912 | 163 | 6 | 12 | Summer | 6 | 11 | Summer | 24 | 13606 | 14315 | 14931 | 15495 | 16404 | 15896 | 16422 | 17002 | 17538 | 18653 | 19920 | 19157 | 19956 | 20792 | 21363 | 21582 | 22611 | 22146 | 22562 | 22890
3913 | 3913 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 1 | 12694 | 13356 | 14402 | 14770 | 15736 | 14939 | 15563 | 15983 | 16847 | 17876 | 19304 | 18295 | 19120 | 19932 | 19648 | 20734 | 22313 | 21357 | 21614 | 21956
3914 | 3914 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 2 | 12394 | 12995 | 13977 | 14278 | 15209 | 14582 | 15136 | 15496 | 16326 | 17291 | 18652 | 17823 | 18567 | 19286 | 18985 | 20049 | 21567 | 20736 | 20949 | 21252
3915 | 3915 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 3 | 12216 | 12797 | 13692 | 13930 | 14909 | 14308 | 14899 | 15224 | 15949 | 16907 | 18191 | 17400 | 18174 | 18764 | 18441 | 19546 | 20988 | 20250 | 20437 | 20656
3916 | 3916 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 4 | 12228 | 12777 | 13519 | 13693 | 14843 | 14203 | 14765 | 15007 | 15550 | 16643 | 17757 | 16956 | 17663 | 18050 | 17741 | 19019 | 20274 | 19525 | 19645 | 19761
3917 | 3917 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 5 | 12469 | 12982 | 13436 | 13444 | 15030 | 14392 | 14824 | 14997 | 15146 | 16599 | 17549 | 16706 | 17293 | 17289 | 16946 | 18697 | 19725 | 18919 | 18960 | 18787
3918 | 3918 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 6 | 13427 | 13903 | 13697 | 13529 | 15950 | 15288 | 15503 | 15647 | 15087 | 17267 | 18049 | 17172 | 17486 | 16805 | 16462 | 19079 | 19883 | 18866 | 18886 | 18100
3919 | 3919 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 7 | 14632 | 15102 | 14107 | 13942 | 17248 | 16355 | 16448 | 16603 | 15270 | 18413 | 18936 | 17942 | 17990 | 16614 | 16393 | 19933 | 20521 | 19189 | 19315 | 17777
3920 | 3920 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 8 | 15315 | 15867 | 14916 | 14766 | 18379 | 17001 | 17052 | 17368 | 16000 | 19530 | 19549 | 18430 | 18384 | 17218 | 17016 | 20897 | 20984 | 19503 | 19856 | 18358
3921 | 3921 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 9 | 15632 | 16368 | 15730 | 15599 | 19095 | 17353 | 17348 | 17902 | 16781 | 20176 | 19874 | 18702 | 18610 | 17965 | 17728 | 21459 | 21187 | 19700 | 20265 | 19093
3922 | 3922 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 10 | 15844 | 16728 | 16292 | 16278 | 19713 | 17631 | 17608 | 18324 | 17424 | 20905 | 20413 | 19086 | 18951 | 18712 | 18561 | 22254 | 21787 | 20108 | 20833 | 19905
3923 | 3923 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 11 | 15984 | 16954 | 16587 | 16835 | 20153 | 17829 | 17849 | 18656 | 17813 | 21421 | 20872 | 19388 | 19311 | 19185 | 19263 | 22834 | 22334 | 20520 | 21327 | 20434
3924 | 3924 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 12 | 16264 | 17209 | 16919 | 17323 | 20574 | 18207 | 18133 | 18966 | 18203 | 21856 | 21235 | 19833 | 19658 | 19594 | 19808 | 23296 | 22743 | 20892 | 21723 | 20863
3925 | 3925 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 13 | 16470 | 17414 | 17000 | 17645 | 20855 | 18423 | 18336 | 19181 | 18292 | 22149 | 21382 | 20060 | 19862 | 19696 | 20137 | 23586 | 22879 | 21113 | 21951 | 20965
3926 | 3926 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 14 | 16802 | 17705 | 17282 | 18098 | 21203 | 18751 | 18605 | 19463 | 18585 | 22462 | 21581 | 20374 | 20110 | 19946 | 20561 | 23877 | 23067 | 21320 | 22180 | 21202
3927 | 3927 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 15 | 17082 | 17883 | 17490 | 18521 | 21513 | 19029 | 18910 | 19609 | 18781 | 22761 | 21768 | 20636 | 20376 | 20120 | 20961 | 24153 | 23228 | 21562 | 22265 | 21365
3928 | 3928 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 16 | 17463 | 18115 | 17665 | 18952 | 21790 | 19352 | 19143 | 19756 | 18905 | 22991 | 22363 | 20876 | 20489 | 20177 | 21292 | 24317 | 23815 | 21604 | 22248 | 21395
3929 | 3929 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 17 | 17908 | 18481 | 18062 | 19591 | 22186 | 19705 | 19490 | 20145 | 19393 | 23395 | 22636 | 21295 | 20822 | 20700 | 21980 | 24693 | 24117 | 21942 | 22674 | 21928
3930 | 3930 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 18 | 17766 | 18336 | 18158 | 19864 | 22198 | 19592 | 19591 | 20323 | 19716 | 23595 | 22528 | 21273 | 21222 | 21296 | 22601 | 25087 | 24122 | 22438 | 23200 | 22586
3931 | 3931 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 19 | 17577 | 18299 | 18272 | 19713 | 22131 | 19578 | 19722 | 20440 | 20039 | 23616 | 22869 | 21598 | 21779 | 21931 | 22954 | 25445 | 24704 | 23180 | 23807 | 23356
3932 | 3932 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 20 | 17363 | 18088 | 18015 | 19474 | 21899 | 19515 | 19769 | 20352 | 19988 | 23584 | 23007 | 21959 | 22310 | 22219 | 23231 | 25767 | 25279 | 23924 | 24423 | 23779
3933 | 3933 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 21 | 16799 | 17526 | 17594 | 18960 | 21150 | 19133 | 19563 | 20075 | 19876 | 23125 | 22981 | 22084 | 22638 | 22576 | 23386 | 25698 | 25655 | 24559 | 24952 | 24360
3934 | 3934 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 22 | 15844 | 16643 | 17066 | 18268 | 20075 | 18264 | 18755 | 19362 | 19558 | 22225 | 22252 | 21528 | 22170 | 22530 | 23107 | 25020 | 25177 | 24277 | 24733 | 24467
3935 | 3935 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 23 | 14536 | 15393 | 16158 | 17130 | 18439 | 16944 | 17555 | 18125 | 18723 | 20631 | 20885 | 20327 | 21102 | 21778 | 22101 | 23479 | 23907 | 23280 | 23697 | 23783
3936 | 3936 | 164 | 6 | 13 | Summer | 6 | 12 | Summer | 24 | 13560 | 14310 | 15181 | 16169 | 17176 | 15911 | 16493 | 17018 | 17732 | 19376 | 19731 | 19338 | 20124 | 20833 | 21187 | 22267 | 22800 | 22351 | 22709 | 22871
3937 | 3937 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 1 | 12867 | 13854 | 14561 | 15538 | 16308 | 15108 | 15531 | 16366 | 16639 | 18763 | 19137 | 18537 | 19190 | 19230 | 20371 | 21988 | 22324 | 21440 | 21803 | 20988
3938 | 3938 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 2 | 12533 | 13460 | 14103 | 15036 | 15795 | 14713 | 15077 | 15881 | 16100 | 18150 | 18512 | 18024 | 18615 | 18598 | 19715 | 21273 | 21587 | 20788 | 21114 | 20303
3939 | 3939 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 3 | 12348 | 13191 | 13766 | 14744 | 15454 | 14495 | 14828 | 15522 | 15684 | 17715 | 18035 | 17654 | 18199 | 18072 | 19229 | 20702 | 20974 | 20285 | 20527 | 19718
3940 | 3940 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 4 | 12344 | 13038 | 13538 | 14683 | 15307 | 14393 | 14655 | 15169 | 15271 | 17334 | 17651 | 17196 | 17635 | 17403 | 18725 | 20008 | 20293 | 19503 | 19639 | 18900
3941 | 3941 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 5 | 12575 | 12953 | 13304 | 14895 | 15443 | 14493 | 14702 | 14837 | 14842 | 17190 | 17434 | 16905 | 17216 | 16648 | 18435 | 19498 | 19721 | 18833 | 18672 | 17971
3942 | 3942 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 6 | 13457 | 13212 | 13410 | 15840 | 16332 | 15208 | 15417 | 14857 | 14728 | 17756 | 17988 | 17181 | 17405 | 16201 | 18845 | 19686 | 19882 | 18768 | 17987 | 17360
3943 | 3943 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 7 | 14483 | 13621 | 13828 | 17134 | 17542 | 16152 | 16402 | 15088 | 14894 | 18680 | 18905 | 17719 | 17988 | 16134 | 19693 | 20310 | 20456 | 19174 | 17633 | 17193
3944 | 3944 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 8 | 15059 | 14402 | 14641 | 18225 | 18244 | 16722 | 17153 | 15811 | 15602 | 19304 | 19536 | 18102 | 18554 | 16727 | 20628 | 20748 | 20960 | 19678 | 18165 | 17776
3945 | 3945 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 9 | 15326 | 15190 | 15492 | 18941 | 18601 | 17007 | 17693 | 16610 | 16397 | 19644 | 19949 | 18330 | 18978 | 17441 | 21203 | 20940 | 21321 | 20079 | 18891 | 18472
3946 | 3946 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 10 | 15469 | 15666 | 16102 | 19496 | 18976 | 17185 | 18032 | 17192 | 17108 | 20107 | 20423 | 18606 | 19442 | 18197 | 21917 | 21487 | 21893 | 20575 | 19629 | 19278
3947 | 3947 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 11 | 15622 | 15960 | 16650 | 19915 | 19318 | 17406 | 18344 | 17561 | 17731 | 20551 | 20811 | 18940 | 19867 | 18885 | 22486 | 22018 | 22362 | 21059 | 20149 | 20008
3948 | 3948 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 12 | 15849 | 16280 | 17142 | 20328 | 19636 | 17692 | 18655 | 17934 | 18250 | 20915 | 21284 | 19282 | 20236 | 19436 | 22956 | 22425 | 22901 | 21460 | 20584 | 20571
3949 | 3949 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 13 | 16080 | 16424 | 17504 | 20663 | 19826 | 17930 | 18906 | 18070 | 18632 | 21102 | 21541 | 19538 | 20508 | 19808 | 23286 | 22611 | 23177 | 21726 | 20728 | 20941
3950 | 3950 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 14 | 16249 | 16585 | 17841 | 20877 | 19914 | 18086 | 19075 | 18234 | 18947 | 21195 | 21765 | 19661 | 20623 | 20122 | 23463 | 22671 | 23371 | 21839 | 20851 | 21243
3951 | 3951 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 15 | 16481 | 16702 | 18179 | 21107 | 20028 | 18307 | 19138 | 18350 | 19281 | 21297 | 21928 | 19847 | 20644 | 20442 | 23658 | 22747 | 23514 | 21831 | 20931 | 21558
3952 | 3952 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 16 | 16828 | 16901 | 18630 | 21402 | 20567 | 18573 | 19318 | 18507 | 19698 | 21912 | 22113 | 19996 | 20713 | 20800 | 23840 | 23365 | 23631 | 21834 | 20977 | 21894
3953 | 3953 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 17 | 17064 | 17172 | 19136 | 21671 | 20735 | 18800 | 19583 | 18866 | 20197 | 22058 | 22452 | 20199 | 21024 | 21361 | 24096 | 23538 | 24017 | 22134 | 21384 | 22456
3954 | 3954 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 18 | 17157 | 17470 | 19575 | 21882 | 20700 | 19112 | 19948 | 19360 | 20895 | 22160 | 22703 | 20788 | 21681 | 22211 | 24711 | 23771 | 24461 | 22890 | 22283 | 23363
3955 | 3955 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 19 | 17350 | 17688 | 19508 | 21906 | 20886 | 19333 | 20138 | 19735 | 21048 | 22539 | 23196 | 21404 | 22200 | 22644 | 25158 | 24439 | 25264 | 23607 | 23163 | 23902
3956 | 3956 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 20 | 17214 | 17439 | 19271 | 21678 | 20805 | 19390 | 20040 | 19645 | 20970 | 22621 | 23489 | 21878 | 22633 | 22912 | 25484 | 25000 | 25883 | 24271 | 23627 | 24278
3957 | 3957 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 21 | 16799 | 16998 | 18728 | 20915 | 20368 | 19131 | 19691 | 19467 | 20709 | 22503 | 23121 | 22129 | 22858 | 23013 | 25371 | 25348 | 25973 | 24788 | 24204 | 24571
3958 | 3958 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 22 | 15900 | 16462 | 18038 | 19842 | 19392 | 18300 | 18945 | 19110 | 20194 | 21744 | 22511 | 21615 | 22447 | 22716 | 24685 | 24855 | 25653 | 24563 | 24321 | 24405
3959 | 3959 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 23 | 14680 | 15568 | 16917 | 18233 | 17931 | 17113 | 17712 | 18265 | 19103 | 20377 | 21142 | 20533 | 21343 | 21718 | 23157 | 23589 | 24378 | 23544 | 23660 | 23467
3960 | 3960 | 165 | 6 | 14 | Summer | 6 | 13 | Summer | 24 | 13704 | 14621 | 15931 | 16953 | 16716 | 16038 | 16575 | 17239 | 18133 | 19196 | 19940 | 19519 | 20285 | 20779 | 21911 | 22464 | 23228 | 22532 | 22727 | 22555
3961 | 3961 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 1 | 12726 | 13966 | 15246 | 16004 | 15952 | 14992 | 15879 | 16174 | 17337 | 18493 | 18755 | 18486 | 19409 | 19897 | 21529 | 21888 | 22118 | 21559 | 20791 | 21634
3962 | 3962 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 2 | 12375 | 13511 | 14743 | 15481 | 15414 | 14535 | 15391 | 15631 | 16765 | 17872 | 18185 | 17913 | 18778 | 19234 | 20808 | 21139 | 21425 | 20855 | 20089 | 20925
3963 | 3963 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 3 | 12186 | 13197 | 14460 | 15154 | 15075 | 14307 | 15048 | 15235 | 16412 | 17422 | 17758 | 17530 | 18282 | 18765 | 20252 | 20542 | 20857 | 20279 | 19508 | 20398
3964 | 3964 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 4 | 12164 | 12997 | 14413 | 15030 | 14992 | 14176 | 14749 | 14870 | 16183 | 17103 | 17354 | 17032 | 17610 | 18301 | 19598 | 19895 | 20125 | 19415 | 18701 | 19790
3965 | 3965 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 5 | 12362 | 12784 | 14640 | 15196 | 15165 | 14270 | 14482 | 14498 | 16182 | 16960 | 17105 | 16691 | 16898 | 18055 | 19133 | 19363 | 19441 | 18473 | 17783 | 19376
3966 | 3966 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 6 | 13282 | 12860 | 15591 | 16097 | 16102 | 15011 | 14555 | 14435 | 16901 | 17573 | 17463 | 16948 | 16469 | 18486 | 19346 | 19541 | 19411 | 17789 | 17161 | 19660
3967 | 3967 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 7 | 14420 | 13254 | 16871 | 17307 | 17233 | 15986 | 14798 | 14627 | 18024 | 18513 | 18134 | 17568 | 16259 | 19320 | 19960 | 20104 | 19840 | 17396 | 16948 | 20409
3968 | 3968 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 8 | 15039 | 13990 | 17881 | 17943 | 17885 | 16641 | 15443 | 15278 | 19024 | 19088 | 18508 | 18077 | 16750 | 20169 | 20319 | 20527 | 20112 | 17827 | 17427 | 21244
3969 | 3969 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 9 | 15402 | 14743 | 18501 | 18191 | 18238 | 17066 | 16130 | 15981 | 19570 | 19407 | 18636 | 18406 | 17378 | 20635 | 20406 | 20789 | 20226 | 18424 | 18005 | 21682
3970 | 3970 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 10 | 15706 | 15400 | 19086 | 18566 | 18616 | 17418 | 16728 | 16695 | 20230 | 19901 | 18822 | 18862 | 18068 | 21373 | 20977 | 21367 | 20488 | 19189 | 18840 | 22467
3971 | 3971 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 11 | 16014 | 16033 | 19602 | 18993 | 19001 | 17813 | 17185 | 17407 | 20830 | 20377 | 19095 | 19370 | 18631 | 22033 | 21602 | 21928 | 20865 | 19807 | 19669 | 23164
3972 | 3972 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 12 | 16258 | 16526 | 20012 | 19310 | 19386 | 18118 | 17552 | 17924 | 21263 | 20841 | 19248 | 19734 | 19042 | 22497 | 22006 | 22462 | 21076 | 20240 | 20232 | 23647
3973 | 3973 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 13 | 16508 | 16882 | 20354 | 19496 | 19626 | 18374 | 17690 | 18303 | 21598 | 21106 | 19373 | 20005 | 19181 | 22842 | 22198 | 22734 | 21220 | 20388 | 20611 | 23986
3974 | 3974 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 14 | 16650 | 17163 | 20529 | 19566 | 19823 | 18503 | 17820 | 18600 | 21769 | 21296 | 19417 | 20105 | 19294 | 22985 | 22225 | 22909 | 21235 | 20476 | 20875 | 24115
3975 | 3975 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 15 | 16814 | 17556 | 20812 | 19734 | 20052 | 18624 | 17986 | 18986 | 22035 | 21514 | 19507 | 20189 | 19439 | 23232 | 22353 | 23107 | 21295 | 20601 | 21237 | 24358
3976 | 3976 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 16 | 17090 | 18018 | 21121 | 20252 | 20312 | 18821 | 18168 | 19418 | 22289 | 21724 | 19641 | 20278 | 19534 | 23431 | 22987 | 23237 | 21312 | 20663 | 21576 | 24538
3977 | 3977 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 17 | 17371 | 18579 | 21430 | 20448 | 20637 | 19133 | 18567 | 19938 | 22600 | 22103 | 19976 | 20613 | 19962 | 23736 | 23204 | 23655 | 21708 | 21107 | 22189 | 24851
3978 | 3978 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 18 | 17490 | 19018 | 21624 | 20474 | 20869 | 19527 | 19068 | 20635 | 23057 | 22381 | 20717 | 21284 | 20817 | 24392 | 23485 | 24146 | 22592 | 22059 | 23149 | 25573
3979 | 3979 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 19 | 17609 | 18960 | 21663 | 20681 | 21115 | 19732 | 19444 | 20786 | 23188 | 22837 | 21266 | 21782 | 21556 | 24836 | 24157 | 24961 | 23441 | 22980 | 23725 | 26133
3980 | 3980 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 20 | 17418 | 18708 | 21398 | 20559 | 21066 | 19607 | 19309 | 20650 | 23128 | 23016 | 21698 | 22141 | 21808 | 25110 | 24669 | 25537 | 24231 | 23444 | 24102 | 26505
3981 | 3981 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 21 | 16839 | 18135 | 20618 | 20079 | 20254 | 19209 | 19067 | 20315 | 22604 | 22571 | 21502 | 22271 | 22090 | 24954 | 24960 | 25574 | 24475 | 24011 | 24392 | 26528
3982 | 3982 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 22 | 15965 | 17428 | 19538 | 19087 | 19339 | 18431 | 18664 | 19768 | 21677 | 21910 | 21031 | 21808 | 22003 | 24242 | 24444 | 25242 | 24265 | 24112 | 24224 | 25937
3983 | 3983 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 23 | 14717 | 16267 | 17893 | 17605 | 17821 | 17150 | 17764 | 18627 | 20075 | 20486 | 19900 | 20641 | 21230 | 22674 | 23125 | 23923 | 23244 | 23401 | 23240 | 24401
3984 | 3984 | 166 | 6 | 15 | Summer | 6 | 14 | Summer | 24 | 13658 | 15294 | 16626 | 16408 | 16624 | 16027 | 16746 | 17660 | 18813 | 19285 | 18941 | 19583 | 20286 | 21433 | 22005 | 22782 | 22314 | 22490 | 22350 | 23195
3985 | 3985 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 1 | 13249 | 14714 | 15746 | 15723 | 15457 | 15445 | 15832 | 16954 | 18139 | 18156 | 17920 | 18817 | 18765 | 21063 | 21501 | 21731 | 21283 | 20650 | 21516 | 23004
3986 | 3986 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 2 | 12851 | 14232 | 15244 | 15194 | 15011 | 14970 | 15299 | 16394 | 17524 | 17607 | 17381 | 18207 | 18128 | 20358 | 20764 | 21050 | 20621 | 19950 | 20806 | 22236
3987 | 3987 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 3 | 12587 | 13958 | 14928 | 14855 | 14725 | 14639 | 14913 | 16049 | 17112 | 17205 | 17083 | 17728 | 17615 | 19818 | 20176 | 20488 | 20180 | 19368 | 20277 | 21630
3988 | 3988 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 4 | 12444 | 13894 | 14802 | 14790 | 14627 | 14365 | 14572 | 15859 | 16782 | 16855 | 16685 | 17111 | 16983 | 19191 | 19553 | 19784 | 19454 | 18562 | 19661 | 20838
3989 | 3989 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 5 | 12378 | 14156 | 14983 | 15006 | 14729 | 14149 | 14252 | 15927 | 16717 | 16690 | 16421 | 16485 | 16290 | 18778 | 19069 | 19164 | 18843 | 17664 | 19257 | 20225
3990 | 3990 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 6 | 12621 | 15136 | 15910 | 15981 | 15452 | 14288 | 14269 | 16721 | 17329 | 17161 | 16701 | 16146 | 15871 | 19062 | 19313 | 19176 | 18726 | 17076 | 19565 | 20315
3991 | 3991 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 7 | 12997 | 16436 | 17151 | 17131 | 16456 | 14559 | 14505 | 17899 | 18268 | 17903 | 17338 | 16000 | 15797 | 19715 | 19909 | 19622 | 19030 | 16864 | 20301 | 20832
3992 | 3992 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 8 | 13696 | 17454 | 17817 | 17793 | 16969 | 15197 | 15162 | 18922 | 18831 | 18308 | 17820 | 16515 | 16311 | 20091 | 20361 | 19899 | 19372 | 17331 | 21132 | 21148
3993 | 3993 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 9 | 14333 | 18096 | 18113 | 18150 | 17111 | 15886 | 15887 | 19500 | 19088 | 18463 | 17990 | 17165 | 16929 | 20207 | 20640 | 20019 | 19517 | 17919 | 21578 | 21233
3994 | 3994 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 10 | 14851 | 18679 | 18495 | 18547 | 17208 | 16476 | 16597 | 20175 | 19575 | 18644 | 18285 | 17865 | 17721 | 20775 | 21227 | 20298 | 19907 | 18759 | 22372 | 21857
3995 | 3995 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 11 | 15249 | 19195 | 18917 | 18920 | 17370 | 16916 | 17296 | 20760 | 20104 | 18899 | 18568 | 18412 | 18506 | 21385 | 21784 | 20661 | 20288 | 19583 | 23073 | 22512
3996 | 3996 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 12 | 15468 | 19512 | 19144 | 19213 | 17371 | 17187 | 17718 | 21103 | 20372 | 18950 | 18676 | 18731 | 18967 | 21695 | 22224 | 20780 | 20452 | 20057 | 23466 | 22844
3997 | 3997 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 13 | 15606 | 19835 | 19298 | 19426 | 17439 | 17290 | 18062 | 21415 | 20550 | 19042 | 18840 | 18848 | 19332 | 21859 | 22459 | 20891 | 20644 | 20402 | 23774 | 23011
3998 | 3998 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 14 | 15713 | 20009 | 19362 | 19617 | 17495 | 17420 | 18360 | 21584 | 20594 | 19095 | 18836 | 18959 | 19599 | 21887 | 22638 | 20901 | 20595 | 20665 | 23907 | 23023
3999 | 3999 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 15 | 15775 | 20183 | 19426 | 19741 | 17498 | 17485 | 18643 | 21747 | 20641 | 19086 | 18818 | 19004 | 19863 | 21920 | 22731 | 20858 | 20541 | 20923 | 24041 | 23042
4000 | 4000 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 16 | 16069 | 20571 | 19956 | 20100 | 17813 | 17758 | 19164 | 22099 | 21325 | 19323 | 19005 | 19204 | 20308 | 22640 | 22956 | 20975 | 20629 | 21349 | 24301 | 23738
4001 | 4001 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 17 | 16486 | 20976 | 20253 | 20544 | 18292 | 18260 | 19781 | 22520 | 21620 | 19762 | 19465 | 19747 | 21024 | 22959 | 23466 | 21494 | 21051 | 22061 | 24714 | 24067
4002 | 4002 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 18 | 16876 | 21191 | 20331 | 20827 | 18826 | 18798 | 20498 | 22970 | 21806 | 20522 | 20244 | 20616 | 21958 | 23284 | 24009 | 22421 | 22009 | 23075 | 25495 | 24460
4003 | 4003 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 19 | 17107 | 21198 | 20502 | 21038 | 19034 | 19138 | 20607 | 23047 | 22165 | 20985 | 20712 | 21291 | 22382 | 23898 | 24776 | 23239 | 22866 | 23645 | 26043 | 25222
4004 | 4004 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 20 | 16814 | 20871 | 20317 | 20917 | 19129 | 18951 | 20410 | 22913 | 22157 | 21279 | 20859 | 21440 | 22569 | 24324 | 25258 | 23960 | 23400 | 23999 | 26389 | 25791
4005 | 4005 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 21 | 16351 | 20063 | 19802 | 20053 | 18488 | 18648 | 20014 | 22317 | 21955 | 20974 | 20901 | 21629 | 22608 | 24551 | 25230 | 24154 | 23889 | 24269 | 26398 | 26247
4006 | 4006 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 22 | 15777 | 18932 | 18764 | 19089 | 17712 | 18177 | 19392 | 21325 | 21133 | 20416 | 20500 | 21459 | 22254 | 23962 | 24806 | 23890 | 23778 | 24055 | 25770 | 25807
4007 | 4007 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 23 | 14874 | 17345 | 17325 | 17611 | 16527 | 17310 | 18282 | 19736 | 19737 | 19310 | 19454 | 20691 | 21226 | 22672 | 23524 | 22895 | 22791 | 23122 | 24280 | 24598
4008 | 4008 | 167 | 6 | 16 | Summer | 6 | 15 | Summer | 24 | 13976 | 16078 | 16114 | 16407 | 15541 | 16287 | 17298 | 18444 | 18543 | 18321 | 18491 | 19717 | 20284 | 21530 | 22371 | 21959 | 21866 | 22211 | 23045 | 23489
4009 | 4009 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 1 | 13121 | 14879 | 15131 | 14901 | 14256 | 15139 | 16282 | 17385 | 17598 | 16976 | 17374 | 17973 | 19172 | 20695 | 20974 | 20586 | 20567 | 21045 | 22531 | 22716
4010 | 4010 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 2 | 12680 | 14374 | 14623 | 14459 | 13836 | 14616 | 15730 | 16782 | 16997 | 16456 | 16816 | 17350 | 18522 | 19968 | 20305 | 19934 | 19904 | 20332 | 21764 | 21930
4011 | 4011 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 3 | 12366 | 14063 | 14295 | 14183 | 13676 | 14237 | 15397 | 16389 | 16563 | 16186 | 16399 | 16853 | 18061 | 19397 | 19759 | 19506 | 19349 | 19804 | 21158 | 21287
4012 | 4012 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 4 | 12175 | 13966 | 14255 | 14112 | 13615 | 13939 | 15255 | 16114 | 16300 | 15868 | 15918 | 16275 | 17632 | 18829 | 19104 | 18817 | 18559 | 19212 | 20379 | 20541
4013 | 4013 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 5 | 11978 | 14158 | 14488 | 14240 | 13738 | 13662 | 15375 | 16108 | 16233 | 15691 | 15311 | 15634 | 17439 | 18401 | 18535 | 18240 | 17591 | 18829 | 19779 | 19899
4014 | 4014 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 6 | 12105 | 15171 | 15498 | 15060 | 14464 | 13745 | 16258 | 16844 | 16970 | 16095 | 15050 | 15342 | 17968 | 18731 | 18627 | 18218 | 16956 | 19180 | 19907 | 20016
4015 | 4015 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 7 | 12565 | 16453 | 16693 | 16145 | 15442 | 14046 | 17525 | 17901 | 18018 | 16852 | 15126 | 15372 | 18886 | 19425 | 19150 | 18595 | 16771 | 19969 | 20471 | 20531
4016 | 4016 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 8 | 13325 | 17160 | 17376 | 16669 | 16040 | 14713 | 18569 | 18515 | 18634 | 17383 | 15718 | 15919 | 19762 | 19909 | 19453 | 18951 | 17251 | 20803 | 20803 | 20955
4017 | 4017 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 9 | 14178 | 17560 | 17827 | 16892 | 16346 | 15508 | 19235 | 18884 | 19057 | 17649 | 16311 | 16627 | 20341 | 20278 | 19659 | 19179 | 17749 | 21332 | 20966 | 21288
4018 | 4018 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 10 | 14988 | 18054 | 18345 | 17102 | 16661 | 16332 | 20020 | 19484 | 19680 | 18052 | 16885 | 17538 | 21207 | 20981 | 20055 | 19682 | 18413 | 22241 | 21711 | 22048
4019 | 4019 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 11 | 15695 | 18557 | 18805 | 17337 | 16910 | 17112 | 20681 | 20086 | 20217 | 18407 | 17384 | 18404 | 21939 | 21617 | 20498 | 20141 | 18989 | 23028 | 22459 | 22737
4020 | 4020 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 12 | 16174 | 18823 | 19173 | 17404 | 17035 | 17602 | 21092 | 20420 | 20651 | 18576 | 17606 | 18933 | 22388 | 22120 | 20683 | 20370 | 19246 | 23493 | 22862 | 23275
4021 | 4021 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 13 | 16575 | 19093 | 19477 | 17549 | 17260 | 18035 | 21497 | 20676 | 20967 | 18836 | 17701 | 19373 | 22793 | 22448 | 20882 | 20632 | 19348 | 23896 | 23122 | 23611
4022 | 4022 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 14 | 16936 | 19221 | 19732 | 17685 | 17360 | 18403 | 21734 | 20802 | 21245 | 18907 | 17719 | 19727 | 23026 | 22696 | 20963 | 20665 | 19357 | 24090 | 23201 | 23858
4023 | 4023 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 15 | 17282 | 19338 | 19918 | 17757 | 17431 | 18744 | 21963 | 20918 | 21412 | 18959 | 17813 | 20058 | 23231 | 22855 | 20986 | 20681 | 19428 | 24287 | 23283 | 24013
4024 | 4024 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 16 | 17860 | 19832 | 20299 | 18108 | 17732 | 19293 | 22338 | 21591 | 21742 | 19181 | 18085 | 20549 | 23544 | 23106 | 21132 | 20799 | 19647 | 24560 | 23993 | 24234
4025 | 4025 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 17 | 18388 | 19999 | 20612 | 18447 | 18032 | 19775 | 22619 | 21743 | 22100 | 19503 | 18548 | 21124 | 23806 | 23487 | 21520 | 21096 | 20143 | 24839 | 24187 | 24630
4026 | 4026 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 18 | 18574 | 19785 | 20594 | 18658 | 18276 | 20187 | 22742 | 21627 | 22131 | 19954 | 18885 | 21731 | 24207 | 23716 | 22152 | 21760 | 20663 | 25330 | 24294 | 24948
4027 | 4027 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 19 | 18245 | 19709 | 20560 | 18616 | 18276 | 20057 | 22570 | 21713 | 22288 | 20130 | 19096 | 21880 | 24396 | 24215 | 22702 | 22363 | 21111 | 25660 | 24834 | 25600
4028 | 4028 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 20 | 17841 | 19408 | 20316 | 18576 | 17940 | 19755 | 22313 | 21539 | 22264 | 20086 | 19363 | 21906 | 24492 | 24550 | 23297 | 22758 | 21780 | 25927 | 25318 | 26105
4029 | 4029 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 21 | 17284 | 18919 | 19479 | 17942 | 17571 | 19363 | 21714 | 21309 | 21758 | 20064 | 19815 | 21918 | 24312 | 24512 | 23483 | 23259 | 22674 | 25972 | 25812 | 26302
4030 | 4030 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 22 | 16498 | 17857 | 18478 | 17118 | 16857 | 18689 | 20670 | 20408 | 20990 | 19593 | 19678 | 21485 | 23507 | 24025 | 23166 | 23090 | 22798 | 25312 | 25348 | 25994
4031 | 4031 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 23 | 15377 | 16427 | 16997 | 15956 | 15733 | 17568 | 19062 | 19003 | 19591 | 18523 | 18876 | 20456 | 21971 | 22720 | 22152 | 22109 | 22094 | 23816 | 24133 | 24769
4032 | 4032 | 168 | 6 | 17 | Summer | 6 | 16 | Summer | 24 | 14402 | 15239 | 15802 | 14994 | 14768 | 16602 | 17777 | 17808 | 18388 | 17550 | 18063 | 19513 | 20724 | 21568 | 21206 | 21189 | 21322 | 22586 | 23020 | 23641
4033 | 4033 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 1 | 14027 | 14793 | 14841 | 14241 | 14391 | 16122 | 17195 | 17356 | 17432 | 17004 | 16762 | 18924 | 20495 | 20692 | 20363 | 20433 | 19549 | 22572 | 22760 | 22820
4034 | 4034 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 2 | 13587 | 14335 | 14458 | 13861 | 13999 | 15616 | 16640 | 16800 | 16935 | 16503 | 16250 | 18322 | 19828 | 20076 | 19763 | 19812 | 18915 | 21847 | 22021 | 22131
4035 | 4035 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 3 | 13330 | 14039 | 14206 | 13727 | 13730 | 15308 | 16276 | 16406 | 16569 | 16127 | 15871 | 17895 | 19318 | 19561 | 19365 | 19285 | 18417 | 21266 | 21397 | 21525
4036 | 4036 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 4 | 13280 | 13992 | 14165 | 13700 | 13578 | 15206 | 16057 | 16205 | 16306 | 15717 | 15417 | 17522 | 18760 | 18965 | 18728 | 18536 | 17711 | 20513 | 20667 | 20748
4037 | 4037 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 5 | 13558 | 14251 | 14320 | 13862 | 13360 | 15373 | 16116 | 16212 | 16230 | 15189 | 14864 | 17392 | 18415 | 18460 | 18206 | 17613 | 16867 | 19941 | 20044 | 20031
4038 | 4038 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 6 | 14549 | 15269 | 15150 | 14609 | 13517 | 16271 | 16892 | 16998 | 16796 | 14990 | 14486 | 17967 | 18769 | 18588 | 18215 | 16992 | 16147 | 20068 | 20144 | 19958
4039 | 4039 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 7 | 16008 | 16602 | 16376 | 15723 | 14055 | 17665 | 18115 | 18201 | 17745 | 15246 | 14493 | 19041 | 19621 | 19257 | 18734 | 16935 | 15879 | 20749 | 20780 | 20502
4040 | 4040 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 8 | 17324 | 17582 | 17206 | 16613 | 15012 | 18990 | 19050 | 19134 | 18476 | 16170 | 15006 | 20231 | 20327 | 19866 | 19390 | 17711 | 16336 | 21365 | 21492 | 21084
4041 | 4041 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 9 | 18143 | 18117 | 17538 | 17000 | 15725 | 19740 | 19523 | 19663 | 18796 | 16877 | 15553 | 20908 | 20635 | 20153 | 19712 | 18296 | 16876 | 21617 | 21922 | 21383
4042 | 4042 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 10 | 18656 | 18431 | 17566 | 17119 | 15997 | 20326 | 19924 | 20084 | 18903 | 17258 | 16002 | 21586 | 21133 | 20359 | 20027 | 18769 | 17397 | 22173 | 22492 | 21642
4043 | 4043 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 11 | 19022 | 18648 | 17556 | 17129 | 16144 | 20731 | 20268 | 20378 | 18993 | 17501 | 16335 | 22081 | 21585 | 20551 | 20235 | 19110 | 17805 | 22675 | 22933 | 21897
4044 | 4044 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 12 | 19277 | 18825 | 17467 | 17099 | 16188 | 20991 | 20449 | 20656 | 18972 | 17569 | 16542 | 22378 | 21833 | 20581 | 20311 | 19216 | 18063 | 22928 | 23320 | 21966
4045 | 4045 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 13 | 19604 | 19067 | 17517 | 17236 | 16167 | 21306 | 20613 | 20886 | 19051 | 17572 | 16658 | 22692 | 21995 | 20685 | 20489 | 19229 | 18178 | 23097 | 23568 | 22106
4046 | 4046 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 14 | 19658 | 19116 | 17491 | 17153 | 16016 | 21379 | 20576 | 20978 | 18992 | 17429 | 16676 | 22745 | 21906 | 20610 | 20360 | 19054 | 18149 | 23010 | 23643 | 22014
4047 | 4047 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 15 | 19884 | 19295 | 17560 | 17227 | 16116 | 21604 | 20688 | 21150 | 19035 | 17527 | 16865 | 22955 | 21994 | 20631 | 20376 | 19128 | 18323 | 23087 | 23795 | 22022
4048 | 4048 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 16 | 20149 | 19540 | 17782 | 17387 | 16300 | 21843 | 21188 | 21337 | 19173 | 17667 | 17174 | 23133 | 22588 | 20655 | 20366 | 19202 | 18580 | 23652 | 23865 | 21986
4049 | 4049 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 17 | 20497 | 19899 | 18176 | 17749 | 16791 | 22190 | 21402 | 21757 | 19535 | 18187 | 17812 | 23461 | 22829 | 21105 | 20722 | 19760 | 19239 | 23911 | 24322 | 22444
4050 | 4050 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 18 | 20560 | 20029 | 18463 | 18089 | 16967 | 22436 | 21419 | 21906 | 20123 | 18624 | 18547 | 23965 | 23001 | 21859 | 21516 | 20405 | 20184 | 24159 | 24778 | 23296
4051 | 4051 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 19 | 20545 | 20183 | 18610 | 18289 | 17127 | 22467 | 21690 | 22235 | 20523 | 18981 | 19070 | 24311 | 23566 | 22586 | 22287 | 21052 | 20949 | 24907 | 25649 | 24153
4052 | 4052 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 20 | 20195 | 19980 | 18620 | 18018 | 17234 | 22286 | 21564 | 22244 | 20744 | 19237 | 19372 | 24448 | 23931 | 23209 | 22733 | 21790 | 21481 | 25483 | 26246 | 24917
4053 | 4053 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 21 | 19367 | 19086 | 17907 | 17565 | 17199 | 21603 | 21221 | 21615 | 20349 | 19552 | 19348 | 24153 | 24085 | 23286 | 23124 | 22583 | 21801 | 25916 | 26390 | 25217
4054 | 4054 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 22 | 18256 | 18112 | 17111 | 16881 | 16841 | 20577 | 20322 | 20849 | 19772 | 19405 | 19107 | 23353 | 23487 | 22970 | 22965 | 22730 | 21784 | 25483 | 26121 | 25058
4055 | 4055 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 23 | 16656 | 16612 | 15915 | 15723 | 15925 | 18931 | 18863 | 19388 | 18623 | 18550 | 18270 | 21759 | 22155 | 21907 | 21938 | 21981 | 21041 | 24215 | 24861 | 24051
4056 | 4056 | 169 | 6 | 18 | Summer | 6 | 17 | Summer | 24 | 15402 | 15428 | 14939 | 14757 | 15061 | 17637 | 17650 | 18154 | 17632 | 17718 | 17516 | 20491 | 21007 | 20942 | 21003 | 21199 | 20334 | 23099 | 23722 | 23099
4057 | 4057 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 1 | 14543 | 14306 | 14006 | 14216 | 14103 | 16816 | 16978 | 16995 | 16621 | 16310 | 16837 | 19999 | 20468 | 19897 | 20062 | 19273 | 19595 | 22631 | 22707 | 22024
4058 | 4058 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 2 | 14077 | 13922 | 13632 | 13821 | 13675 | 16258 | 16420 | 16506 | 16147 | 15800 | 16421 | 19341 | 19782 | 19300 | 19444 | 18639 | 19088 | 21868 | 22008 | 21360
4059 | 4059 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 3 | 13781 | 13679 | 13504 | 13560 | 13406 | 15904 | 16040 | 16160 | 15913 | 15442 | 16172 | 18850 | 19242 | 18918 | 18929 | 18151 | 18732 | 21255 | 21396 | 20893
4060 | 4060 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 4 | 13694 | 13634 | 13496 | 13427 | 13206 | 15722 | 15888 | 15952 | 15669 | 15036 | 15894 | 18345 | 18729 | 18331 | 18218 | 17467 | 18202 | 20544 | 20627 | 20119
4061 | 4061 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 5 | 13883 | 13806 | 13678 | 13231 | 12989 | 15824 | 15952 | 15942 | 15573 | 14538 | 15819 | 18061 | 18364 | 17864 | 17337 | 16647 | 17805 | 19939 | 19917 | 19436
4062 | 4062 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 6 | 14881 | 14680 | 14442 | 13409 | 12943 | 16637 | 16789 | 16582 | 16033 | 14213 | 16385 | 18471 | 18726 | 17917 | 16749 | 15941 | 18082 | 20054 | 19838 | 19284
4063 | 4063 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 7 | 16306 | 15972 | 15633 | 14022 | 13207 | 17935 | 18078 | 17647 | 16996 | 14322 | 17200 | 19431 | 19616 | 18517 | 16766 | 15736 | 18714 | 20738 | 20424 | 19753
4064 | 4064 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 8 | 17360 | 16840 | 16579 | 15028 | 13835 | 18920 | 19066 | 18451 | 17881 | 14908 | 17861 | 20218 | 20454 | 19231 | 17595 | 16235 | 19292 | 21491 | 21037 | 20430
4065 | 4065 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 9 | 18065 | 17356 | 17209 | 15960 | 14647 | 19609 | 19822 | 19002 | 18448 | 15700 | 18322 | 20761 | 21141 | 19765 | 18403 | 16997 | 19716 | 22126 | 21543 | 20970
4066 | 4066 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 10 | 18585 | 17619 | 17546 | 16450 | 15208 | 20211 | 20447 | 19324 | 18871 | 16358 | 18785 | 21472 | 21869 | 20290 | 19089 | 17733 | 20250 | 22922 | 22021 | 21550
4067 | 4067 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 11 | 19005 | 17739 | 17708 | 16741 | 15615 | 20693 | 20882 | 19553 | 19135 | 16836 | 19169 | 22066 | 22420 | 20643 | 19578 | 18286 | 20721 | 23517 | 22430 | 21962
4068 | 4068 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 12 | 19151 | 17721 | 17750 | 16843 | 15829 | 20945 | 21230 | 19584 | 19196 | 17115 | 19367 | 22364 | 22819 | 20791 | 19760 | 18603 | 20932 | 23978 | 22573 | 22143
4069 | 4069 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 13 | 19294 | 17735 | 17850 | 16792 | 15885 | 21073 | 21422 | 19631 | 19319 | 17197 | 19557 | 22499 | 23017 | 20929 | 19737 | 18693 | 21126 | 24188 | 22665 | 22307
4070 | 4070 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 14 | 19303 | 17729 | 17818 | 16716 | 15964 | 21088 | 21565 | 19651 | 19280 | 17268 | 19587 | 22490 | 23149 | 20857 | 19619 | 18737 | 21134 | 24313 | 22632 | 22220
4071 | 4071 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 15 | 19357 | 17710 | 17812 | 16740 | 16094 | 21115 | 21649 | 19617 | 19269 | 17377 | 19630 | 22500 | 23247 | 20790 | 19610 | 18835 | 21190 | 24374 | 22552 | 22143
4072 | 4072 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 16 | 19683 | 17935 | 17976 | 16923 | 16445 | 21605 | 21840 | 19768 | 19360 | 17689 | 19747 | 23073 | 23357 | 20783 | 19688 | 19075 | 21253 | 24437 | 22517 | 22099
4073 | 4073 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 17 | 19724 | 18128 | 18122 | 17204 | 16790 | 21618 | 22054 | 19917 | 19533 | 18112 | 19840 | 23110 | 23593 | 20933 | 20038 | 19532 | 21439 | 24684 | 22772 | 22259
4074 | 4074 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 18 | 19430 | 18135 | 18162 | 17107 | 17122 | 21401 | 21955 | 20200 | 19857 | 18579 | 20057 | 23026 | 23710 | 21489 | 20437 | 20239 | 21746 | 24909 | 23386 | 22891
4075 | 4075 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 19 | 19350 | 18054 | 18114 | 17024 | 17222 | 21429 | 22031 | 20331 | 19987 | 18826 | 20491 | 23318 | 24175 | 22007 | 20833 | 20779 | 22436 | 25561 | 24031 | 23566
4076 | 4076 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 20 | 19093 | 18019 | 17789 | 17082 | 17278 | 21258 | 21986 | 20467 | 19935 | 19029 | 20990 | 23594 | 24522 | 22375 | 21509 | 21270 | 23207 | 26143 | 24780 | 24067
4077 | 4077 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 21 | 18529 | 17274 | 17278 | 16990 | 16891 | 20843 | 21263 | 19975 | 19758 | 18906 | 20940 | 23648 | 24332 | 22671 | 22232 | 21532 | 23482 | 26244 | 25051 | 24596
4078 | 4078 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 22 | 17505 | 16466 | 16568 | 16595 | 16426 | 19896 | 20434 | 19328 | 19276 | 18616 | 20368 | 22980 | 23858 | 22458 | 22325 | 21478 | 23122 | 25944 | 24875 | 24546
4079 | 4079 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 23 | 16057 | 15283 | 15416 | 15680 | 15504 | 18429 | 18953 | 18142 | 18162 | 17772 | 19195 | 21623 | 22499 | 21419 | 21570 | 20714 | 22023 | 24669 | 23874 | 23566
4080 | 4080 | 170 | 6 | 19 | Summer | 6 | 18 | Summer | 24 | 14880 | 14344 | 14463 | 14833 | 14735 | 17234 | 17729 | 17150 | 17179 | 17020 | 18140 | 20472 | 21329 | 20498 | 20792 | 20015 | 20946 | 23546 | 22949 | 22662
4081 | 4081 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 1 | 14192 | 13409 | 13898 | 13862 | 14084 | 16481 | 16478 | 16076 | 16412 | 16302 | 17869 | 19838 | 20168 | 19523 | 18863 | 19220 | 20935 | 22450 | 21828 | 21576
4082 | 4082 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 2 | 13727 | 13043 | 13516 | 13423 | 13752 | 15921 | 15991 | 15606 | 15905 | 15891 | 17349 | 19151 | 19534 | 18905 | 18228 | 18699 | 20301 | 21743 | 21146 | 20888
4083 | 4083 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 3 | 13446 | 12887 | 13269 | 13163 | 13602 | 15558 | 15670 | 15395 | 15545 | 15666 | 16955 | 18638 | 19033 | 18411 | 17755 | 18358 | 19779 | 21145 | 20682 | 20319
4084 | 4084 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 4 | 13403 | 12909 | 13166 | 12992 | 13581 | 15454 | 15518 | 15223 | 15205 | 15444 | 16603 | 18195 | 18499 | 17755 | 17111 | 17864 | 19139 | 20403 | 19930 | 19482
4085 | 4085 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 5 | 13655 | 13109 | 12988 | 12792 | 13774 | 15564 | 15562 | 15196 | 14743 | 15421 | 16414 | 17896 | 18051 | 16922 | 16323 | 17492 | 18651 | 19705 | 19253 | 18434
4086 | 4086 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 6 | 14694 | 13977 | 13234 | 12804 | 14652 | 16486 | 16306 | 15776 | 14634 | 16086 | 16886 | 18363 | 18264 | 16422 | 15689 | 17825 | 18814 | 19675 | 19142 | 17733
4087 | 4087 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 7 | 15932 | 15049 | 13754 | 12966 | 15597 | 17680 | 17294 | 16685 | 14851 | 16826 | 17613 | 19182 | 18882 | 16347 | 15375 | 18337 | 19205 | 20133 | 19475 | 17527
4088 | 4088 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 8 | 16695 | 15694 | 14533 | 13342 | 16085 | 18415 | 17853 | 17344 | 15588 | 17259 | 18065 | 19792 | 19292 | 16934 | 15627 | 18662 | 19468 | 20478 | 19883 | 18092
4089 | 4089 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 9 | 17039 | 15907 | 15080 | 13760 | 16159 | 18763 | 18012 | 17523 | 16128 | 17334 | 18228 | 20101 | 19414 | 17344 | 15988 | 18685 | 19565 | 20580 | 20005 | 18485
4090 | 4090 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 10 | 17376 | 16052 | 15382 | 14130 | 16328 | 19185 | 18131 | 17754 | 16528 | 17605 | 18704 | 20632 | 19640 | 17834 | 16532 | 19029 | 20124 | 20866 | 20402 | 19042
4091 | 4091 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 11 | 17698 | 16153 | 15623 | 14475 | 16559 | 19559 | 18297 | 17953 | 16858 | 17934 | 19159 | 21117 | 19922 | 18268 | 17035 | 19440 | 20657 | 21222 | 20770 | 19538
4092 | 4092 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 12 | 17937 | 16231 | 15745 | 14740 | 16735 | 19921 | 18345 | 18059 | 17021 | 18153 | 19464 | 21556 | 20048 | 18473 | 17376 | 19701 | 21009 | 21388 | 20975 | 19763
4093 | 4093 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 13 | 18258 | 16427 | 15795 | 14907 | 17013 | 20215 | 18490 | 18288 | 17095 | 18445 | 19813 | 21866 | 20236 | 18555 | 17570 | 20008 | 21381 | 21585 | 21231 | 19855
4094 | 4094 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 14 | 18403 | 16484 | 15776 | 15043 | 17121 | 20413 | 18566 | 18314 | 17072 | 18536 | 19975 | 22059 | 20281 | 18497 | 17674 | 20080 | 21521 | 21598 | 21207 | 19784
4095 | 4095 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 15 | 18599 | 16591 | 15908 | 15259 | 17272 | 20611 | 18650 | 18392 | 17182 | 18695 | 20204 | 22247 | 20322 | 18603 | 17884 | 20224 | 21708 | 21633 | 21238 | 19881
4096 | 4096 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 16 | 18870 | 16764 | 16113 | 15637 | 17467 | 20835 | 18835 | 18527 | 17350 | 18848 | 20778 | 22396 | 20377 | 18714 | 18165 | 20310 | 22266 | 21618 | 21223 | 19970
4097 | 4097 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 17 | 19291 | 17149 | 16638 | 16232 | 17849 | 21303 | 19233 | 18945 | 17920 | 19187 | 21176 | 22878 | 20876 | 19316 | 18872 | 20748 | 22637 | 22125 | 21643 | 20585
4098 | 4098 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 18 | 19445 | 17401 | 16732 | 16794 | 18115 | 21450 | 19722 | 19472 | 18345 | 19622 | 21446 | 23240 | 21628 | 19957 | 19818 | 21313 | 23011 | 22988 | 22534 | 21313
4099 | 4099 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 19 | 19506 | 17491 | 16771 | 17012 | 18436 | 21655 | 19969 | 19681 | 18575 | 20153 | 21858 | 23781 | 22237 | 20463 | 20482 | 22125 | 23768 | 23790 | 23358 | 21947
4100 | 4100 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 20 | 19265 | 17134 | 16788 | 17038 | 18719 | 21565 | 20061 | 19552 | 18747 | 20568 | 22080 | 24049 | 22785 | 21078 | 20935 | 22871 | 24347 | 24545 | 23854 | 22690
4101 | 4101 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 21 | 18363 | 16651 | 16693 | 16648 | 18365 | 20814 | 19529 | 19317 | 18982 | 20469 | 21871 | 23804 | 22799 | 21769 | 21185 | 23142 | 24543 | 24833 | 24407 | 23609
4102 | 4102 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 22 | 17344 | 15907 | 16274 | 16152 | 17560 | 19941 | 18830 | 18762 | 18757 | 19845 | 21332 | 23242 | 22410 | 21807 | 21097 | 22744 | 24249 | 24636 | 24337 | 23813
4103 | 4103 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 23 | 15862 | 14764 | 15373 | 15255 | 16346 | 18460 | 17641 | 17636 | 17896 | 18676 | 20110 | 21871 | 21342 | 21050 | 20329 | 21647 | 23102 | 23639 | 23374 | 23107
4104 | 4104 | 171 | 6 | 20 | Summer | 6 | 19 | Summer | 24 | 14726 | 13828 | 14519 | 14494 | 15306 | 17228 | 16630 | 16642 | 17072 | 17607 | 19098 | 20696 | 20380 | 20256 | 19614 | 20586 | 22144 | 22701 | 22469 | 22332
4105 | 4105 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 1 | 13577 | 13317 | 13619 | 13859 | 14815 | 15985 | 15587 | 15909 | 15724 | 17299 | 18826 | 19528 | 19304 | 18414 | 18833 | 20567 | 22085 | 21603 | 21388 | 20219
4106 | 4106 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 2 | 13200 | 12955 | 13205 | 13540 | 14407 | 15522 | 15142 | 15427 | 15224 | 16810 | 18227 | 18932 | 18715 | 17802 | 18331 | 19955 | 21373 | 20941 | 20724 | 19545
4107 | 4107 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 3 | 12991 | 12735 | 12967 | 13420 | 14152 | 15231 | 14965 | 15108 | 14909 | 16451 | 17838 | 18477 | 18376 | 17356 | 18012 | 19453 | 20854 | 20496 | 20168 | 19034
4108 | 4108 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 4 | 12950 | 12632 | 12806 | 13407 | 14094 | 15111 | 14838 | 14818 | 14560 | 16153 | 17435 | 17999 | 17853 | 16745 | 17542 | 18833 | 20139 | 19750 | 19332 | 18270
4109 | 4109 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 5 | 13119 | 12486 | 12621 | 13617 | 14251 | 15198 | 14869 | 14420 | 14112 | 16028 | 17193 | 17623 | 17446 | 15997 | 17204 | 18374 | 19539 | 19089 | 18293 | 17346
4110 | 4110 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 6 | 14026 | 12733 | 12649 | 14518 | 15070 | 15973 | 15508 | 14390 | 13868 | 16560 | 17613 | 17915 | 17588 | 15394 | 17550 | 18565 | 19583 | 18980 | 17587 | 16576
4111 | 4111 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 7 | 15345 | 13407 | 12991 | 15641 | 16249 | 17135 | 16621 | 14834 | 14043 | 17502 | 18448 | 18755 | 18255 | 15258 | 18240 | 19134 | 20137 | 19465 | 17526 | 16344
4112 | 4112 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 8 | 16230 | 14521 | 13691 | 16421 | 17149 | 17995 | 17602 | 15903 | 14681 | 18303 | 19234 | 19489 | 19016 | 15821 | 18872 | 19708 | 20773 | 20179 | 18382 | 16901
4113 | 4113 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 9 | 16561 | 15324 | 14383 | 16746 | 17662 | 18399 | 18042 | 16711 | 15327 | 18739 | 19703 | 19862 | 19398 | 16442 | 19165 | 20046 | 21136 | 20550 | 19028 | 17518
4114 | 4114 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 10 | 16833 | 15832 | 14950 | 17103 | 18221 | 18703 | 18458 | 17300 | 15988 | 19408 | 20345 | 20276 | 19933 | 17175 | 19697 | 20804 | 21868 | 21143 | 19780 | 18307
4115 | 4115 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 11 | 16909 | 16061 | 15300 | 17337 | 18574 | 18860 | 18649 | 17632 | 16423 | 19861 | 20773 | 20559 | 20249 | 17678 | 20104 | 21348 | 22394 | 21514 | 20277 | 18859
4116 | 4116 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 12 | 16832 | 16084 | 15469 | 17417 | 18742 | 18808 | 18653 | 17695 | 16639 | 20065 | 21120 | 20582 | 20333 | 17922 | 20268 | 21603 | 22813 | 21622 | 20407 | 19123
4117 | 4117 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 13 | 16967 | 16146 | 15650 | 17706 | 19082 | 18961 | 18891 | 17777 | 16838 | 20422 | 21472 | 20770 | 20590 | 18132 | 20593 | 21977 | 23169 | 21888 | 20517 | 19340
4118 | 4118 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 14 | 17039 | 16176 | 15831 | 17849 | 19308 | 19083 | 18962 | 17795 | 17007 | 20639 | 21596 | 20859 | 20622 | 18286 | 20711 | 22160 | 23259 | 21899 | 20491 | 19481
4119 | 4119 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 15 | 17003 | 16175 | 15913 | 17883 | 19414 | 19035 | 18908 | 17789 | 17087 | 20735 | 21686 | 20784 | 20534 | 18366 | 20725 | 22226 | 23318 | 21794 | 20456 | 19559
4120 | 4120 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 16 | 17304 | 16419 | 16338 | 18124 | 19963 | 19281 | 19102 | 18015 | 17479 | 21358 | 21840 | 20909 | 20621 | 18698 | 20858 | 22850 | 23394 | 21827 | 20583 | 19874
4121 | 4121 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 17 | 17529 | 16709 | 16683 | 18258 | 20127 | 19441 | 19280 | 18330 | 17918 | 21507 | 21942 | 21151 | 20789 | 19170 | 21058 | 22968 | 23515 | 22008 | 20957 | 20356
4122 | 4122 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 18 | 17463 | 16458 | 16875 | 18189 | 20004 | 19600 | 19454 | 18394 | 18306 | 21449 | 21809 | 21559 | 21269 | 19802 | 21302 | 23042 | 23511 | 22595 | 21380 | 21043
4123 | 4123 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 19 | 17313 | 16281 | 16850 | 18288 | 20010 | 19609 | 19407 | 18365 | 18448 | 21586 | 22095 | 21905 | 21679 | 20218 | 21879 | 23573 | 24049 | 23204 | 21806 | 21565
4124 | 4124 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 20 | 17209 | 16241 | 16817 | 18504 | 19819 | 19650 | 19207 | 18431 | 18534 | 21683 | 22323 | 22346 | 21916 | 20600 | 22566 | 24074 | 24689 | 23682 | 22531 | 22041
4125 | 4125 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 21 | 16437 | 16069 | 16353 | 18081 | 19158 | 19021 | 18854 | 18535 | 18333 | 21337 | 22635 | 22215 | 22117 | 20753 | 22751 | 24178 | 25424 | 24173 | 23393 | 22371
4126 | 4126 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 22 | 15632 | 15630 | 15856 | 17288 | 18351 | 18296 | 18260 | 18283 | 17996 | 20759 | 22151 | 21789 | 21852 | 20632 | 22343 | 23871 | 25221 | 24099 | 23604 | 22387
4127 | 4127 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 23 | 14475 | 14726 | 14953 | 16092 | 17031 | 17096 | 17116 | 17401 | 17157 | 19513 | 20988 | 20702 | 20815 | 19856 | 21235 | 22722 | 24179 | 23122 | 22893 | 21655
4128 | 4128 | 172 | 6 | 21 | Summer | 6 | 20 | Summer | 24 | 13559 | 13878 | 14184 | 15055 | 15985 | 16094 | 16117 | 16550 | 16399 | 18495 | 19876 | 19723 | 19871 | 19133 | 20163 | 21762 | 23102 | 22219 | 22120 | 20947
4129 | 4129 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 1 | 12514 | 12881 | 13409 | 14381 | 15324 | 14890 | 15262 | 15123 | 15524 | 18022 | 19557 | 18466 | 18775 | 18198 | 19956 | 21494 | 22876 | 20995 | 19863 | 19994
4130 | 4130 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 2 | 12193 | 12495 | 13124 | 14002 | 14880 | 14478 | 14814 | 14657 | 15156 | 17463 | 18881 | 17919 | 18203 | 17726 | 19374 | 20808 | 22073 | 20344 | 19210 | 19468
4131 | 4131 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 3 | 12039 | 12257 | 13007 | 13745 | 14630 | 14316 | 14506 | 14347 | 14965 | 17097 | 18393 | 17594 | 17736 | 17420 | 18883 | 20286 | 21445 | 19797 | 18697 | 19098
4132 | 4132 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 4 | 12047 | 12090 | 12991 | 13690 | 14531 | 14213 | 14253 | 14027 | 14773 | 16741 | 17905 | 17117 | 17116 | 16973 | 18290 | 19588 | 20636 | 18967 | 17926 | 18500
4133 | 4133 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 5 | 12261 | 11932 | 13218 | 13879 | 14669 | 14296 | 13922 | 13639 | 14812 | 16576 | 17717 | 16791 | 16349 | 16683 | 17878 | 19029 | 20071 | 17955 | 17017 | 18034
4134 | 4134 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 6 | 13130 | 11996 | 14139 | 14729 | 15496 | 14976 | 13960 | 13468 | 15518 | 17069 | 18259 | 17023 | 15896 | 17074 | 18108 | 19119 | 20182 | 17264 | 16249 | 18275
4135 | 4135 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 7 | 14416 | 12391 | 15350 | 15998 | 16736 | 16177 | 14514 | 13757 | 16515 | 18028 | 19343 | 17815 | 16079 | 17842 | 18768 | 19761 | 20946 | 17265 | 16072 | 18968
4136 | 4136 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 8 | 15174 | 12939 | 15974 | 16763 | 17441 | 16992 | 15436 | 14274 | 17102 | 18689 | 20338 | 18453 | 16830 | 18318 | 19194 | 20258 | 21864 | 17955 | 16458 | 19441
4137 | 4137 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 9 | 15525 | 13531 | 16221 | 17185 | 17825 | 17332 | 16146 | 14845 | 17344 | 19080 | 21198 | 18755 | 17401 | 18508 | 19442 | 20531 | 22750 | 18487 | 16971 | 19626
4138 | 4138 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 10 | 15713 | 13957 | 16430 | 17587 | 18201 | 17584 | 16576 | 15350 | 17655 | 19566 | 22115 | 19124 | 17944 | 18887 | 20048 | 21110 | 23758 | 19091 | 17615 | 20062
4139 | 4139 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 11 | 15670 | 14186 | 16524 | 17785 | 18371 | 17622 | 16759 | 15633 | 17833 | 19846 | 22746 | 19280 | 18237 | 19151 | 20443 | 21486 | 24471 | 19453 | 18029 | 20378
4140 | 4140 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 12 | 15512 | 14215 | 16461 | 17796 | 18506 | 17482 | 16676 | 15691 | 17809 | 20046 | 23132 | 19207 | 18206 | 19172 | 20555 | 21747 | 24924 | 19443 | 18154 | 20427
4141 | 4141 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 13 | 15685 | 14363 | 16711 | 18097 | 18813 | 17678 | 16713 | 15849 | 18080 | 20361 | 23593 | 19427 | 18265 | 19464 | 20893 | 22064 | 25403 | 19508 | 18332 | 20722
4142 | 4142 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 14 | 15638 | 14389 | 16693 | 18172 | 18799 | 17588 | 16577 | 15868 | 18060 | 20332 | 23765 | 19307 | 18107 | 19426 | 20921 | 22004 | 25544 | 19326 | 18315 | 20675
4143 | 4143 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 15 | 15868 | 14690 | 16967 | 18521 | 19151 | 17777 | 16806 | 16190 | 18328 | 20665 | 24141 | 19469 | 18320 | 19681 | 21232 | 22308 | 25887 | 19523 | 18626 | 20927
4144 | 4144 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 16 | 16165 | 15205 | 17296 | 19127 | 19474 | 18062 | 17129 | 16676 | 18614 | 20923 | 24392 | 19659 | 18575 | 19912 | 21946 | 22475 | 26036 | 19738 | 19025 | 21130
4145 | 4145 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 17 | 16368 | 15599 | 17489 | 19355 | 19643 | 18306 | 17503 | 17170 | 18766 | 21090 | 24632 | 19877 | 18991 | 20169 | 22135 | 22662 | 26305 | 20179 | 19570 | 21416
4146 | 4146 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 18 | 16540 | 15996 | 17608 | 19478 | 19589 | 18694 | 17761 | 17749 | 19124 | 21166 | 24964 | 20553 | 19551 | 20647 | 22436 | 22890 | 26897 | 20845 | 20504 | 21957
4147 | 4147 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 19 | 16553 | 16092 | 17825 | 19599 | 19752 | 18766 | 17839 | 17988 | 19536 | 21524 | 25324 | 21044 | 19941 | 21332 | 23071 | 23541 | 27564 | 21410 | 21173 | 22744
4148 | 4148 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 20 | 16182 | 16040 | 18026 | 19414 | 19739 | 18560 | 17880 | 18059 | 19884 | 21680 | 25363 | 21249 | 20484 | 21992 | 23543 | 24187 | 27911 | 22153 | 21665 | 23489
4149 | 4149 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 21 | 15703 | 15624 | 17644 | 18781 | 19658 | 18220 | 17984 | 17854 | 19732 | 21949 | 25448 | 21421 | 21108 | 22193 | 23665 | 24939 | 28444 | 23063 | 22059 | 23850
4150 | 4150 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 22 | 14944 | 15096 | 16818 | 17932 | 18862 | 17569 | 17662 | 17465 | 19064 | 21390 | 24749 | 21079 | 21099 | 21729 | 23308 | 24684 | 28023 | 23232 | 22042 | 23508
4151 | 4151 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 23 | 13792 | 14186 | 15605 | 16588 | 17571 | 16398 | 16745 | 16578 | 17879 | 20197 | 23286 | 19991 | 20297 | 20593 | 22118 | 23605 | 26653 | 22491 | 21297 | 22409
4152 | 4152 | 173 | 6 | 22 | Summer | 6 | 21 | Summer | 24 | 12908 | 13442 | 14580 | 15568 | 16433 | 15416 | 15907 | 15814 | 16822 | 19088 | 21900 | 19054 | 19508 | 19524 | 21159 | 22547 | 25321 | 21735 | 20610 | 21351
4153 | 4153 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 1 | 12586 | 12962 | 14183 | 15197 | 16336 | 14886 | 14829 | 15236 | 16581 | 19021 | 20283 | 18281 | 17858 | 19551 | 21155 | 22593 | 23693 | 19775 | 19931 | 21514
4154 | 4154 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 2 | 12274 | 12708 | 13832 | 14769 | 15791 | 14460 | 14383 | 14890 | 16138 | 18375 | 19445 | 17738 | 17284 | 18991 | 20493 | 21804 | 22732 | 19135 | 19411 | 20888
4155 | 4155 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 3 | 12064 | 12599 | 13592 | 14527 | 15448 | 14171 | 14093 | 14716 | 15804 | 17919 | 18839 | 17298 | 16855 | 18524 | 19989 | 21191 | 21979 | 18629 | 19046 | 20354
4156 | 4156 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 4 | 11986 | 12634 | 13579 | 14479 | 15302 | 13987 | 13842 | 14595 | 15577 | 17528 | 18266 | 16765 | 16300 | 18002 | 19360 | 20443 | 21069 | 17903 | 18485 | 19663
4157 | 4157 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 5 | 11865 | 12888 | 13786 | 14650 | 15520 | 13711 | 13510 | 14693 | 15527 | 17427 | 17930 | 16074 | 15610 | 17645 | 18852 | 19920 | 20310 | 17017 | 18034 | 19106
4158 | 4158 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 6 | 12153 | 13868 | 14678 | 15546 | 16510 | 13829 | 13432 | 15507 | 16159 | 18096 | 18330 | 15743 | 15090 | 17960 | 19022 | 20105 | 20302 | 16298 | 18313 | 19226
4159 | 4159 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 7 | 12770 | 14993 | 15866 | 16690 | 17736 | 14297 | 13653 | 16442 | 17092 | 19137 | 19319 | 15874 | 14921 | 18547 | 19588 | 20772 | 21006 | 16008 | 18880 | 19671
4160 | 4160 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 8 | 13601 | 15466 | 16518 | 17255 | 18688 | 15070 | 14032 | 16904 | 17619 | 20018 | 20144 | 16503 | 15198 | 18844 | 19957 | 21557 | 21733 | 16238 | 19196 | 19909
4161 | 4161 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 9 | 14087 | 15499 | 16775 | 17432 | 19354 | 15580 | 14412 | 16967 | 17769 | 20696 | 20802 | 16890 | 15522 | 18911 | 20034 | 22240 | 22386 | 16549 | 19184 | 19952
4162 | 4162 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 10 | 14382 | 15611 | 17077 | 17701 | 20093 | 15894 | 14802 | 17168 | 18196 | 21500 | 21481 | 17318 | 16026 | 19405 | 20512 | 23141 | 23176 | 17089 | 19518 | 20508
4163 | 4163 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 11 | 14527 | 15750 | 17327 | 17926 | 20678 | 16116 | 15128 | 17397 | 18553 | 22170 | 21999 | 17660 | 16445 | 19850 | 20940 | 23910 | 23791 | 17555 | 19888 | 21008
4164 | 4164 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 12 | 14556 | 15839 | 17493 | 18213 | 21158 | 16184 | 15335 | 17524 | 18759 | 22703 | 22268 | 17782 | 16698 | 20114 | 21355 | 24504 | 24103 | 17834 | 20091 | 21300
4165 | 4165 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 13 | 14514 | 16026 | 17737 | 18458 | 21520 | 16162 | 15433 | 17733 | 19020 | 23108 | 22498 | 17782 | 16813 | 20394 | 21613 | 24925 | 24346 | 17955 | 20331 | 21594
4166 | 4166 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 14 | 14465 | 16088 | 17892 | 18526 | 21792 | 16109 | 15535 | 17794 | 19151 | 23371 | 22588 | 17708 | 16887 | 20501 | 21642 | 25144 | 24394 | 18019 | 20362 | 21694
4167 | 4167 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 15 | 14591 | 16255 | 18143 | 18776 | 22089 | 16239 | 15756 | 17960 | 19385 | 23655 | 22647 | 17824 | 17098 | 20717 | 21845 | 25392 | 24420 | 18232 | 20511 | 21896
4168 | 4168 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 16 | 14929 | 16588 | 18678 | 19118 | 22449 | 16574 | 16252 | 18262 | 20087 | 23923 | 22822 | 18100 | 17535 | 21443 | 22035 | 25556 | 24520 | 18628 | 20718 | 22588
4169 | 4169 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 17 | 15463 | 16953 | 19083 | 19474 | 22784 | 17124 | 16918 | 18592 | 20483 | 24341 | 23092 | 18699 | 18244 | 21805 | 22398 | 26004 | 24874 | 19353 | 21177 | 22959
4170 | 4170 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 18 | 15465 | 17073 | 19235 | 19445 | 22943 | 17392 | 17486 | 18917 | 20682 | 24669 | 23522 | 19249 | 19130 | 22133 | 22652 | 26619 | 25435 | 20323 | 21758 | 23344
4171 | 4171 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 19 | 15523 | 17390 | 19450 | 19692 | 23130 | 17560 | 17810 | 19405 | 21009 | 25071 | 23830 | 19692 | 19752 | 22835 | 23372 | 27372 | 26057 | 21098 | 22660 | 24197
4172 | 4172 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 20 | 15521 | 17596 | 19265 | 19664 | 22889 | 17611 | 17890 | 19724 | 21100 | 25039 | 23929 | 20185 | 20143 | 23290 | 23998 | 27711 | 26534 | 21637 | 23444 | 24782
4173 | 4173 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 21 | 15403 | 17153 | 18599 | 19548 | 22536 | 17661 | 17635 | 19517 | 20753 | 25021 | 23522 | 20720 | 20316 | 23353 | 24695 | 28205 | 26594 | 22022 | 23803 | 25053
4174 | 4174 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 22 | 14927 | 16341 | 17752 | 18735 | 21550 | 17318 | 17224 | 18823 | 20113 | 24281 | 22956 | 20667 | 20148 | 22968 | 24412 | 27768 | 26298 | 22011 | 23472 | 24823
4175 | 4175 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 23 | 14040 | 15170 | 16441 | 17475 | 20003 | 16422 | 16352 | 17644 | 18856 | 22819 | 21540 | 19863 | 19355 | 21796 | 23353 | 26411 | 24973 | 21281 | 22406 | 23734
4176 | 4176 | 174 | 6 | 23 | Summer | 6 | 22 | Summer | 24 | 13216 | 14171 | 15407 | 16343 | 18611 | 15575 | 15575 | 16567 | 17839 | 21405 | 20135 | 19058 | 18633 | 20818 | 22279 | 25061 | 23583 | 20579 | 21346 | 22785
4177 | 4177 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 1 | 12532 | 13764 | 15029 | 16215 | 17011 | 14566 | 14986 | 16254 | 17596 | 19769 | 19088 | 17487 | 17960 | 20774 | 22278 | 23406 | 22285 | 19875 | 21477 | 22886
4178 | 4178 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 2 | 12148 | 13403 | 14602 | 15656 | 16283 | 14112 | 14631 | 15806 | 17054 | 18931 | 18386 | 16912 | 17500 | 20108 | 21482 | 22440 | 21475 | 19342 | 20841 | 22145
4179 | 4179 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 3 | 11899 | 13180 | 14361 | 15311 | 15808 | 13820 | 14460 | 15480 | 16699 | 18344 | 17821 | 16489 | 17193 | 19612 | 20873 | 21691 | 20775 | 18971 | 20294 | 21573
4180 | 4180 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 4 | 11753 | 13157 | 14315 | 15175 | 15551 | 13589 | 14364 | 15291 | 16422 | 17828 | 17235 | 15970 | 16800 | 19015 | 20152 | 20805 | 19887 | 18410 | 19593 | 20789
4181 | 4181 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 5 | 11612 | 13377 | 14502 | 15427 | 15571 | 13298 | 14513 | 15307 | 16337 | 17577 | 16492 | 15342 | 16568 | 18562 | 19677 | 20089 | 18817 | 17978 | 19046 | 20119
4182 | 4182 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 6 | 11723 | 14265 | 15398 | 16452 | 16337 | 13251 | 15380 | 16001 | 16931 | 18064 | 16180 | 14888 | 17034 | 18781 | 19904 | 20115 | 18166 | 18264 | 19168 | 20125
4183 | 4183 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 7 | 11899 | 15369 | 16429 | 17610 | 17569 | 13376 | 16245 | 16906 | 17725 | 19016 | 16245 | 14675 | 17613 | 19281 | 20490 | 20750 | 17908 | 18723 | 19502 | 20442
4184 | 4184 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 8 | 12307 | 16054 | 17005 | 18561 | 18538 | 13757 | 16716 | 17473 | 18264 | 19883 | 17005 | 14973 | 17954 | 19677 | 21291 | 21477 | 18514 | 19035 | 19747 | 20775
4185 | 4185 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 9 | 12742 | 16377 | 17244 | 19287 | 19235 | 14179 | 16838 | 17712 | 18513 | 20610 | 17807 | 15363 | 18006 | 19817 | 22031 | 22188 | 19284 | 19072 | 19841 | 20888
4186 | 4186 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 10 | 13201 | 16783 | 17634 | 20121 | 19934 | 14683 | 17149 | 18234 | 19015 | 21398 | 18607 | 15968 | 18408 | 20412 | 23051 | 23079 | 20178 | 19527 | 20519 | 21545
4187 | 4187 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 11 | 13604 | 17117 | 17950 | 20790 | 20459 | 15096 | 17461 | 18676 | 19446 | 21998 | 19199 | 16477 | 18831 | 20928 | 23910 | 23778 | 20874 | 19990 | 21114 | 22124
4188 | 4188 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 12 | 13867 | 17336 | 18317 | 21346 | 20755 | 15372 | 17655 | 18956 | 19863 | 22337 | 19553 | 16806 | 19076 | 21408 | 24572 | 24173 | 21276 | 20263 | 21478 | 22630
4189 | 4189 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 13 | 13934 | 17546 | 18538 | 21688 | 20930 | 15442 | 17839 | 19195 | 20096 | 22548 | 19717 | 16897 | 19284 | 21644 | 24970 | 24394 | 21456 | 20479 | 21750 | 22868
4190 | 4190 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 14 | 14079 | 17737 | 18642 | 22007 | 21068 | 15585 | 17940 | 19378 | 20189 | 22682 | 19828 | 17024 | 19365 | 21715 | 25231 | 24493 | 21548 | 20542 | 21885 | 22923
4191 | 4191 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 15 | 14262 | 17987 | 18891 | 22309 | 21148 | 15799 | 18103 | 19613 | 20416 | 22743 | 19984 | 17238 | 19515 | 21921 | 25485 | 24525 | 21695 | 20688 | 22086 | 23117
4192 | 4192 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 16 | 14675 | 18403 | 19144 | 22581 | 21305 | 16211 | 18318 | 20181 | 20592 | 22836 | 20189 | 17594 | 19656 | 22028 | 25567 | 24530 | 21822 | 20805 | 22685 | 23190
4193 | 4193 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 17 | 15143 | 18714 | 19418 | 22825 | 21514 | 16786 | 18552 | 20482 | 20844 | 23016 | 20660 | 18211 | 19998 | 22300 | 25926 | 24788 | 22264 | 21172 | 22966 | 23473
4194 | 4194 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 18 | 15573 | 18902 | 19414 | 22962 | 21693 | 17363 | 18856 | 20689 | 20954 | 23421 | 21380 | 19080 | 20513 | 22558 | 26540 | 25360 | 23165 | 21771 | 23373 | 23813
4195 | 4195 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 19 | 15740 | 19062 | 19617 | 23112 | 21625 | 17644 | 19292 | 20956 | 21346 | 23634 | 21607 | 19639 | 21252 | 23211 | 27232 | 25945 | 23742 | 22652 | 24200 | 24614
4196 | 4196 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 20 | 15702 | 18831 | 19555 | 22832 | 21400 | 17709 | 19585 | 20972 | 21458 | 23627 | 21706 | 19954 | 21893 | 23782 | 27524 | 26375 | 24198 | 23447 | 24787 | 25332
4197 | 4197 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 21 | 15225 | 18118 | 19357 | 22373 | 20495 | 17359 | 19282 | 20484 | 21600 | 23061 | 21588 | 19991 | 21997 | 24357 | 27907 | 26321 | 24520 | 23745 | 24997 | 26144
4198 | 4198 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 22 | 14703 | 17259 | 18527 | 21375 | 19645 | 16914 | 18554 | 19795 | 21006 | 22439 | 21371 | 19781 | 21519 | 24029 | 27432 | 26004 | 24576 | 23400 | 24759 | 25988
4199 | 4199 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 23 | 13803 | 15928 | 17244 | 19817 | 18139 | 16014 | 17334 | 18503 | 19797 | 20982 | 20436 | 18951 | 20374 | 22925 | 26041 | 24655 | 23708 | 22320 | 23644 | 24961
4200 | 4200 | 175 | 6 | 24 | Summer | 6 | 23 | Summer | 24 | 13044 | 14884 | 16096 | 18419 | 16728 | 15233 | 16242 | 17456 | 18676 | 19547 | 19413 | 18208 | 19297 | 21833 | 24676 | 23256 | 22706 | 21240 | 22686 | 23899
4201 | 4201 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 1 | 12370 | 14329 | 15816 | 16650 | 15783 | 14476 | 15715 | 16998 | 18393 | 18384 | 18054 | 17367 | 19073 | 21657 | 22850 | 21820 | 20930 | 21193 | 22587 | 23784
4202 | 4202 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 2 | 12127 | 13947 | 15303 | 15949 | 15202 | 14154 | 15302 | 16489 | 17768 | 17722 | 17397 | 16934 | 18527 | 20899 | 21914 | 21037 | 20163 | 20574 | 21869 | 22954
4203 | 4203 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 3 | 12025 | 13731 | 14986 | 15510 | 14794 | 14014 | 15013 | 16185 | 17343 | 17204 | 16856 | 16671 | 18086 | 20327 | 21201 | 20367 | 19491 | 20043 | 21318 | 22300
4204 | 4204 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 4 | 12055 | 13705 | 14880 | 15290 | 14525 | 13962 | 14881 | 15974 | 17008 | 16689 | 16326 | 16338 | 17601 | 19666 | 20366 | 19518 | 18693 | 19370 | 20552 | 21457
4205 | 4205 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 5 | 12318 | 13898 | 15147 | 15335 | 14165 | 14146 | 14951 | 15949 | 16988 | 16016 | 15676 | 16154 | 17304 | 19243 | 19693 | 18481 | 17749 | 18840 | 19888 | 20824
4206 | 4206 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 6 | 13314 | 14846 | 16217 | 16155 | 14271 | 15063 | 15721 | 16627 | 17751 | 15797 | 15385 | 16701 | 17688 | 19541 | 19782 | 17879 | 17173 | 18994 | 19918 | 20920
4207 | 4207 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 7 | 14537 | 16121 | 17614 | 17628 | 14828 | 16155 | 16895 | 17683 | 18938 | 16149 | 15614 | 17544 | 18413 | 20373 | 20658 | 17857 | 17190 | 19547 | 20459 | 21628
4208 | 4208 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 8 | 15275 | 16939 | 18844 | 18872 | 15954 | 16879 | 17754 | 18519 | 20114 | 17212 | 16553 | 18177 | 19003 | 21454 | 21665 | 18736 | 18080 | 20057 | 21055 | 22683
4209 | 4209 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 9 | 15479 | 17323 | 19737 | 19716 | 16964 | 17139 | 18155 | 18943 | 20996 | 18191 | 17688 | 18393 | 19294 | 22334 | 22527 | 19668 | 19225 | 20296 | 21321 | 23560
4210 | 4210 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 10 | 15772 | 17779 | 20649 | 20482 | 17700 | 17507 | 18736 | 19504 | 21969 | 19053 | 18677 | 18860 | 19968 | 23424 | 23485 | 20628 | 20285 | 21044 | 22044 | 24701
4211 | 4211 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 11 | 15855 | 17946 | 21167 | 20834 | 18030 | 17652 | 19009 | 19755 | 22579 | 19479 | 19367 | 19110 | 20356 | 24123 | 24024 | 21150 | 21050 | 21483 | 22463 | 25456
4212 | 4212 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 12 | 15957 | 18214 | 21642 | 21051 | 18264 | 17764 | 19206 | 20093 | 23111 | 19754 | 19921 | 19269 | 20626 | 24702 | 24338 | 21475 | 21661 | 21768 | 22889 | 26070
4213 | 4213 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 13 | 16064 | 18398 | 21942 | 21187 | 18350 | 17908 | 19404 | 20290 | 23429 | 19876 | 20192 | 19438 | 20831 | 25058 | 24521 | 21605 | 21939 | 21997 | 23092 | 26454
4214 | 4214 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 14 | 16063 | 18404 | 22189 | 21254 | 18376 | 17933 | 19514 | 20312 | 23651 | 19913 | 20366 | 19451 | 20898 | 25252 | 24548 | 21626 | 22090 | 22057 | 23077 | 26632
4215 | 4215 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 15 | 16152 | 18575 | 22405 | 21256 | 18461 | 18010 | 19664 | 20461 | 23860 | 19984 | 20584 | 19524 | 21042 | 25425 | 24499 | 21687 | 22311 | 22173 | 23183 | 26793
4216 | 4216 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 16 | 16375 | 18811 | 22671 | 21412 | 18721 | 18215 | 20188 | 20640 | 24054 | 20188 | 20974 | 19668 | 21663 | 25511 | 24499 | 21812 | 22672 | 22750 | 23232 | 26828
4217 | 4217 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 17 | 16537 | 18973 | 22801 | 21515 | 19053 | 18342 | 20383 | 20789 | 24254 | 20546 | 21570 | 19900 | 21815 | 25760 | 24652 | 22150 | 23284 | 22929 | 23410 | 27102
4218 | 4218 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 18 | 16594 | 18868 | 22789 | 21572 | 19428 | 18540 | 20491 | 20796 | 24484 | 21129 | 22167 | 20288 | 22062 | 26266 | 25112 | 22942 | 24038 | 23246 | 23657 | 27698
4219 | 4219 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 19 | 16808 | 18976 | 22834 | 21399 | 19383 | 18887 | 20644 | 21061 | 24734 | 21216 | 22458 | 20898 | 22622 | 26839 | 25584 | 23426 | 24578 | 23995 | 24383 | 28408
4220 | 4220 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 20 | 16981 | 18874 | 22493 | 21117 | 19101 | 19158 | 20606 | 21088 | 24596 | 21194 | 22445 | 21467 | 22992 | 27055 | 25949 | 23830 | 24821 | 24569 | 25088 | 28763
4221 | 4221 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 21 | 16435 | 18642 | 21977 | 20143 | 18522 | 18792 | 20041 | 21119 | 24411 | 20956 | 22393 | 21471 | 22907 | 27346 | 25815 | 24076 | 25103 | 24743 | 25870 | 29288
4222 | 4222 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 22 | 15619 | 17790 | 20957 | 19260 | 18037 | 18033 | 19305 | 20465 | 23614 | 20683 | 21933 | 20937 | 22479 | 26821 | 25458 | 24095 | 24837 | 24484 | 25704 | 28927
4223 | 4223 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 23 | 14448 | 16513 | 19394 | 17764 | 17031 | 16805 | 17984 | 19235 | 22125 | 19741 | 20811 | 19775 | 21280 | 25411 | 24094 | 23228 | 23756 | 23347 | 24672 | 27577
4224 | 4224 | 176 | 6 | 25 | Summer | 6 | 24 | Summer | 24 | 13488 | 15411 | 18003 | 16367 | 16015 | 15733 | 16937 | 18097 | 20709 | 18719 | 19647 | 18697 | 20290 | 24055 | 22696 | 22236 | 22574 | 22401 | 23624 | 26230
4225 | 4225 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 1 | 12898 | 15100 | 16221 | 15416 | 15096 | 15143 | 16408 | 17774 | 18871 | 17414 | 18726 | 18341 | 19997 | 22189 | 21247 | 20463 | 21472 | 22251 | 23482 | 24358
4226 | 4226 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 2 | 12569 | 14602 | 15544 | 14847 | 14555 | 14747 | 15918 | 17171 | 18075 | 16779 | 18076 | 17825 | 19376 | 21272 | 20478 | 19712 | 20720 | 21542 | 22658 | 23371
4227 | 4227 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 3 | 12368 | 14286 | 15104 | 14437 | 14127 | 14458 | 15621 | 16757 | 17523 | 16248 | 17609 | 17442 | 18911 | 20569 | 19814 | 19040 | 20152 | 20994 | 21994 | 22580
4228 | 4228 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 4 | 12350 | 14217 | 14898 | 14191 | 13856 | 14359 | 15456 | 16480 | 17079 | 15762 | 17227 | 17027 | 18368 | 19778 | 19001 | 18269 | 19496 | 20241 | 21154 | 21597
4229 | 4229 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 5 | 12581 | 14505 | 14991 | 13876 | 13536 | 14500 | 15517 | 16547 | 16920 | 15194 | 17031 | 16802 | 17989 | 19188 | 18031 | 17372 | 18999 | 19625 | 20555 | 20791
4230 | 4230 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 6 | 13472 | 15580 | 15840 | 14009 | 13585 | 15316 | 16255 | 17392 | 17495 | 14966 | 17487 | 17255 | 18276 | 19332 | 17471 | 16815 | 19181 | 19673 | 20655 | 20733
4231 | 4231 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 7 | 14739 | 16934 | 17269 | 14528 | 14018 | 16448 | 17280 | 18579 | 18660 | 15171 | 18606 | 17998 | 18973 | 20167 | 17407 | 16771 | 20077 | 20140 | 21282 | 21432
4232 | 4232 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 8 | 15569 | 18027 | 18392 | 15518 | 14841 | 17180 | 17995 | 19644 | 19677 | 16008 | 19853 | 18520 | 19524 | 21053 | 18166 | 17518 | 21262 | 20601 | 22192 | 22282
4233 | 4233 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 9 | 15962 | 18813 | 19189 | 16446 | 15835 | 17500 | 18348 | 20459 | 20472 | 17077 | 20938 | 18725 | 19759 | 21833 | 19024 | 18577 | 22358 | 20789 | 22984 | 23088
4234 | 4234 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 10 | 16327 | 19601 | 19850 | 17082 | 16617 | 17957 | 18786 | 21341 | 21218 | 17960 | 22119 | 19219 | 20314 | 22676 | 19869 | 19545 | 23566 | 21403 | 24019 | 23986
4235 | 4235 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 11 | 16440 | 20064 | 20148 | 17348 | 17160 | 18161 | 18968 | 21884 | 21590 | 18594 | 22994 | 19490 | 20606 | 23156 | 20332 | 20253 | 24555 | 21770 | 24728 | 24526
4236 | 4236 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 12 | 16483 | 20475 | 20296 | 17499 | 17574 | 18284 | 19235 | 22327 | 21761 | 19071 | 23600 | 19690 | 20923 | 23397 | 20588 | 20777 | 25252 | 22130 | 25274 | 24797
4237 | 4237 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 13 | 16719 | 20853 | 20493 | 17664 | 17886 | 18541 | 19494 | 22723 | 22002 | 19405 | 24318 | 19950 | 21198 | 23641 | 20789 | 21135 | 26143 | 22398 | 25716 | 25066
4238 | 4238 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 14 | 16919 | 21182 | 20643 | 17785 | 18147 | 18735 | 19601 | 23045 | 22151 | 19665 | 24674 | 20067 | 21281 | 23756 | 20891 | 21381 | 26671 | 22459 | 25982 | 25182
4239 | 4239 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 15 | 17104 | 21400 | 20665 | 17876 | 18382 | 18905 | 19769 | 23262 | 22146 | 19904 | 24974 | 20194 | 21423 | 23726 | 20972 | 21611 | 27153 | 22585 | 26152 | 25141
4240 | 4240 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 16 | 17494 | 21678 | 20847 | 18151 | 18812 | 19439 | 19974 | 23484 | 22246 | 20321 | 25384 | 20487 | 21526 | 23755 | 21117 | 21985 | 27664 | 22646 | 26206 | 25132
4241 | 4241 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 17 | 17828 | 21887 | 21018 | 18575 | 19485 | 19723 | 20208 | 23768 | 22428 | 20992 | 25748 | 20758 | 21804 | 23995 | 21530 | 22695 | 28253 | 22906 | 26560 | 25384
4242 | 4242 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 18 | 18035 | 21913 | 21089 | 18992 | 19915 | 19914 | 20290 | 24013 | 22791 | 21653 | 26070 | 21091 | 22045 | 24528 | 22403 | 23532 | 28798 | 23235 | 27234 | 25976
4243 | 4243 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 19 | 18161 | 22027 | 20947 | 18986 | 20037 | 20105 | 20581 | 24257 | 22926 | 21931 | 25955 | 21676 | 22629 | 25008 | 22909 | 24095 | 28712 | 24016 | 28008 | 26621
4244 | 4244 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 20 | 17873 | 21653 | 20615 | 18663 | 19862 | 20030 | 20552 | 24050 | 22821 | 21822 | 25668 | 22102 | 23118 | 25313 | 23266 | 24312 | 28371 | 24709 | 28352 | 27057
4245 | 4245 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 21 | 17201 | 21175 | 19680 | 18123 | 19540 | 19491 | 20599 | 23857 | 22207 | 21774 | 25126 | 22252 | 23662 | 25187 | 23527 | 24641 | 27887 | 25549 | 28946 | 27164
4246 | 4246 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 22 | 16322 | 20137 | 18766 | 17600 | 18874 | 18699 | 19881 | 22986 | 21524 | 21257 | 24212 | 21751 | 23277 | 24767 | 23499 | 24333 | 27142 | 25350 | 28563 | 26913
4247 | 4247 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 23 | 15010 | 18611 | 17281 | 16598 | 17731 | 17374 | 18628 | 21474 | 20062 | 20128 | 22702 | 20578 | 22158 | 23399 | 22621 | 23228 | 25551 | 24312 | 27223 | 25603
4248 | 4248 | 177 | 6 | 26 | Summer | 6 | 25 | Summer | 24 | 13977 | 17228 | 15873 | 15591 | 16575 | 16325 | 17479 | 20042 | 18617 | 18958 | 21047 | 19511 | 21052 | 21983 | 21613 | 22056 | 23895 | 23259 | 25880 | 24194
4249 | 4249 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 1 | 13672 | 15755 | 15251 | 15012 | 16156 | 16045 | 17409 | 18479 | 17749 | 18289 | 18885 | 19511 | 21107 | 20843 | 20183 | 21250 | 21930 | 23367 | 24285 | 22902
4250 | 4250 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 2 | 13314 | 15095 | 14703 | 14477 | 15610 | 15566 | 16818 | 17705 | 17108 | 17667 | 18261 | 18905 | 20378 | 20095 | 19450 | 20508 | 21197 | 22556 | 23303 | 22084
4251 | 4251 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 3 | 13066 | 14629 | 14282 | 14031 | 15236 | 15259 | 16400 | 17147 | 16580 | 17193 | 17762 | 18438 | 19790 | 19424 | 18767 | 19934 | 20572 | 21875 | 22487 | 21338
4252 | 4252 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 4 | 13097 | 14497 | 14115 | 13836 | 15184 | 15194 | 16228 | 16825 | 16184 | 16914 | 17383 | 18017 | 19238 | 18719 | 18088 | 19365 | 19914 | 21108 | 21578 | 20449
4253 | 4253 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 5 | 13314 | 14616 | 13830 | 13551 | 15354 | 15312 | 16360 | 16751 | 15601 | 16768 | 17192 | 17721 | 18902 | 17807 | 17236 | 18908 | 19400 | 20533 | 20788 | 19329
4254 | 4254 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 6 | 14228 | 15435 | 13945 | 13581 | 16155 | 16050 | 17225 | 17369 | 15408 | 17258 | 17628 | 18035 | 19220 | 17249 | 16662 | 19070 | 19515 | 20596 | 20684 | 18569
4255 | 4255 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 7 | 15388 | 16861 | 14466 | 13986 | 17581 | 17079 | 18435 | 18551 | 15700 | 18421 | 18407 | 18744 | 19979 | 17191 | 16608 | 19928 | 19986 | 21194 | 21360 | 18384
4256 | 4256 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 8 | 16056 | 18008 | 15493 | 14816 | 18965 | 17824 | 19539 | 19626 | 16659 | 19736 | 19032 | 19345 | 20940 | 17972 | 17368 | 21140 | 20431 | 22112 | 22220 | 19149
4257 | 4257 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 9 | 16316 | 18709 | 16416 | 15776 | 20069 | 18137 | 20334 | 20392 | 17531 | 20798 | 19288 | 19556 | 21720 | 18792 | 18394 | 22196 | 20617 | 22869 | 22966 | 19970
4258 | 4258 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 10 | 16463 | 19167 | 16854 | 16350 | 20862 | 18360 | 21003 | 20934 | 18073 | 21788 | 19699 | 19902 | 22495 | 19430 | 19156 | 23207 | 21107 | 23703 | 23671 | 20682
4259 | 4259 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 11 | 16656 | 19540 | 17191 | 16969 | 21541 | 18600 | 21604 | 21384 | 18506 | 22747 | 20122 | 20267 | 23207 | 19958 | 19931 | 24273 | 21616 | 24482 | 24284 | 21274
4260 | 4260 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 12 | 16923 | 19796 | 17437 | 17500 | 21987 | 18959 | 22143 | 21665 | 18796 | 23455 | 20417 | 20691 | 23808 | 20310 | 20558 | 25087 | 21951 | 25130 | 24656 | 21661
4261 | 4261 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 13 | 17123 | 19926 | 17539 | 17737 | 22324 | 19154 | 22467 | 21831 | 18926 | 24117 | 20596 | 20892 | 24187 | 20448 | 20850 | 25899 | 22164 | 25501 | 24855 | 21812
4262 | 4262 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 14 | 17110 | 19954 | 17552 | 17888 | 22444 | 19155 | 22682 | 21877 | 18952 | 24362 | 20548 | 20871 | 24376 | 20447 | 20991 | 26314 | 22103 | 25646 | 24857 | 21807
4263 | 4263 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 15 | 17384 | 20063 | 17726 | 18205 | 22739 | 19411 | 22988 | 21960 | 19126 | 24761 | 20736 | 21105 | 24655 | 20613 | 21304 | 26881 | 22263 | 25908 | 24895 | 21969
4264 | 4264 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 16 | 17704 | 20315 | 18054 | 18700 | 23061 | 19679 | 23270 | 22141 | 19410 | 25244 | 21414 | 21280 | 24831 | 20818 | 21734 | 27450 | 22941 | 26011 | 24944 | 22150
4265 | 4265 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 17 | 17950 | 20464 | 18461 | 19333 | 23359 | 19908 | 23545 | 22271 | 19841 | 25615 | 21676 | 21523 | 25148 | 21231 | 22436 | 27997 | 23201 | 26357 | 25182 | 22571
4266 | 4266 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 18 | 17963 | 20524 | 18834 | 19745 | 23661 | 20010 | 23756 | 22599 | 20495 | 25892 | 21896 | 21764 | 25734 | 22113 | 23283 | 28555 | 23560 | 27056 | 25822 | 23525
4267 | 4267 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 19 | 18218 | 20457 | 18877 | 19939 | 23741 | 20359 | 24053 | 22761 | 20688 | 25775 | 22488 | 22383 | 26411 | 22669 | 23908 | 28532 | 24456 | 27911 | 26544 | 24205
4268 | 4268 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 20 | 18137 | 20145 | 18572 | 19786 | 23582 | 20354 | 23852 | 22627 | 20631 | 25487 | 22651 | 22837 | 26605 | 23015 | 24143 | 28220 | 24958 | 28318 | 27036 | 24685
4269 | 4269 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 21 | 17953 | 19178 | 17980 | 19427 | 22825 | 20320 | 23573 | 21920 | 20361 | 24839 | 22471 | 23287 | 26877 | 23193 | 24409 | 27697 | 25186 | 28880 | 27117 | 25088
4270 | 4270 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 22 | 17016 | 18192 | 17396 | 18697 | 21737 | 19517 | 22619 | 21124 | 19970 | 23841 | 21803 | 22790 | 26236 | 23078 | 24033 | 26899 | 24757 | 28437 | 26809 | 25125
4271 | 4271 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 23 | 15775 | 16748 | 16429 | 17600 | 20125 | 18281 | 21116 | 19671 | 19035 | 22321 | 20524 | 21672 | 24843 | 22218 | 22954 | 25333 | 23548 | 27119 | 25523 | 24330
4272 | 4272 | 178 | 6 | 27 | Summer | 6 | 26 | Summer | 24 | 14690 | 15385 | 15413 | 16466 | 18581 | 17121 | 19662 | 18211 | 18010 | 20635 | 19393 | 20551 | 23455 | 21210 | 21785 | 23670 | 22447 | 25770 | 24128 | 23346
4273 | 4273 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 1 | 14558 | 14687 | 14760 | 15942 | 15899 | 16937 | 18005 | 17256 | 16962 | 18908 | 19155 | 20481 | 21764 | 19728 | 20876 | 22382 | 22154 | 24078 | 22736 | 21617
4274 | 4274 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 2 | 14050 | 14110 | 14216 | 15376 | 15365 | 16335 | 17222 | 16603 | 16320 | 18133 | 18465 | 19737 | 20850 | 18974 | 20122 | 21471 | 21369 | 23077 | 21895 | 20798
4275 | 4275 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 3 | 13765 | 13745 | 13828 | 15051 | 15034 | 15977 | 16729 | 16139 | 15837 | 17564 | 17976 | 19221 | 20183 | 18357 | 19605 | 20744 | 20757 | 22314 | 21193 | 20108
4276 | 4276 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 4 | 13729 | 13550 | 13618 | 14978 | 14906 | 15808 | 16422 | 15761 | 15429 | 17080 | 17492 | 18693 | 19472 | 17685 | 19031 | 19907 | 19989 | 21384 | 20283 | 19277
4277 | 4277 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 5 | 14007 | 13311 | 13330 | 15159 | 15056 | 15968 | 16392 | 15236 | 14914 | 16584 | 17228 | 18423 | 18943 | 16856 | 18591 | 18969 | 19430 | 20595 | 19157 | 18265
4278 | 4278 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 6 | 15077 | 13462 | 13440 | 16043 | 15901 | 16931 | 17137 | 15176 | 14734 | 16629 | 17656 | 18876 | 19150 | 16377 | 18844 | 18574 | 19544 | 20561 | 18459 | 17636
4279 | 4279 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 7 | 16305 | 13894 | 13783 | 17414 | 16892 | 18076 | 18281 | 15458 | 14852 | 16901 | 18566 | 19620 | 19912 | 16260 | 19629 | 18557 | 20133 | 21150 | 18179 | 17450
4280 | 4280 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 8 | 17216 | 14750 | 14449 | 18631 | 17475 | 18989 | 19183 | 16264 | 15520 | 17464 | 19342 | 20435 | 20651 | 16840 | 20661 | 19000 | 20730 | 21817 | 18744 | 18051
4281 | 4281 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 9 | 17909 | 15624 | 15406 | 19692 | 17765 | 19745 | 19929 | 17124 | 16515 | 18334 | 19783 | 21194 | 21356 | 17831 | 21691 | 19867 | 21113 | 22525 | 19529 | 19071
4282 | 4282 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 10 | 18601 | 16158 | 16089 | 20599 | 18178 | 20513 | 20572 | 17772 | 17301 | 19142 | 20355 | 22074 | 22119 | 18694 | 22813 | 20789 | 21759 | 23343 | 20349 | 20002
4283 | 4283 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 11 | 19154 | 16518 | 16718 | 21289 | 18499 | 21115 | 21023 | 18209 | 18015 | 19825 | 20849 | 22783 | 22687 | 19474 | 23891 | 21576 | 22344 | 23967 | 20952 | 20831
4284 | 4284 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 12 | 19676 | 16764 | 17245 | 21740 | 18752 | 21651 | 21299 | 18502 | 18599 | 20283 | 21337 | 23386 | 23035 | 20098 | 24702 | 22105 | 22925 | 24339 | 21338 | 21485
4285 | 4285 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 13 | 20052 | 16918 | 17545 | 22125 | 18962 | 22033 | 21519 | 18683 | 18914 | 20568 | 21618 | 23806 | 23260 | 20454 | 25571 | 22407 | 23203 | 24596 | 21551 | 21861
4286 | 4286 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 14 | 20302 | 16962 | 17723 | 22265 | 18967 | 22281 | 21598 | 18728 | 19093 | 20645 | 21715 | 24019 | 23308 | 20626 | 26026 | 22449 | 23276 | 24627 | 21577 | 22031
4287 | 4287 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 15 | 20549 | 17088 | 17992 | 22518 | 19113 | 22539 | 21630 | 18855 | 19360 | 20826 | 21870 | 24255 | 23311 | 20894 | 26548 | 22611 | 23396 | 24615 | 21686 | 22302
4288 | 4288 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 16 | 20891 | 17453 | 18507 | 22862 | 19724 | 22861 | 21846 | 19170 | 19843 | 21186 | 22142 | 24466 | 23426 | 21353 | 27148 | 22902 | 23568 | 24690 | 21892 | 22754
4289 | 4289 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 17 | 21210 | 17947 | 19238 | 23284 | 20079 | 23236 | 22087 | 19709 | 20613 | 21628 | 22616 | 24892 | 23765 | 22161 | 27798 | 23436 | 24004 | 25034 | 22421 | 23581
4290 | 4290 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 18 | 21263 | 18331 | 19620 | 23586 | 20218 | 23462 | 22391 | 20339 | 21290 | 22254 | 23097 | 25468 | 24318 | 23035 | 28386 | 24214 | 24609 | 25706 | 23408 | 24497
4291 | 4291 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 19 | 21428 | 18295 | 19753 | 23583 | 20541 | 23700 | 22469 | 20430 | 21585 | 22702 | 23402 | 26038 | 24798 | 23596 | 28291 | 25014 | 25266 | 26389 | 24057 | 25163
4292 | 4292 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 20 | 21116 | 17971 | 19565 | 23386 | 20419 | 23464 | 22291 | 20297 | 21488 | 22597 | 23488 | 26155 | 25091 | 23782 | 27937 | 25311 | 25726 | 26874 | 24530 | 25422
4293 | 4293 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 21 | 20590 | 17354 | 19169 | 22587 | 19828 | 23132 | 21509 | 19941 | 21344 | 22219 | 23059 | 26327 | 24862 | 23986 | 27369 | 25404 | 25720 | 26934 | 24920 | 25795
4294 | 4294 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 22 | 19561 | 16817 | 18491 | 21552 | 18964 | 22195 | 20724 | 19568 | 20816 | 21784 | 22500 | 25700 | 24407 | 23642 | 26597 | 25241 | 25431 | 26669 | 25012 | 25558
4295 | 4295 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 23 | 18034 | 15834 | 17354 | 19919 | 17540 | 20647 | 19218 | 18582 | 19678 | 20710 | 21175 | 24248 | 23011 | 22524 | 24985 | 24253 | 24171 | 25338 | 24187 | 24449
4296 | 4296 | 179 | 6 | 28 | Summer | 6 | 27 | Summer | 24 | 16680 | 14874 | 16224 | 18410 | 16400 | 19218 | 17770 | 17560 | 18529 | 19566 | 19957 | 22868 | 21597 | 21369 | 23341 | 23134 | 22975 | 23967 | 23225 | 23284
4297 | 4297 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 1 | 15101 | 14211 | 15694 | 15694 | 16184 | 17517 | 16825 | 16555 | 17882 | 18608 | 19107 | 21130 | 20362 | 20464 | 21438 | 21809 | 22236 | 22568 | 21464 | 22287
4298 | 4298 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 2 | 14457 | 13706 | 15175 | 15104 | 15614 | 16775 | 16214 | 15950 | 17268 | 17963 | 18368 | 20252 | 19626 | 19743 | 20611 | 21051 | 21402 | 21759 | 20675 | 21510
4299 | 4299 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 3 | 14025 | 13333 | 14854 | 14774 | 15231 | 16293 | 15757 | 15475 | 16850 | 17490 | 17887 | 19603 | 18999 | 19204 | 20026 | 20440 | 20781 | 21050 | 19975 | 20932
4300 | 4300 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 4 | 13862 | 13132 | 14788 | 14642 | 15041 | 16021 | 15424 | 15110 | 16604 | 17059 | 17431 | 18953 | 18308 | 18682 | 19343 | 19699 | 20032 | 20150 | 19149 | 20239
4301 | 4301 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 5 | 13971 | 12866 | 14983 | 14767 | 15122 | 16038 | 14961 | 14646 | 16544 | 16862 | 17139 | 18497 | 17440 | 18281 | 18781 | 19169 | 19381 | 19041 | 18148 | 19671
4302 | 4302 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 6 | 14831 | 12961 | 15874 | 15589 | 15890 | 16810 | 14955 | 14529 | 17157 | 17346 | 17504 | 18784 | 16984 | 18529 | 18860 | 19312 | 19383 | 18345 | 17506 | 19793
4303 | 4303 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 7 | 16192 | 13348 | 17294 | 16783 | 17045 | 18012 | 15318 | 14738 | 18389 | 18343 | 18377 | 19650 | 16895 | 19365 | 19523 | 19965 | 20010 | 18095 | 17339 | 20539
4304 | 4304 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 8 | 17142 | 14034 | 18527 | 17800 | 17930 | 18922 | 16148 | 15441 | 19595 | 19167 | 19345 | 20425 | 17512 | 20433 | 20423 | 20583 | 20887 | 18661 | 17935 | 21573
4305 | 4305 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 9 | 17757 | 14958 | 19608 | 18532 | 18433 | 19654 | 17001 | 16452 | 20676 | 19618 | 20135 | 21138 | 18295 | 21456 | 21215 | 20958 | 21638 | 19428 | 18937 | 22595
4306 | 4306 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 10 | 18336 | 15650 | 20519 | 19139 | 18928 | 20284 | 17640 | 17230 | 21696 | 20190 | 20857 | 21883 | 19060 | 22638 | 22007 | 21601 | 22462 | 20250 | 19868 | 23778
4307 | 4307 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 11 | 18712 | 16268 | 21224 | 19679 | 19305 | 20720 | 18065 | 17933 | 22458 | 20674 | 21528 | 22433 | 19592 | 23674 | 22751 | 22176 | 23215 | 20852 | 20697 | 24898
4308 | 4308 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 12 | 19000 | 16797 | 21708 | 20089 | 19728 | 21012 | 18369 | 18522 | 22978 | 21173 | 22005 | 22787 | 19972 | 24439 | 23274 | 22760 | 23765 | 21254 | 21369 | 25754
4309 | 4309 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 13 | 19226 | 17120 | 22138 | 20492 | 20020 | 21250 | 18566 | 18868 | 23410 | 21476 | 22455 | 23052 | 20201 | 25213 | 23743 | 23074 | 24248 | 21485 | 21765 | 26678
4310 | 4310 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 14 | 19324 | 17344 | 22358 | 20740 | 20184 | 21380 | 18669 | 19104 | 23588 | 21631 | 22678 | 23158 | 20289 | 25529 | 23943 | 23206 | 24435 | 21567 | 21988 | 27175
4311 | 4311 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 15 | 19448 | 17675 | 22687 | 21034 | 20416 | 21477 | 18849 | 19434 | 23884 | 21849 | 22953 | 23232 | 20460 | 25937 | 24189 | 23393 | 24682 | 21727 | 22315 | 27762
4312 | 4312 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 16 | 19715 | 18179 | 23034 | 21380 | 20747 | 21682 | 19165 | 19920 | 24172 | 22122 | 23196 | 23354 | 20688 | 26384 | 24359 | 23574 | 24815 | 21919 | 22746 | 28343
4313 | 4313 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 17 | 19940 | 18876 | 23427 | 21785 | 21208 | 21901 | 19679 | 20660 | 24650 | 22575 | 23690 | 23665 | 21187 | 26880 | 24888 | 23987 | 25344 | 22431 | 23551 | 28992
4314 | 4314 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 18 | 19947 | 19158 | 23586 | 22122 | 21504 | 22114 | 20187 | 21222 | 25024 | 22953 | 24345 | 24107 | 22009 | 27349 | 25702 | 24520 | 26199 | 23351 | 24405 | 29556
4315 | 4315 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 19 | 19793 | 19241 | 23491 | 22166 | 21563 | 22132 | 20207 | 21435 | 25119 | 23158 | 24678 | 24489 | 22430 | 27373 | 26243 | 25107 | 26737 | 23961 | 25034 | 29493
4316 | 4316 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 20 | 19443 | 19001 | 23221 | 21922 | 21257 | 21918 | 20026 | 21259 | 25017 | 23139 | 24701 | 24680 | 22679 | 27273 | 26528 | 25504 | 27149 | 24424 | 25298 | 29169
4317 | 4317 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 21 | 18422 | 18564 | 22344 | 21089 | 20371 | 21052 | 19568 | 21016 | 24415 | 22597 | 24320 | 24325 | 22742 | 26867 | 26468 | 25420 | 27188 | 24768 | 25636 | 28682
4318 | 4318 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 22 | 17492 | 17875 | 21278 | 20136 | 19540 | 20220 | 19134 | 20435 | 23543 | 21975 | 23648 | 23807 | 22650 | 26083 | 25975 | 25089 | 26785 | 24839 | 25387 | 27973
4319 | 4319 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 23 | 16040 | 16768 | 19657 | 18633 | 18138 | 18720 | 18146 | 19303 | 21977 | 20640 | 22207 | 22402 | 21755 | 24570 | 24588 | 23837 | 25425 | 24002 | 24293 | 26411
4320 | 4320 | 180 | 6 | 29 | Summer | 6 | 28 | Summer | 24 | 14733 | 15649 | 18109 | 17223 | 16878 | 17258 | 17100 | 18129 | 20396 | 19390 | 20770 | 20956 | 20740 | 22894 | 23165 | 22628 | 24001 | 23017 | 23112 | 24758
4321 | 4321 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 1 | 14025 | 15074 | 15606 | 15904 | 15909 | 16316 | 16110 | 17418 | 17812 | 18474 | 19524 | 19713 | 19231 | 20886 | 21367 | 21815 | 22772 | 21228 | 22064 | 22812
4322 | 4322 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 2 | 13502 | 14577 | 15084 | 15344 | 15318 | 15722 | 15523 | 16821 | 17141 | 17760 | 18752 | 19001 | 18528 | 20157 | 20623 | 20994 | 21866 | 20448 | 21293 | 22025
4323 | 4323 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 3 | 13151 | 14271 | 14741 | 14986 | 14985 | 15286 | 15072 | 16438 | 16728 | 17312 | 18147 | 18413 | 17928 | 19584 | 20033 | 20400 | 21117 | 19761 | 20728 | 21382
4324 | 4324 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 4 | 12956 | 14211 | 14583 | 14808 | 14822 | 14989 | 14747 | 16232 | 16395 | 16916 | 17582 | 17774 | 17289 | 18917 | 19324 | 19673 | 20236 | 18947 | 20043 | 20547
4325 | 4325 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 5 | 12780 | 14447 | 14742 | 14950 | 14913 | 14608 | 14365 | 16257 | 16286 | 16732 | 17002 | 17012 | 16540 | 18484 | 18869 | 19091 | 19284 | 17997 | 19513 | 19915
4326 | 4326 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 6 | 12908 | 15390 | 15577 | 15746 | 15684 | 14645 | 14301 | 16939 | 16842 | 17180 | 16929 | 16639 | 16088 | 18679 | 19053 | 19124 | 18800 | 17364 | 19635 | 19902
4327 | 4327 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 7 | 13375 | 16803 | 16797 | 16929 | 16878 | 15026 | 14540 | 18239 | 17876 | 18112 | 17182 | 16621 | 16030 | 19443 | 19736 | 19769 | 18739 | 17185 | 20378 | 20509
4328 | 4328 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 8 | 14290 | 18084 | 17712 | 17864 | 17929 | 15895 | 15286 | 19519 | 18896 | 19148 | 17758 | 17308 | 16666 | 20183 | 20402 | 20698 | 19245 | 17807 | 21447 | 21178
4329 | 4329 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 9 | 15164 | 19204 | 18257 | 18433 | 18717 | 16798 | 16364 | 20686 | 19714 | 20015 | 18669 | 18161 | 17703 | 20651 | 20860 | 21508 | 20187 | 18862 | 22529 | 21637
4330 | 4330 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 10 | 15655 | 20050 | 18682 | 18862 | 19302 | 17375 | 17083 | 21638 | 20356 | 20681 | 19467 | 18857 | 18524 | 21234 | 21451 | 22271 | 21092 | 19743 | 23658 | 22272
4331 | 4331 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 11 | 16041 | 20764 | 19054 | 19242 | 19881 | 17792 | 17782 | 22403 | 21005 | 21344 | 20186 | 19391 | 19322 | 21795 | 22025 | 23037 | 21919 | 20577 | 24780 | 22895
4332 | 4332 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 12 | 16270 | 21242 | 19449 | 19632 | 20271 | 18069 | 18343 | 22886 | 21432 | 21791 | 20662 | 19736 | 19935 | 22342 | 22589 | 23552 | 22455 | 21225 | 25616 | 23486
4333 | 4333 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 13 | 16396 | 21649 | 19689 | 19875 | 20634 | 18221 | 18643 | 23266 | 21830 | 22200 | 20930 | 19917 | 20271 | 22611 | 22860 | 23986 | 22744 | 21577 | 26492 | 23764
4334 | 4334 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 14 | 16501 | 21886 | 19855 | 20039 | 20887 | 18318 | 18873 | 23438 | 22076 | 22429 | 21050 | 20008 | 20506 | 22746 | 22990 | 24175 | 22855 | 21793 | 26984 | 23887
4335 | 4335 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 15 | 16625 | 22165 | 20026 | 20209 | 21124 | 18431 | 19134 | 23676 | 22301 | 22643 | 21213 | 20121 | 20780 | 22868 | 23110 | 24364 | 23020 | 22051 | 27498 | 23997
4336 | 4336 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 16 | 16954 | 22526 | 20356 | 20537 | 21434 | 18740 | 19606 | 23956 | 22556 | 22882 | 21523 | 20353 | 21200 | 23049 | 23280 | 24495 | 23258 | 22463 | 28051 | 24141
4337 | 4337 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 17 | 17430 | 22947 | 20835 | 21022 | 21905 | 19277 | 20362 | 24446 | 23050 | 23401 | 22033 | 20873 | 21995 | 23537 | 23715 | 25034 | 23790 | 23289 | 28729 | 24628
4338 | 4338 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 18 | 17811 | 23102 | 21116 | 21369 | 22316 | 19831 | 20950 | 24833 | 23629 | 24083 | 22655 | 21710 | 22860 | 24093 | 24293 | 25948 | 24662 | 24203 | 29356 | 25260
4339 | 4339 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 19 | 17685 | 22907 | 21099 | 21378 | 22358 | 19779 | 21083 | 24854 | 23811 | 24295 | 23095 | 22040 | 23316 | 24507 | 24810 | 26430 | 25429 | 24794 | 29259 | 25815
4340 | 4340 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 20 | 17327 | 22552 | 20779 | 21039 | 22129 | 19572 | 20879 | 24702 | 23705 | 24219 | 23077 | 22222 | 23428 | 24799 | 25153 | 26814 | 25687 | 25065 | 28937 | 26252
4341 | 4341 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 21 | 16640 | 21625 | 19812 | 20102 | 21314 | 19051 | 20574 | 24021 | 23123 | 23731 | 22759 | 22191 | 23520 | 24581 | 25001 | 26801 | 25765 | 25384 | 28429 | 26265
4342 | 4342 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 22 | 16085 | 20549 | 18931 | 19235 | 20387 | 18584 | 19966 | 23104 | 22356 | 23004 | 22368 | 22019 | 23143 | 24177 | 24640 | 26342 | 25624 | 25126 | 27720 | 26029
4343 | 4343 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 23 | 15141 | 18939 | 17543 | 17845 | 18893 | 17594 | 18839 | 21523 | 20899 | 21553 | 21342 | 21100 | 22035 | 22916 | 23380 | 24978 | 24661 | 24042 | 26167 | 24829
4344 | 4344 | 181 | 6 | 30 | Summer | 6 | 29 | Summer | 24 | 14221 | 17430 | 16269 | 16589 | 17470 | 16550 | 17660 | 19927 | 19446 | 20105 | 20175 | 20077 | 20864 | 21688 | 22164 | 23569 | 23531 | 22861 | 24523 | 23636
4345 | 4345 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 1 | 13576 | 15789 | 16377 | 16647 | 16297 | 17372 | 17803 | 18227 | 17979 | 19270 | 19821 | 20456 | 19948 | 21512 | 21989 | 22397 | 21832 | 23039 | 23244 | 23414
4346 | 4346 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 2 | 13070 | 15154 | 15726 | 15981 | 15637 | 16665 | 17096 | 17506 | 17339 | 18511 | 19040 | 19651 | 19227 | 20668 | 21130 | 21526 | 20989 | 22151 | 22347 | 22522
4347 | 4347 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 3 | 12735 | 14704 | 15249 | 15492 | 15187 | 16151 | 16567 | 16958 | 16906 | 17915 | 18419 | 19004 | 18725 | 19980 | 20422 | 20802 | 20321 | 21404 | 21591 | 21760
4348 | 4348 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 4 | 12542 | 14418 | 14928 | 15151 | 14933 | 15757 | 16134 | 16478 | 16525 | 17323 | 17771 | 18293 | 18240 | 19162 | 19561 | 19904 | 19464 | 20448 | 20618 | 20773
4349 | 4349 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 5 | 12298 | 14252 | 14742 | 14948 | 14724 | 15491 | 15824 | 16145 | 16400 | 16833 | 17250 | 17675 | 17892 | 18424 | 18775 | 19076 | 18518 | 19557 | 19706 | 19850
4350 | 4350 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 6 | 12414 | 14326 | 14810 | 15044 | 15063 | 15497 | 15819 | 16088 | 16973 | 16644 | 16998 | 17320 | 18206 | 17942 | 18243 | 18502 | 17899 | 18919 | 19049 | 19184
4351 | 4351 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 7 | 12906 | 14850 | 15270 | 15509 | 15685 | 15867 | 16191 | 16367 | 18123 | 16831 | 17080 | 17371 | 19185 | 17877 | 18137 | 18362 | 17835 | 18735 | 18854 | 18985
4352 | 4352 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 8 | 13784 | 15824 | 16213 | 16384 | 16507 | 16864 | 17033 | 17183 | 19158 | 17573 | 17889 | 18185 | 20458 | 18520 | 18758 | 18974 | 18616 | 19326 | 19448 | 19574
4353 | 4353 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 9 | 14729 | 16826 | 17240 | 17344 | 17419 | 17863 | 17999 | 18139 | 19691 | 18494 | 18787 | 19075 | 21566 | 19386 | 19621 | 19832 | 19475 | 20186 | 20313 | 20447
4354 | 4354 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 10 | 15469 | 17727 | 18156 | 18257 | 18201 | 18819 | 18978 | 19136 | 20298 | 19525 | 19830 | 20138 | 22781 | 20476 | 20731 | 20950 | 20361 | 21327 | 21465 | 21605
4355 | 4355 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 11 | 16128 | 18357 | 18805 | 18906 | 18850 | 19511 | 19693 | 19869 | 20812 | 20290 | 20608 | 20937 | 23855 | 21300 | 21569 | 21794 | 21090 | 22197 | 22342 | 22488
4356 | 4356 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 12 | 16457 | 18683 | 19144 | 19248 | 19086 | 19877 | 20068 | 20253 | 21106 | 20695 | 21021 | 21365 | 24431 | 21743 | 22019 | 22248 | 21267 | 22659 | 22808 | 22956
4357 | 4357 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 13 | 16704 | 18816 | 19280 | 19389 | 19283 | 20023 | 20219 | 20409 | 21338 | 20860 | 21188 | 21537 | 25135 | 21918 | 22195 | 22426 | 21465 | 22840 | 22992 | 23144
4358 | 4358 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 14 | 16945 | 18963 | 19428 | 19541 | 19423 | 20175 | 20371 | 20563 | 21510 | 21009 | 21336 | 21685 | 25464 | 22059 | 22333 | 22561 | 21565 | 22974 | 23126 | 23281
4359 | 4359 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 15 | 17210 | 19167 | 19657 | 19773 | 19601 | 20401 | 20595 | 20786 | 21669 | 21227 | 21552 | 21898 | 25807 | 22263 | 22532 | 22757 | 21635 | 23166 | 23318 | 23472
4360 | 4360 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 16 | 17649 | 19495 | 20016 | 20201 | 19926 | 20864 | 21063 | 21273 | 21893 | 21763 | 22098 | 22448 | 26198 | 22829 | 23087 | 23294 | 21818 | 23696 | 23850 | 24004
4361 | 4361 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 17 | 18368 | 19945 | 20474 | 20670 | 20350 | 21335 | 21523 | 21695 | 22379 | 22259 | 22548 | 22964 | 26723 | 23356 | 23617 | 23828 | 22465 | 24234 | 24387 | 24547
4362 | 4362 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 18 | 18538 | 20091 | 20618 | 20777 | 20611 | 21504 | 21643 | 21887 | 22640 | 22443 | 22808 | 23263 | 27063 | 23698 | 23969 | 24204 | 23272 | 24620 | 24783 | 24953
4363 | 4363 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 19 | 18530 | 19916 | 20515 | 20705 | 20734 | 21471 | 21637 | 21917 | 22710 | 22584 | 23018 | 23476 | 26987 | 24014 | 24336 | 24610 | 23720 | 25068 | 25237 | 25412
4364 | 4364 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 20 | 18254 | 19616 | 20202 | 20473 | 20414 | 21218 | 21467 | 21778 | 22599 | 22558 | 23080 | 23598 | 26820 | 24272 | 24636 | 24952 | 24116 | 25444 | 25604 | 25776
4365 | 4365 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 21 | 17844 | 18945 | 19549 | 19848 | 19720 | 20664 | 20962 | 21335 | 22006 | 22267 | 22876 | 23475 | 26391 | 24292 | 24729 | 25087 | 24404 | 25645 | 25824 | 26005
4366 | 4366 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 22 | 17132 | 18368 | 18971 | 19285 | 19052 | 20149 | 20483 | 20896 | 21317 | 21917 | 22571 | 23222 | 25549 | 24120 | 24598 | 24986 | 24340 | 25596 | 25787 | 25975
4367 | 4367 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 23 | 16028 | 17365 | 17964 | 18279 | 17949 | 19141 | 19484 | 19898 | 19971 | 20963 | 21623 | 22287 | 24029 | 23224 | 23701 | 24106 | 23451 | 24744 | 24937 | 25125
4368 | 4368 | 182 | 7 | 1 | Summer | 6 | 30 | Summer | 24 | 14955 | 16401 | 16966 | 17269 | 16824 | 18013 | 18451 | 18883 | 18726 | 19947 | 20512 | 21176 | 22355 | 22239 | 22720 | 23131 | 22342 | 23782 | 23976 | 24158
4369 | 4369 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 1 | 15195 | 15147 | 15448 | 16108 | 16970 | 16669 | 17100 | 17586 | 18772 | 18238 | 18526 | 19501 | 21079 | 20955 | 22009 | 21532 | 22848 | 21942 | 22711 | 22962
4370 | 4370 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 2 | 14585 | 14616 | 14873 | 15462 | 16292 | 16088 | 16503 | 16968 | 18020 | 17544 | 17734 | 18804 | 20250 | 20153 | 21113 | 20707 | 21965 | 21176 | 21916 | 22084
4371 | 4371 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 3 | 14171 | 14294 | 14583 | 15034 | 15805 | 15756 | 16155 | 16568 | 17462 | 17051 | 17183 | 18334 | 19599 | 19614 | 20426 | 20062 | 21239 | 20633 | 21295 | 21469
4372 | 4372 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 4 | 13908 | 14160 | 14464 | 14805 | 15442 | 15621 | 15985 | 16241 | 16929 | 16543 | 16576 | 17898 | 18835 | 18967 | 19614 | 19235 | 20309 | 19957 | 20466 | 20652
4373 | 4373 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 5 | 13790 | 14304 | 14596 | 14633 | 15224 | 15720 | 16075 | 16187 | 16513 | 16038 | 16022 | 17618 | 18160 | 18471 | 18733 | 18336 | 19457 | 19431 | 19845 | 19959
4374 | 4374 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 6 | 13879 | 15142 | 15460 | 15007 | 15242 | 16529 | 16840 | 16826 | 16340 | 15834 | 15532 | 17995 | 17717 | 18619 | 18354 | 17744 | 18831 | 19608 | 19904 | 19925
4375 | 4375 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 7 | 14316 | 16349 | 16751 | 15583 | 15588 | 17939 | 18186 | 17946 | 16470 | 16000 | 15475 | 18957 | 17628 | 19363 | 18376 | 17628 | 18584 | 20421 | 20510 | 20570
4376 | 4376 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 8 | 15154 | 17320 | 17838 | 16281 | 16473 | 19236 | 19493 | 18876 | 17156 | 16796 | 16345 | 20124 | 18182 | 20330 | 18921 | 18287 | 19181 | 21467 | 21158 | 21511
4377 | 4377 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 9 | 16123 | 17864 | 18622 | 17140 | 17391 | 20350 | 20623 | 19368 | 18086 | 17643 | 17341 | 21185 | 19023 | 21101 | 19832 | 19092 | 20000 | 22470 | 21564 | 22297
4378 | 4378 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 10 | 16952 | 18338 | 19235 | 17870 | 18265 | 21310 | 21607 | 19923 | 19050 | 18373 | 18315 | 22347 | 20050 | 21887 | 20762 | 19924 | 21085 | 23632 | 22249 | 23138
4379 | 4379 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 11 | 17554 | 18764 | 19827 | 18517 | 18926 | 22098 | 22411 | 20433 | 19795 | 19002 | 19130 | 23422 | 20861 | 22678 | 21598 | 20652 | 21947 | 24802 | 22920 | 23989
4380 | 4380 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 12 | 18053 | 19143 | 20251 | 18947 | 19474 | 22603 | 22919 | 20922 | 20381 | 19330 | 19657 | 24190 | 21495 | 23214 | 22159 | 21024 | 22601 | 25674 | 23533 | 24571
4381 | 4381 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 13 | 18193 | 19377 | 20602 | 19162 | 19629 | 22971 | 23284 | 21170 | 20554 | 19526 | 19864 | 24908 | 21682 | 23632 | 22438 | 21239 | 22795 | 26540 | 23808 | 25014
4382 | 4382 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 14 | 18380 | 19624 | 20916 | 19356 | 19827 | 23219 | 23528 | 21396 | 20749 | 19688 | 20032 | 25285 | 21858 | 23902 | 22612 | 21394 | 22975 | 27103 | 24005 | 25267
4383 | 4383 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 15 | 18804 | 20053 | 21384 | 19778 | 20281 | 23702 | 24002 | 21796 | 21190 | 20024 | 20415 | 25878 | 22293 | 24341 | 23015 | 21707 | 23395 | 27857 | 24358 | 25705
4384 | 4384 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 16 | 19220 | 20425 | 21741 | 20188 | 20843 | 24032 | 24324 | 22114 | 21834 | 20364 | 20846 | 26367 | 22963 | 24536 | 23311 | 21985 | 24045 | 28452 | 24540 | 25847
4385 | 4385 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 17 | 19525 | 20804 | 22125 | 20514 | 21235 | 24432 | 24674 | 22509 | 22236 | 20811 | 21479 | 26791 | 23404 | 24992 | 23762 | 22526 | 24499 | 29038 | 24893 | 26320
4386 | 4386 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 18 | 19562 | 20879 | 22142 | 20640 | 21295 | 24490 | 24812 | 22661 | 22348 | 21354 | 22043 | 26990 | 23616 | 25589 | 24327 | 23221 | 24774 | 29341 | 25274 | 27016
4387 | 4387 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 19 | 19346 | 20719 | 22002 | 20646 | 21122 | 24334 | 24683 | 22592 | 22346 | 21366 | 22283 | 26772 | 23819 | 25886 | 24895 | 23559 | 25128 | 29127 | 25753 | 27435
4388 | 4388 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 20 | 19000 | 20279 | 21674 | 20273 | 20898 | 24104 | 24466 | 22388 | 22179 | 21327 | 22075 | 26519 | 23991 | 26137 | 25050 | 23903 | 25476 | 28864 | 26152 | 27806
4389 | 4389 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 21 | 18280 | 19280 | 20808 | 19483 | 20273 | 23323 | 23729 | 21661 | 21778 | 21068 | 22120 | 25966 | 23906 | 26007 | 25037 | 24092 | 25619 | 28345 | 26152 | 27880
4390 | 4390 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 22 | 17713 | 18388 | 19851 | 18819 | 19735 | 22331 | 22770 | 20944 | 21388 | 20731 | 21737 | 25101 | 23705 | 25481 | 24836 | 24013 | 25547 | 27628 | 25906 | 27495
4391 | 4391 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 23 | 16715 | 16996 | 18369 | 17733 | 18728 | 20730 | 21171 | 19586 | 20437 | 19767 | 20638 | 23576 | 22793 | 24093 | 23866 | 23127 | 24677 | 26051 | 24685 | 26145
4392 | 4392 | 183 | 7 | 2 | Summer | 7 | 1 | Summer | 24 | 15767 | 15757 | 16938 | 16609 | 17599 | 19145 | 19588 | 18322 | 19424 | 18671 | 19436 | 21893 | 21792 | 22661 | 22735 | 22020 | 23591 | 24390 | 23501 | 24737
4393 | 4393 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 1 | 14507 | 14848 | 15810 | 15500 | 15894 | 16428 | 17131 | 17418 | 18300 | 18021 | 18568 | 18601 | 20425 | 21470 | 21094 | 20828 | 21175 | 22484 | 22769 | 23546
4394 | 4394 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 2 | 14028 | 14320 | 15205 | 14931 | 15217 | 15899 | 16541 | 16749 | 17579 | 17267 | 17875 | 18075 | 19717 | 20624 | 20302 | 19968 | 20385 | 21708 | 21912 | 22618
4395 | 4395 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 3 | 13738 | 14017 | 14778 | 14540 | 14758 | 15550 | 16150 | 16359 | 17041 | 16724 | 17471 | 17652 | 19171 | 19935 | 19661 | 19303 | 19877 | 21084 | 21300 | 21845
4396 | 4396 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 4 | 13693 | 13928 | 14587 | 14310 | 14414 | 15388 | 15889 | 16093 | 16621 | 16182 | 17122 | 17240 | 18565 | 19187 | 18887 | 18494 | 19294 | 20292 | 20508 | 20920
4397 | 4397 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 5 | 13885 | 14060 | 14435 | 14079 | 14135 | 15486 | 15887 | 16030 | 16176 | 15677 | 17013 | 17013 | 18197 | 18354 | 18022 | 17726 | 18926 | 19694 | 19817 | 19879
4398 | 4398 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 6 | 14808 | 14924 | 14816 | 14141 | 13930 | 16258 | 16561 | 16641 | 16275 | 15228 | 17483 | 17425 | 18496 | 18004 | 17446 | 16991 | 19142 | 19745 | 19762 | 19334
4399 | 4399 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 7 | 16333 | 16273 | 15468 | 14626 | 14122 | 17322 | 17767 | 17767 | 16731 | 15263 | 18496 | 18095 | 19347 | 18105 | 17400 | 16738 | 20009 | 20412 | 20428 | 19314
4400 | 4400 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 8 | 17710 | 17390 | 16212 | 15549 | 15090 | 18011 | 18738 | 18886 | 17422 | 16201 | 19796 | 18514 | 20137 | 18690 | 18114 | 17553 | 21271 | 21091 | 21395 | 19881
4401 | 4401 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 9 | 18812 | 18226 | 17181 | 16466 | 16189 | 18410 | 19315 | 19803 | 18370 | 17290 | 20875 | 18766 | 20639 | 19673 | 19004 | 18616 | 22288 | 21574 | 22257 | 20895
4402 | 4402 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 10 | 19763 | 18915 | 17988 | 17151 | 17132 | 18949 | 19926 | 20562 | 19248 | 18340 | 21883 | 19366 | 21333 | 20664 | 19902 | 19742 | 23361 | 22321 | 23171 | 21954
4403 | 4403 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 11 | 20535 | 19482 | 18626 | 17664 | 17859 | 19365 | 20412 | 21235 | 19987 | 19144 | 22722 | 19856 | 21941 | 21493 | 20621 | 20629 | 24289 | 22979 | 24018 | 22842
4404 | 4404 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 12 | 21014 | 19867 | 19024 | 17914 | 18300 | 19634 | 20869 | 21671 | 20439 | 19635 | 23285 | 20158 | 22481 | 22022 | 20964 | 21165 | 24888 | 23568 | 24564 | 23412
4405 | 4405 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 13 | 21333 | 20147 | 19179 | 18027 | 18424 | 19783 | 21061 | 22005 | 20619 | 19788 | 23779 | 20366 | 22670 | 22242 | 21122 | 21327 | 25376 | 23782 | 24952 | 23661
4406 | 4406 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 14 | 21535 | 20349 | 19256 | 18084 | 18471 | 19782 | 21177 | 22205 | 20695 | 19853 | 24151 | 20456 | 22759 | 22287 | 21157 | 21362 | 25717 | 23850 | 25086 | 23714
4407 | 4407 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 15 | 21699 | 20432 | 19299 | 18046 | 18491 | 19795 | 21206 | 22286 | 20735 | 19864 | 24453 | 20508 | 22767 | 22319 | 21099 | 21363 | 26014 | 23838 | 25141 | 23744
4408 | 4408 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 16 | 22014 | 20725 | 19624 | 18342 | 18868 | 20331 | 21442 | 22509 | 21010 | 20214 | 24854 | 21114 | 22906 | 22541 | 21296 | 21676 | 26378 | 23931 | 25202 | 23939
4409 | 4409 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 17 | 22470 | 21184 | 19989 | 18867 | 19517 | 20674 | 21900 | 22984 | 21487 | 20901 | 25530 | 21451 | 23324 | 23057 | 21904 | 22362 | 27094 | 24349 | 25735 | 24465
4410 | 4410 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 18 | 22530 | 21363 | 20229 | 19340 | 20075 | 20772 | 22206 | 23460 | 21973 | 21625 | 26005 | 21760 | 23812 | 23794 | 22766 | 23266 | 27762 | 24906 | 26616 | 25287
4411 | 4411 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 19 | 22231 | 21312 | 20314 | 19203 | 20256 | 20987 | 22223 | 23577 | 22260 | 21901 | 26070 | 22302 | 24207 | 24427 | 23175 | 23872 | 27976 | 25503 | 27146 | 26067
4412 | 4412 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 20 | 21841 | 20986 | 19943 | 19001 | 19830 | 20842 | 22015 | 23358 | 22075 | 21652 | 25575 | 22631 | 24423 | 24560 | 23515 | 23932 | 27788 | 25939 | 27559 | 26323
4413 | 4413 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 21 | 20913 | 20107 | 19144 | 18415 | 19562 | 20284 | 21252 | 22722 | 21579 | 21649 | 24848 | 22497 | 24148 | 24522 | 23679 | 24302 | 27395 | 25935 | 27648 | 26490
4414 | 4414 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 22 | 19840 | 19155 | 18471 | 17869 | 18980 | 19454 | 20498 | 21908 | 21104 | 21222 | 23968 | 22008 | 23707 | 24285 | 23573 | 24088 | 26699 | 25681 | 27262 | 26396
4415 | 4415 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 23 | 18242 | 17687 | 17395 | 16883 | 17846 | 18068 | 19118 | 20435 | 20061 | 20113 | 22358 | 20787 | 22413 | 23313 | 22683 | 23005 | 25099 | 24462 | 25923 | 25440
4416 | 4416 | 184 | 7 | 3 | Summer | 7 | 2 | Summer | 24 | 16812 | 16327 | 16290 | 15853 | 16701 | 16932 | 17866 | 19002 | 18915 | 18920 | 20798 | 19794 | 21210 | 22193 | 21580 | 21797 | 23502 | 23282 | 24537 | 24323
4417 | 4417 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 1 | 14469 | 15185 | 15193 | 15648 | 15946 | 16635 | 16917 | 17764 | 17576 | 18036 | 19525 | 19695 | 20378 | 20556 | 20417 | 20801 | 22523 | 22517 | 23321 | 22524
4418 | 4418 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 2 | 13985 | 14603 | 14649 | 14986 | 15371 | 16063 | 16271 | 17068 | 16931 | 17368 | 18799 | 19045 | 19609 | 19787 | 19577 | 20038 | 21672 | 21673 | 22398 | 21684
4419 | 4419 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 3 | 13656 | 14199 | 14272 | 14536 | 15040 | 15687 | 15902 | 16554 | 16452 | 16987 | 18270 | 18534 | 19079 | 19167 | 18926 | 19541 | 21014 | 21064 | 21635 | 20993
4420 | 4420 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 4 | 13553 | 14022 | 14064 | 14213 | 14945 | 15467 | 15684 | 16196 | 16022 | 16686 | 17794 | 18048 | 18502 | 18440 | 18152 | 18988 | 20263 | 20290 | 20726 | 20098
4421 | 4421 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 5 | 13707 | 13882 | 13864 | 13963 | 15119 | 15520 | 15684 | 15830 | 15595 | 16636 | 17582 | 17753 | 18070 | 17639 | 17429 | 18655 | 19743 | 19627 | 19710 | 19096
4422 | 4422 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 6 | 14535 | 14278 | 13959 | 13781 | 15890 | 16244 | 16360 | 16009 | 15448 | 17167 | 18005 | 18119 | 18268 | 17119 | 16734 | 18889 | 19830 | 19592 | 19178 | 18393
4423 | 4423 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 7 | 15821 | 14993 | 14525 | 14032 | 17198 | 17527 | 17581 | 16575 | 15753 | 18280 | 18671 | 19001 | 19151 | 17153 | 16548 | 19805 | 20198 | 20307 | 19203 | 18315
4424 | 4424 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 8 | 17040 | 15976 | 15708 | 15224 | 18746 | 18739 | 18950 | 17506 | 16829 | 19847 | 19387 | 19903 | 20375 | 18105 | 17597 | 21272 | 20806 | 21489 | 19983 | 19262
4425 | 4425 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 9 | 17871 | 17127 | 16860 | 16532 | 19998 | 19517 | 20070 | 18685 | 17966 | 21143 | 19981 | 20560 | 21433 | 19197 | 18867 | 22490 | 21374 | 22541 | 21190 | 20362
4426 | 4426 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 10 | 18389 | 17893 | 17514 | 17444 | 20940 | 20083 | 20790 | 19526 | 18727 | 22117 | 20659 | 21184 | 22259 | 20057 | 19960 | 23535 | 22132 | 23435 | 22214 | 21290
4427 | 4427 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 11 | 18840 | 18548 | 18055 | 18185 | 21670 | 20585 | 21480 | 20273 | 19362 | 22978 | 21218 | 21744 | 23066 | 20796 | 20869 | 24480 | 22784 | 24313 | 23128 | 22099
4428 | 4428 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 12 | 19132 | 18926 | 18283 | 18607 | 22112 | 21010 | 21885 | 20706 | 19641 | 23514 | 21536 | 22216 | 23553 | 21112 | 21385 | 25062 | 23156 | 24832 | 23686 | 22450
4429 | 4429 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 13 | 19240 | 19008 | 18324 | 18673 | 22400 | 21124 | 22142 | 20824 | 19708 | 23937 | 21674 | 22341 | 23847 | 21201 | 21478 | 25490 | 23313 | 25149 | 23859 | 22553
4430 | 4430 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 14 | 19611 | 19335 | 18616 | 18963 | 22821 | 21474 | 22569 | 21144 | 19997 | 24553 | 21779 | 22713 | 24232 | 21486 | 21762 | 26084 | 23382 | 25525 | 24157 | 22824
4431 | 4431 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 15 | 19674 | 19376 | 18578 | 18982 | 22956 | 21507 | 22663 | 21181 | 19954 | 24862 | 21767 | 22726 | 24307 | 21429 | 21764 | 26377 | 23345 | 25584 | 24175 | 22766
4432 | 4432 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 16 | 19712 | 19442 | 18627 | 19114 | 22999 | 21511 | 22655 | 21228 | 19961 | 25027 | 22149 | 22683 | 24181 | 21388 | 21833 | 26500 | 23722 | 25399 | 24120 | 22708
4433 | 4433 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 17 | 19973 | 19662 | 18980 | 19596 | 23332 | 21815 | 22973 | 21539 | 20289 | 25526 | 22422 | 22976 | 24519 | 21827 | 22346 | 27055 | 23977 | 25770 | 24489 | 23176
4434 | 4434 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 18 | 20083 | 19724 | 19245 | 19972 | 23354 | 21987 | 23284 | 21809 | 20822 | 25848 | 22413 | 23238 | 25146 | 22539 | 23106 | 27576 | 24153 | 26515 | 25163 | 23965
4435 | 4435 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 19 | 19939 | 19681 | 18979 | 20048 | 23322 | 21884 | 23246 | 21962 | 20807 | 25752 | 22887 | 23591 | 25411 | 22818 | 23591 | 27686 | 24932 | 26940 | 25855 | 24354
4436 | 4436 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 20 | 19491 | 19258 | 18717 | 19578 | 22943 | 21619 | 22963 | 21680 | 20720 | 25143 | 22878 | 23778 | 25619 | 23082 | 23591 | 27448 | 25192 | 27333 | 26087 | 24725
4437 | 4437 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 21 | 18500 | 18459 | 18094 | 19282 | 22128 | 20783 | 22261 | 21100 | 20407 | 24351 | 22501 | 23454 | 25436 | 23181 | 23916 | 27020 | 25221 | 27409 | 26242 | 25033
4438 | 4438 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 22 | 17582 | 17792 | 17532 | 18678 | 21101 | 19987 | 21401 | 20570 | 20015 | 23444 | 21942 | 22965 | 24859 | 23033 | 23675 | 26290 | 24866 | 27003 | 26141 | 25020
4439 | 4439 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 23 | 16212 | 16750 | 16563 | 17571 | 19567 | 18624 | 19922 | 19531 | 19056 | 21831 | 20628 | 21673 | 23468 | 22144 | 22598 | 24716 | 23616 | 25666 | 25205 | 24173
4440 | 4440 | 185 | 7 | 4 | Summer | 7 | 3 | Summer | 24 | 15017 | 15648 | 15517 | 16428 | 18040 | 17362 | 18480 | 18355 | 17974 | 20257 | 19441 | 20464 | 22048 | 21034 | 21378 | 23106 | 22449 | 24266 | 24079 | 23050
4441 | 4441 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 1 | 13994 | 14536 | 15291 | 15601 | 16445 | 16318 | 17165 | 16963 | 17310 | 18849 | 18620 | 19618 | 20747 | 19863 | 20304 | 22015 | 21724 | 22979 | 22229 | 21603
4442 | 4442 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 2 | 13490 | 13982 | 14633 | 15018 | 15817 | 15671 | 16472 | 16319 | 16571 | 18128 | 18020 | 18863 | 19898 | 19014 | 19531 | 21159 | 21011 | 22048 | 21377 | 20679
4443 | 4443 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 3 | 13204 | 13614 | 14194 | 14697 | 15416 | 15321 | 15981 | 15865 | 16054 | 17626 | 17545 | 18368 | 19235 | 18389 | 19058 | 20527 | 20403 | 21288 | 20683 | 19987
4444 | 4444 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 4 | 13132 | 13407 | 13880 | 14609 | 15215 | 15133 | 15664 | 15482 | 15559 | 17196 | 17122 | 17847 | 18554 | 17643 | 18527 | 19798 | 19696 | 20381 | 19785 | 19099
4445 | 4445 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 5 | 13274 | 13207 | 13639 | 14792 | 15354 | 15167 | 15350 | 15107 | 15104 | 17042 | 16916 | 17477 | 17789 | 16953 | 18217 | 19305 | 19120 | 19391 | 18795 | 18260
4446 | 4446 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 6 | 14176 | 13344 | 13508 | 15608 | 16130 | 15905 | 15619 | 15055 | 14728 | 17557 | 17303 | 17777 | 17531 | 16323 | 18508 | 19444 | 19161 | 18898 | 18124 | 17484
4447 | 4447 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 7 | 15589 | 13927 | 13798 | 16940 | 17069 | 17164 | 16245 | 15436 | 14855 | 18298 | 18119 | 18726 | 17728 | 16173 | 19443 | 19827 | 19735 | 18935 | 18051 | 17250
4448 | 4448 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 8 | 16733 | 14941 | 14830 | 18310 | 17739 | 18343 | 17007 | 16369 | 15846 | 18868 | 18795 | 19802 | 18358 | 17042 | 20740 | 20262 | 20270 | 19528 | 18801 | 18129
4449 | 4449 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 9 | 17516 | 15862 | 15959 | 19339 | 18191 | 19244 | 17979 | 17313 | 16927 | 19279 | 19214 | 20650 | 19334 | 18098 | 21756 | 20621 | 20647 | 20510 | 19682 | 19199
4450 | 4450 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 10 | 18196 | 16521 | 16891 | 20293 | 18769 | 19962 | 18826 | 18083 | 17954 | 19965 | 19815 | 21480 | 20307 | 19202 | 22814 | 21393 | 21337 | 21550 | 20625 | 20360
4451 | 4451 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 11 | 18783 | 17038 | 17626 | 21021 | 19195 | 20635 | 19557 | 18709 | 18782 | 20505 | 20321 | 22273 | 21150 | 20105 | 23755 | 22037 | 21944 | 22462 | 21428 | 21314
4452 | 4452 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 12 | 19098 | 17234 | 17998 | 21410 | 19425 | 20991 | 19933 | 18931 | 19206 | 20786 | 20742 | 22703 | 21617 | 20571 | 24283 | 22371 | 22464 | 22964 | 21731 | 21807
4453 | 4453 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 13 | 19435 | 17380 | 18185 | 21823 | 19669 | 21357 | 20165 | 19117 | 19420 | 21043 | 20995 | 23117 | 21900 | 20788 | 24838 | 22647 | 22752 | 23255 | 21956 | 22033
4454 | 4454 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 14 | 19584 | 17368 | 18171 | 21948 | 19495 | 21485 | 20180 | 19104 | 19416 | 20847 | 21101 | 23216 | 21909 | 20770 | 25132 | 22429 | 22865 | 23246 | 21922 | 22015
4455 | 4455 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 15 | 19734 | 17416 | 18253 | 22148 | 19563 | 21646 | 20281 | 19133 | 19503 | 20900 | 21173 | 23358 | 22009 | 20840 | 25496 | 22454 | 22938 | 23328 | 21928 | 22081
4456 | 4456 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 16 | 19980 | 17666 | 18584 | 22407 | 20039 | 21850 | 20534 | 19355 | 19809 | 21475 | 21412 | 23453 | 22192 | 21118 | 25825 | 23033 | 23110 | 23470 | 22070 | 22353
4457 | 4457 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 17 | 20359 | 18077 | 19125 | 22828 | 20315 | 22240 | 20909 | 19761 | 20400 | 21811 | 21718 | 23886 | 22613 | 21705 | 26458 | 23392 | 23498 | 23920 | 22616 | 22978
4458 | 4458 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 18 | 20405 | 18330 | 19462 | 22865 | 20270 | 22554 | 21162 | 20279 | 20990 | 21801 | 21995 | 24491 | 23210 | 22492 | 27006 | 23589 | 23859 | 24626 | 23442 | 23811
4459 | 4459 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 19 | 20416 | 18217 | 19668 | 22947 | 20675 | 22664 | 21434 | 20355 | 21296 | 22371 | 22453 | 24863 | 23874 | 23104 | 27241 | 24498 | 24614 | 25474 | 23988 | 24518
4460 | 4460 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 20 | 20086 | 17943 | 19205 | 22567 | 20428 | 22396 | 21152 | 20237 | 21006 | 22320 | 22565 | 25023 | 23954 | 23097 | 27003 | 24748 | 25064 | 25742 | 24395 | 24577
4461 | 4461 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 21 | 19188 | 17339 | 18911 | 21758 | 19656 | 21670 | 20537 | 19874 | 20933 | 21885 | 22166 | 24765 | 23828 | 23392 | 26559 | 24752 | 25054 | 25909 | 24722 | 25048
4462 | 4462 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 22 | 18248 | 16770 | 18297 | 20728 | 18894 | 20773 | 19957 | 19439 | 20483 | 21277 | 21703 | 24150 | 23564 | 23116 | 25800 | 24385 | 24878 | 25790 | 24701 | 24882
4463 | 4463 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 23 | 16808 | 15805 | 17191 | 19206 | 17506 | 19287 | 18899 | 18467 | 19391 | 19948 | 20474 | 22737 | 22586 | 22028 | 24214 | 23136 | 23730 | 24847 | 23852 | 23820
4464 | 4464 | 186 | 7 | 5 | Summer | 7 | 4 | Summer | 24 | 15497 | 14805 | 16046 | 17702 | 16342 | 17865 | 17740 | 17379 | 18202 | 18772 | 19286 | 21314 | 21452 | 20820 | 22613 | 21984 | 22528 | 23732 | 22746 | 22604
4465 | 4465 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 1 | 14602 | 14912 | 15538 | 16379 | 15694 | 16853 | 16687 | 17091 | 17556 | 18207 | 18795 | 20298 | 20083 | 20055 | 21784 | 21519 | 22063 | 22194 | 21602 | 21768
4466 | 4466 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 2 | 14021 | 14271 | 14973 | 15754 | 15205 | 16175 | 16056 | 16362 | 16892 | 17625 | 18210 | 19478 | 19313 | 19296 | 20944 | 20810 | 21359 | 21343 | 20688 | 20954
4467 | 4467 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 3 | 13631 | 13831 | 14662 | 15361 | 14860 | 15701 | 15620 | 15860 | 16532 | 17177 | 17780 | 18845 | 18714 | 18832 | 20313 | 20214 | 20779 | 20664 | 19998 | 20425
4468 | 4468 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 4 | 13460 | 13551 | 14590 | 15179 | 14731 | 15424 | 15287 | 15409 | 16271 | 16813 | 17358 | 18213 | 18030 | 18337 | 19621 | 19536 | 20052 | 19786 | 19115 | 19790
4469 | 4469 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 5 | 13319 | 13319 | 14784 | 15342 | 14845 | 15148 | 14969 | 15006 | 16265 | 16670 | 17125 | 17520 | 17282 | 18063 | 19164 | 18996 | 19495 | 18808 | 18286 | 19362
4470 | 4470 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 6 | 13733 | 13175 | 15607 | 16134 | 15530 | 15434 | 14961 | 14683 | 16858 | 17107 | 17334 | 17332 | 16833 | 18369 | 19316 | 19056 | 19380 | 18131 | 17492 | 19533
4471 | 4471 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 7 | 14327 | 13346 | 16832 | 16974 | 16507 | 15943 | 15255 | 14735 | 17878 | 17843 | 17930 | 17462 | 16787 | 19187 | 19593 | 19525 | 19691 | 17924 | 17115 | 20295
4472 | 4472 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 8 | 14986 | 14265 | 18081 | 17544 | 17183 | 16575 | 16065 | 15632 | 19130 | 18424 | 18643 | 17998 | 17429 | 20355 | 19911 | 19952 | 20289 | 18530 | 17851 | 21481
4473 | 4473 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 9 | 15818 | 15311 | 19071 | 17927 | 17569 | 17460 | 16949 | 16663 | 20148 | 18789 | 19252 | 18901 | 18253 | 21297 | 20206 | 20261 | 20923 | 19337 | 18841 | 22415
4474 | 4474 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 10 | 16487 | 16100 | 19898 | 18367 | 17930 | 18171 | 17568 | 17554 | 21007 | 19257 | 19830 | 19729 | 18988 | 22222 | 20845 | 20818 | 21602 | 20142 | 19872 | 23400
4475 | 4475 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 11 | 17053 | 16724 | 20541 | 18693 | 18233 | 18808 | 18093 | 18285 | 21775 | 19667 | 20382 | 20481 | 19631 | 23075 | 21399 | 21330 | 22262 | 20852 | 20744 | 24308
4476 | 4476 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 12 | 17503 | 17218 | 21070 | 19053 | 18675 | 19306 | 18451 | 18838 | 22390 | 20219 | 20816 | 21062 | 20045 | 23739 | 21870 | 21978 | 22773 | 21287 | 21374 | 24993
4477 | 4477 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 13 | 17711 | 17414 | 21496 | 19296 | 18919 | 19548 | 18641 | 19051 | 22949 | 20482 | 21140 | 21346 | 20265 | 24302 | 22157 | 22265 | 23117 | 21518 | 21610 | 25559
4478 | 4478 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 14 | 17834 | 17503 | 21728 | 19208 | 19112 | 19658 | 18723 | 19136 | 23362 | 20685 | 21361 | 21446 | 20350 | 24695 | 22037 | 22465 | 23304 | 21585 | 21680 | 25944
4479 | 4479 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 15 | 18010 | 17640 | 22016 | 19347 | 19250 | 19832 | 18817 | 19291 | 23809 | 20831 | 21575 | 21621 | 20427 | 25134 | 22138 | 22601 | 23494 | 21655 | 21816 | 26393
4480 | 4480 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 16 | 18381 | 18095 | 22397 | 19914 | 19654 | 20208 | 19161 | 19721 | 24288 | 21200 | 21797 | 21933 | 20709 | 25578 | 22838 | 22903 | 23609 | 21907 | 22197 | 26833
4481 | 4481 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 17 | 18728 | 18667 | 22862 | 20252 | 20062 | 20640 | 19619 | 20360 | 24913 | 21561 | 22353 | 22413 | 21278 | 26260 | 23251 | 23346 | 24142 | 22504 | 22874 | 27536
4482 | 4482 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 18 | 18896 | 19055 | 22903 | 20291 | 20302 | 20953 | 20167 | 20979 | 25321 | 21891 | 23171 | 23050 | 22070 | 26873 | 23505 | 23771 | 25178 | 23396 | 23784 | 28222
4483 | 4483 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 19 | 18993 | 19278 | 22989 | 20698 | 20454 | 21219 | 20255 | 21266 | 25343 | 22311 | 23548 | 23673 | 22493 | 27110 | 24411 | 24524 | 25845 | 23986 | 24523 | 28546
4484 | 4484 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 20 | 18578 | 18779 | 22548 | 20398 | 20247 | 20905 | 20088 | 20912 | 24728 | 22313 | 23634 | 23668 | 22707 | 26825 | 24613 | 24924 | 26250 | 24392 | 24583 | 28335
4485 | 4485 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 21 | 17794 | 18447 | 21693 | 19604 | 19414 | 20222 | 19623 | 20785 | 23875 | 21800 | 23438 | 23465 | 22749 | 26313 | 24548 | 24874 | 26482 | 24685 | 25031 | 28001
4486 | 4486 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 22 | 17121 | 17826 | 20648 | 18795 | 18675 | 19609 | 19153 | 20276 | 22920 | 21290 | 22842 | 23129 | 22558 | 25530 | 24154 | 24659 | 26117 | 24657 | 24865 | 27313
4487 | 4487 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 23 | 16074 | 16714 | 19105 | 17398 | 17390 | 18529 | 18157 | 19144 | 21280 | 20031 | 21616 | 22102 | 21638 | 23930 | 22880 | 23489 | 24955 | 23788 | 23793 | 25714
4488 | 4488 | 187 | 7 | 6 | Summer | 7 | 5 | Summer | 24 | 15024 | 15601 | 17592 | 16241 | 16215 | 17379 | 17063 | 17943 | 19714 | 18836 | 20406 | 20961 | 20525 | 22337 | 21716 | 22282 | 23753 | 22679 | 22586 | 24092
4489 | 4489 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 1 | 14121 | 14996 | 16122 | 15442 | 15558 | 16230 | 16715 | 17168 | 18397 | 18184 | 19183 | 19494 | 19586 | 21306 | 21093 | 21661 | 22486 | 21416 | 21604 | 23224
4490 | 4490 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 2 | 13591 | 14475 | 15532 | 14972 | 15108 | 15629 | 16015 | 16532 | 17727 | 17636 | 18468 | 18760 | 18770 | 20492 | 20411 | 20979 | 21664 | 20527 | 20802 | 22352
4491 | 4491 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 3 | 13229 | 14171 | 15146 | 14634 | 14820 | 15205 | 15525 | 16184 | 17248 | 17230 | 17919 | 18183 | 18150 | 19875 | 19828 | 20412 | 20968 | 19834 | 20272 | 21660
4492 | 4492 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 4 | 13032 | 14096 | 14984 | 14529 | 14696 | 14912 | 15115 | 15968 | 16877 | 16875 | 17431 | 17561 | 17448 | 19226 | 19187 | 19720 | 20158 | 18974 | 19647 | 20846
4493 | 4493 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 5 | 12846 | 14317 | 15172 | 14678 | 14830 | 14651 | 14768 | 16020 | 16789 | 16731 | 17183 | 16884 | 16809 | 18820 | 18698 | 19203 | 19537 | 18162 | 19233 | 20256
4494 | 4494 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 6 | 12962 | 15158 | 15976 | 15389 | 15409 | 14689 | 14505 | 16679 | 17336 | 17030 | 17474 | 16507 | 16199 | 19024 | 18801 | 19117 | 19444 | 17381 | 19412 | 20280
4495 | 4495 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 7 | 13478 | 16458 | 16908 | 16449 | 16313 | 15065 | 14657 | 17809 | 18042 | 17749 | 18220 | 16582 | 16001 | 19391 | 19368 | 19505 | 19958 | 17063 | 20226 | 20541
4496 | 4496 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 8 | 14368 | 17680 | 17497 | 17123 | 17095 | 15851 | 15539 | 19074 | 18518 | 18471 | 19137 | 17243 | 16751 | 19715 | 19798 | 20101 | 20815 | 17775 | 21388 | 20822
4497 | 4497 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 9 | 15195 | 18677 | 17919 | 17524 | 17723 | 16738 | 16593 | 20129 | 18876 | 19109 | 19964 | 18085 | 17749 | 20030 | 20135 | 20739 | 21624 | 18775 | 22334 | 21121
4498 | 4498 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 10 | 15746 | 19509 | 18395 | 17900 | 18231 | 17365 | 17497 | 21005 | 19452 | 19707 | 20717 | 18835 | 18749 | 20688 | 20706 | 21436 | 22480 | 19826 | 23341 | 21836
4499 | 4499 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 11 | 16135 | 20123 | 18709 | 18172 | 18638 | 17854 | 18196 | 21744 | 19871 | 20221 | 21337 | 19446 | 19538 | 21215 | 21190 | 22069 | 23190 | 20673 | 24224 | 22426
4500 | 4500 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 12 | 16401 | 20575 | 18991 | 18543 | 18930 | 18133 | 18668 | 22291 | 20204 | 20571 | 21815 | 19785 | 20068 | 21603 | 21765 | 22502 | 23740 | 21227 | 24842 | 22844
4501 | 4501 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 13 | 16562 | 21029 | 19256 | 18808 | 19232 | 18342 | 18901 | 22864 | 20487 | 20920 | 22191 | 20026 | 20315 | 21913 | 22070 | 22867 | 24131 | 21483 | 25434 | 23170
4502 | 4502 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 14 | 16699 | 21349 | 19245 | 19078 | 19534 | 18505 | 19066 | 23359 | 20451 | 21235 | 22373 | 20181 | 20452 | 21865 | 22339 | 23123 | 24258 | 21625 | 25888 | 23112
4503 | 4503 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 15 | 16856 | 21681 | 19411 | 19242 | 19799 | 18631 | 19253 | 23839 | 20624 | 21486 | 22532 | 20300 | 20637 | 22011 | 22511 | 23353 | 24413 | 21791 | 26362 | 23242
4504 | 4504 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 16 | 17206 | 22043 | 19897 | 19645 | 20117 | 18963 | 19666 | 24309 | 21289 | 21708 | 22675 | 20578 | 21021 | 22704 | 22800 | 23462 | 24497 | 22150 | 26781 | 23908
4505 | 4505 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 17 | 17744 | 22577 | 20291 | 20112 | 20718 | 19484 | 20361 | 25001 | 21767 | 22325 | 23164 | 21198 | 21748 | 23182 | 23306 | 24056 | 25029 | 22890 | 27548 | 24394
4506 | 4506 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 18 | 18019 | 22581 | 20305 | 20311 | 21252 | 19970 | 20915 | 25320 | 21796 | 23073 | 23589 | 21930 | 22560 | 23411 | 23697 | 25061 | 25650 | 23792 | 28217 | 24709
4507 | 4507 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 19 | 17790 | 22491 | 20525 | 20316 | 21283 | 19885 | 21019 | 25159 | 22198 | 23220 | 23904 | 22154 | 23020 | 24113 | 24267 | 25567 | 26230 | 24374 | 28391 | 25548
4508 | 4508 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 20 | 17463 | 21992 | 20178 | 20056 | 20999 | 19688 | 20626 | 24479 | 22036 | 23203 | 23933 | 22293 | 22940 | 24249 | 24602 | 25934 | 26641 | 24429 | 28169 | 25800
4509 | 4509 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 21 | 16819 | 21073 | 19334 | 19174 | 20373 | 19176 | 20434 | 23540 | 21492 | 22883 | 23844 | 22234 | 23154 | 24115 | 24488 | 26104 | 26980 | 24856 | 27817 | 25883
4510 | 4510 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 22 | 16265 | 20057 | 18528 | 18437 | 19547 | 18694 | 19910 | 22571 | 20859 | 22273 | 23243 | 22013 | 22858 | 23706 | 24259 | 25737 | 26617 | 24700 | 27148 | 25603
4511 | 4511 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 23 | 15293 | 18534 | 17138 | 17150 | 18253 | 17692 | 18773 | 20919 | 19493 | 21030 | 21929 | 21074 | 21748 | 22419 | 23082 | 24569 | 25332 | 23630 | 25552 | 24364
4512 | 4512 | 188 | 7 | 7 | Summer | 7 | 6 | Summer | 24 | 14339 | 17058 | 15979 | 15979 | 17078 | 16605 | 17569 | 19355 | 18322 | 19801 | 20531 | 19954 | 20533 | 21257 | 21864 | 23384 | 23937 | 22414 | 23942 | 23201
4513 | 4513 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 1 | 14372 | 15607 | 15213 | 15341 | 15902 | 16356 | 16834 | 18005 | 17622 | 18594 | 18661 | 19137 | 19662 | 20648 | 21254 | 22142 | 21908 | 21469 | 23095 | 22662
4514 | 4514 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 2 | 13741 | 15016 | 14748 | 14880 | 15308 | 15653 | 16196 | 17318 | 17055 | 17884 | 17950 | 18319 | 18908 | 19966 | 20571 | 21310 | 21049 | 20652 | 22207 | 21910
4515 | 4515 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 3 | 13313 | 14646 | 14431 | 14609 | 14921 | 15184 | 15870 | 16866 | 16642 | 17373 | 17433 | 17726 | 18463 | 19410 | 20030 | 20635 | 20393 | 20134 | 21528 | 21278
4516 | 4516 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 4 | 13061 | 14505 | 14351 | 14516 | 14761 | 14812 | 15698 | 16552 | 16347 | 16958 | 16837 | 17079 | 18017 | 18819 | 19383 | 19862 | 19495 | 19530 | 20730 | 20517
4517 | 4517 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 5 | 12832 | 14703 | 14509 | 14670 | 14868 | 14492 | 15783 | 16514 | 16273 | 16778 | 16280 | 16487 | 17781 | 18373 | 18905 | 19265 | 18594 | 19125 | 20142 | 19865
4518 | 4518 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 6 | 12708 | 15525 | 15239 | 15309 | 15581 | 14272 | 16505 | 17147 | 16794 | 17166 | 15869 | 15965 | 18143 | 18544 | 18880 | 19228 | 17809 | 19330 | 20183 | 19841
4519 | 4519 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 7 | 13108 | 16641 | 16453 | 16398 | 16801 | 14597 | 17828 | 18075 | 17791 | 18134 | 15927 | 15980 | 19207 | 19290 | 19448 | 19912 | 17569 | 20293 | 20595 | 20452
4520 | 4520 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 8 | 14415 | 17648 | 17529 | 17558 | 18167 | 15865 | 19494 | 18967 | 18765 | 19475 | 16754 | 17120 | 20771 | 20128 | 20440 | 21153 | 18358 | 21830 | 21260 | 21239
4521 | 4521 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 9 | 15695 | 18330 | 18192 | 18441 | 19182 | 17163 | 20811 | 19613 | 19404 | 20568 | 17721 | 18385 | 21978 | 20726 | 21329 | 22211 | 19361 | 23020 | 21805 | 21823
4522 | 4522 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 10 | 16715 | 19019 | 18789 | 19159 | 20037 | 18264 | 21892 | 20396 | 20097 | 21523 | 18550 | 19589 | 23129 | 21511 | 22241 | 23268 | 20293 | 24244 | 22746 | 22671
4523 | 4523 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 11 | 17406 | 19400 | 19153 | 19660 | 20648 | 19046 | 22717 | 20912 | 20569 | 22226 | 19071 | 20470 | 24068 | 22083 | 22967 | 24083 | 20923 | 25220 | 23430 | 23315
4524 | 4524 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 12 | 17736 | 19578 | 19454 | 19867 | 20978 | 19432 | 23170 | 21158 | 20948 | 22616 | 19311 | 20919 | 24576 | 22564 | 23313 | 24551 | 21210 | 25764 | 23766 | 23843
4525 | 4525 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 13 | 17919 | 19809 | 19683 | 20143 | 21280 | 19629 | 23719 | 21413 | 21202 | 22962 | 19420 | 21137 | 25131 | 22837 | 23646 | 24917 | 21346 | 26324 | 24059 | 24129
4526 | 4526 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 14 | 17991 | 19701 | 19837 | 20356 | 21382 | 19680 | 24100 | 21292 | 21395 | 23042 | 19370 | 21189 | 25506 | 23008 | 23807 | 24955 | 21289 | 26677 | 23902 | 24307
4527 | 4527 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 15 | 18017 | 19757 | 19877 | 20494 | 21423 | 19742 | 24457 | 21336 | 21432 | 23088 | 19344 | 21244 | 25861 | 23057 | 23915 | 24980 | 21254 | 27026 | 23908 | 24360
4528 | 4528 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 16 | 18199 | 19951 | 20026 | 20558 | 21377 | 19907 | 24677 | 21710 | 21526 | 22996 | 19344 | 21376 | 26027 | 23104 | 23783 | 24812 | 21196 | 27185 | 24322 | 24384
4529 | 4529 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 17 | 18578 | 20087 | 20258 | 20897 | 21587 | 20359 | 25123 | 21919 | 21709 | 23236 | 19634 | 21832 | 26525 | 23365 | 24134 | 25083 | 21504 | 27710 | 24563 | 24664
4530 | 4530 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 18 | 18672 | 19858 | 20208 | 21156 | 21462 | 20651 | 25159 | 21690 | 21733 | 23391 | 20084 | 22361 | 26853 | 23491 | 24874 | 25453 | 22228 | 28126 | 24627 | 24884
4531 | 4531 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 19 | 18666 | 19977 | 20126 | 21093 | 21434 | 20683 | 24906 | 21974 | 21887 | 23569 | 20498 | 22715 | 26834 | 23951 | 25283 | 25935 | 22888 | 28240 | 25398 | 25489
4532 | 4532 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 20 | 18148 | 19623 | 19844 | 20788 | 21227 | 20292 | 24211 | 21768 | 21812 | 23516 | 20565 | 22589 | 26497 | 24245 | 25626 | 26325 | 23219 | 28039 | 25663 | 25912
4533 | 4533 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 21 | 17787 | 18782 | 18910 | 20116 | 20710 | 20052 | 23209 | 21139 | 21200 | 23320 | 20533 | 22724 | 25939 | 24061 | 25725 | 26611 | 23584 | 27667 | 25729 | 25952
4534 | 4534 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 22 | 17157 | 17914 | 18151 | 19256 | 19841 | 19487 | 22188 | 20444 | 20637 | 22648 | 20302 | 22369 | 25122 | 23762 | 25304 | 26206 | 23554 | 26967 | 25421 | 25817
4535 | 4535 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 23 | 16065 | 16541 | 16865 | 17985 | 18473 | 18349 | 20528 | 19063 | 19385 | 21307 | 19507 | 21254 | 23496 | 22569 | 24128 | 24913 | 22814 | 25365 | 24178 | 24661
4536 | 4536 | 189 | 7 | 8 | Summer | 7 | 7 | Summer | 24 | 15006 | 15405 | 15691 | 16806 | 17105 | 17156 | 18970 | 17871 | 18198 | 19897 | 18487 | 20033 | 21903 | 21352 | 22909 | 23527 | 21776 | 23766 | 23023 | 23444
4537 | 4537 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 1 | 14313 | 14488 | 14914 | 15486 | 15316 | 16308 | 17427 | 16992 | 17404 | 17921 | 16979 | 19027 | 20698 | 20590 | 21541 | 21368 | 19780 | 22750 | 22327 | 22698
4538 | 4538 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 2 | 13815 | 14056 | 14488 | 14921 | 14745 | 15690 | 16770 | 16463 | 16877 | 17247 | 16412 | 18312 | 19896 | 19937 | 20738 | 20542 | 19104 | 21879 | 21595 | 21970
4539 | 4539 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 3 | 13524 | 13776 | 14242 | 14552 | 14372 | 15360 | 16347 | 16078 | 16518 | 16768 | 15983 | 17893 | 19315 | 19436 | 20093 | 19907 | 18548 | 21217 | 20978 | 21383
4540 | 4540 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 4 | 13448 | 13696 | 14160 | 14404 | 14075 | 15225 | 16069 | 15824 | 16221 | 16222 | 15490 | 17481 | 18709 | 18826 | 19352 | 19030 | 17802 | 20428 | 20217 | 20601
4541 | 4541 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 5 | 13675 | 13886 | 14345 | 14548 | 13911 | 15350 | 16090 | 15817 | 16147 | 15738 | 15002 | 17308 | 18355 | 18409 | 18812 | 18174 | 16999 | 19865 | 19585 | 19983
4542 | 4542 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 6 | 14554 | 14615 | 15032 | 15314 | 13880 | 16086 | 16794 | 16415 | 16547 | 15417 | 14550 | 17750 | 18641 | 18451 | 18838 | 17440 | 16249 | 19948 | 19585 | 19841
4543 | 4543 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 7 | 15802 | 15634 | 15944 | 16351 | 13965 | 17199 | 17559 | 17246 | 17256 | 15328 | 14318 | 18648 | 18998 | 18841 | 19342 | 17007 | 15842 | 20150 | 19975 | 20123
4544 | 4544 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 8 | 17018 | 16350 | 16730 | 17334 | 14473 | 18484 | 18090 | 17864 | 18006 | 15806 | 14777 | 19844 | 19347 | 19447 | 20197 | 17406 | 16244 | 20419 | 20374 | 20731
4545 | 4545 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 9 | 18013 | 16807 | 17425 | 18132 | 15208 | 19564 | 18524 | 18305 | 18677 | 16568 | 15478 | 20841 | 19715 | 20114 | 21032 | 18188 | 16970 | 20736 | 20729 | 21424
4546 | 4546 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 10 | 18800 | 17145 | 17888 | 18731 | 15648 | 20439 | 19046 | 18743 | 19219 | 17137 | 16084 | 21751 | 20334 | 20759 | 21837 | 18868 | 17658 | 21415 | 21327 | 22128
4547 | 4547 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 11 | 19469 | 17450 | 18343 | 19294 | 16001 | 21177 | 19510 | 19168 | 19774 | 17608 | 16612 | 22624 | 20912 | 21430 | 22600 | 19453 | 18272 | 22058 | 21928 | 22873
4548 | 4548 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 12 | 19898 | 17754 | 18608 | 19682 | 16246 | 21633 | 19814 | 19601 | 20101 | 17904 | 16979 | 23189 | 21280 | 21833 | 23120 | 19796 | 18690 | 22452 | 22512 | 23325
4549 | 4549 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 13 | 20350 | 17993 | 18903 | 20010 | 16352 | 22079 | 20087 | 19878 | 20437 | 18034 | 17185 | 23773 | 21585 | 22186 | 23504 | 19948 | 18922 | 22766 | 22820 | 23705
4550 | 4550 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 14 | 20555 | 18129 | 19100 | 20085 | 16288 | 22251 | 19956 | 20031 | 20617 | 17976 | 17295 | 24131 | 21421 | 22341 | 23538 | 19871 | 19009 | 22596 | 22983 | 23836
4551 | 4551 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 15 | 20852 | 18273 | 19304 | 20201 | 16330 | 22505 | 20072 | 20153 | 20818 | 18024 | 17543 | 24562 | 21512 | 22520 | 23638 | 19913 | 19266 | 22673 | 23107 | 24006
4552 | 4552 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 16 | 21202 | 18654 | 19640 | 20432 | 16636 | 22856 | 20662 | 20530 | 21062 | 18300 | 17970 | 25001 | 22210 | 22667 | 23742 | 20121 | 19650 | 23351 | 23390 | 24095
4553 | 4553 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 17 | 21665 | 19040 | 20135 | 20811 | 17010 | 23338 | 21045 | 20877 | 21601 | 18753 | 18623 | 25667 | 22613 | 23191 | 24184 | 20606 | 20387 | 23761 | 23839 | 24639
4554 | 4554 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 18 | 21706 | 19316 | 20618 | 20960 | 17561 | 23627 | 21102 | 21204 | 22384 | 19463 | 19435 | 26252 | 22880 | 24210 | 24834 | 21619 | 21285 | 24124 | 24364 | 25750
4555 | 4555 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 19 | 21713 | 19374 | 20722 | 21092 | 17920 | 23741 | 21536 | 21484 | 22602 | 19991 | 19836 | 26374 | 23643 | 24777 | 25462 | 22448 | 21901 | 25074 | 25140 | 26435
4556 | 4556 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 20 | 21220 | 19086 | 20397 | 20867 | 17744 | 23319 | 21310 | 21364 | 22525 | 19981 | 19997 | 25998 | 23760 | 25080 | 25826 | 22756 | 22303 | 25362 | 25584 | 26857
4557 | 4557 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 21 | 20306 | 18154 | 19709 | 20327 | 17332 | 22540 | 20636 | 20692 | 22147 | 19877 | 19776 | 25367 | 23573 | 25126 | 26076 | 23103 | 22374 | 25429 | 25634 | 27133
4558 | 4558 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 22 | 19275 | 17361 | 18848 | 19456 | 16889 | 21543 | 19911 | 20093 | 21467 | 19613 | 19460 | 24526 | 23109 | 24686 | 25648 | 23068 | 22237 | 25117 | 25497 | 26817
4559 | 4559 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 23 | 17769 | 16104 | 17602 | 18114 | 16042 | 20012 | 18536 | 18835 | 20225 | 18830 | 18612 | 22918 | 21812 | 23515 | 24391 | 22338 | 21438 | 23893 | 24370 | 25690
4560 | 4560 | 190 | 7 | 9 | Summer | 7 | 8 | Summer | 24 | 16364 | 14996 | 16425 | 16757 | 15100 | 18476 | 17362 | 17638 | 19021 | 17814 | 17645 | 21336 | 20648 | 22329 | 23004 | 21312 | 20435 | 22751 | 23177 | 24481
4561 | 4561 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 1 | 14999 | 14507 | 15363 | 15229 | 14350 | 17143 | 16700 | 17068 | 17897 | 16635 | 16895 | 20304 | 20094 | 21174 | 21092 | 19600 | 19590 | 22276 | 22669 | 23306
4562 | 4562 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 2 | 14437 | 14085 | 14817 | 14667 | 13893 | 16498 | 16184 | 16560 | 17228 | 16086 | 16404 | 19523 | 19446 | 20387 | 20279 | 18931 | 19000 | 21549 | 21952 | 22446
4563 | 4563 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 3 | 14062 | 13825 | 14440 | 14285 | 13558 | 16068 | 15795 | 16205 | 16734 | 15657 | 16098 | 18946 | 18896 | 19741 | 19639 | 18367 | 18580 | 20915 | 21338 | 21705
4564 | 4564 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 4 | 13941 | 13774 | 14329 | 14024 | 13338 | 15842 | 15603 | 15978 | 16396 | 15227 | 15812 | 18410 | 18365 | 19062 | 18815 | 17663 | 18057 | 20186 | 20588 | 20845
4565 | 4565 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 5 | 14168 | 13990 | 14507 | 13895 | 13125 | 15915 | 15663 | 15980 | 16310 | 14801 | 15761 | 18126 | 17992 | 18587 | 18011 | 16897 | 17769 | 19585 | 19989 | 20162
4566 | 4566 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 6 | 14975 | 14649 | 15265 | 13858 | 12913 | 16620 | 16279 | 16423 | 16754 | 14370 | 16128 | 18436 | 18201 | 18624 | 17276 | 16134 | 17906 | 19562 | 19805 | 20016
4567 | 4567 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 7 | 16013 | 15667 | 16438 | 14075 | 13049 | 17518 | 17249 | 17304 | 17665 | 14294 | 16860 | 18959 | 18894 | 19265 | 16973 | 15842 | 18420 | 20064 | 20188 | 20550
4568 | 4568 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 8 | 16835 | 16661 | 17625 | 14776 | 13787 | 18248 | 18071 | 18271 | 18831 | 14977 | 17696 | 19528 | 19560 | 20330 | 17571 | 16434 | 19164 | 20654 | 20967 | 21601
4569 | 4569 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 9 | 17428 | 17448 | 18580 | 15635 | 14597 | 18810 | 18644 | 19084 | 19837 | 15821 | 18353 | 20038 | 20075 | 21282 | 18488 | 17273 | 19839 | 21135 | 21785 | 22601
4570 | 4570 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 10 | 17976 | 18003 | 19289 | 16180 | 15223 | 19422 | 19174 | 19728 | 20649 | 16534 | 18898 | 20759 | 20731 | 22185 | 19267 | 18072 | 20479 | 21836 | 22596 | 23568
4571 | 4571 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 11 | 18244 | 18400 | 19803 | 16483 | 15597 | 19819 | 19536 | 20228 | 21250 | 17010 | 19385 | 21282 | 21210 | 22893 | 19798 | 18640 | 21054 | 22387 | 23289 | 24337
4572 | 4572 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 12 | 18455 | 18652 | 20175 | 16712 | 15896 | 20104 | 19950 | 20533 | 21680 | 17358 | 19660 | 21629 | 21732 | 23395 | 20131 | 19038 | 21384 | 22956 | 23724 | 24886
4573 | 4573 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 13 | 18866 | 19118 | 20662 | 16978 | 16233 | 20533 | 20388 | 21027 | 22202 | 17728 | 20068 | 22093 | 22192 | 23943 | 20446 | 19431 | 21803 | 23428 | 24264 | 25458
4574 | 4574 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 14 | 18943 | 19480 | 20928 | 17108 | 16543 | 20589 | 20725 | 21405 | 22467 | 18028 | 20237 | 22130 | 22548 | 24168 | 20558 | 19713 | 21975 | 23774 | 24590 | 25661
4575 | 4575 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 15 | 19231 | 19856 | 21200 | 17307 | 16941 | 20866 | 21003 | 21766 | 22739 | 18440 | 20449 | 22384 | 22831 | 24428 | 20758 | 20128 | 22201 | 24053 | 24911 | 25920
4576 | 4576 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 16 | 19573 | 20112 | 21345 | 17534 | 17306 | 21365 | 21294 | 21949 | 22827 | 18784 | 20599 | 22983 | 23058 | 24457 | 20882 | 20438 | 22315 | 24248 | 24914 | 25932
4577 | 4577 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 17 | 19636 | 20354 | 21474 | 17668 | 17736 | 21516 | 21408 | 22235 | 22992 | 19188 | 20841 | 23157 | 23254 | 24668 | 21135 | 20951 | 22559 | 24461 | 25226 | 26159
4578 | 4578 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 18 | 19404 | 20489 | 21237 | 17869 | 18031 | 21253 | 21398 | 22639 | 23104 | 19657 | 20990 | 23098 | 23356 | 24990 | 21818 | 21523 | 22854 | 24667 | 26020 | 26566
4579 | 4579 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 19 | 19431 | 20312 | 21073 | 17946 | 17906 | 21405 | 21379 | 22548 | 23149 | 19725 | 21190 | 23543 | 23675 | 25305 | 22350 | 21852 | 23326 | 25173 | 26442 | 27028
4580 | 4580 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 20 | 18999 | 19918 | 20739 | 17668 | 17808 | 21085 | 21151 | 22335 | 22955 | 19740 | 21436 | 23516 | 23864 | 25540 | 22545 | 22159 | 23799 | 25543 | 26790 | 27384
4581 | 4581 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 21 | 18135 | 19155 | 20139 | 17187 | 17271 | 20335 | 20388 | 21846 | 22661 | 19426 | 21426 | 23216 | 23594 | 25695 | 22810 | 22169 | 24069 | 25545 | 27030 | 27757
4582 | 4582 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 22 | 17272 | 18330 | 19272 | 16744 | 16775 | 19590 | 19756 | 21132 | 21962 | 19082 | 20760 | 22716 | 23257 | 25241 | 22760 | 22024 | 23572 | 25401 | 26723 | 27437
4583 | 4583 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 23 | 15946 | 17070 | 17913 | 15898 | 15893 | 18187 | 18466 | 19872 | 20627 | 18203 | 19520 | 21384 | 22063 | 23926 | 21997 | 21212 | 22389 | 24246 | 25581 | 26155
4584 | 4584 | 191 | 7 | 10 | Summer | 7 | 9 | Summer | 24 | 14841 | 15921 | 16538 | 14960 | 14957 | 17004 | 17257 | 18635 | 19232 | 17223 | 18379 | 20217 | 20855 | 22543 | 20965 | 20211 | 21207 | 23045 | 24376 | 24765
4585 | 4585 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 1 | 14017 | 14734 | 14896 | 14113 | 14183 | 16175 | 16526 | 17362 | 17389 | 16343 | 17940 | 19488 | 20171 | 20520 | 19157 | 19237 | 21022 | 22384 | 23065 | 22626
4586 | 4586 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 2 | 13590 | 14180 | 14339 | 13644 | 13776 | 15658 | 16022 | 16692 | 16729 | 15855 | 17344 | 18843 | 19526 | 19710 | 18487 | 18634 | 20315 | 21654 | 22189 | 21736
4587 | 4587 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 3 | 13330 | 13855 | 13992 | 13341 | 13606 | 15307 | 15711 | 16245 | 16283 | 15593 | 16939 | 18342 | 19049 | 19112 | 17960 | 18245 | 19784 | 21070 | 21482 | 21055
4588 | 4588 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 4 | 13262 | 13754 | 13744 | 13126 | 13555 | 15145 | 15522 | 15954 | 15804 | 15347 | 16574 | 17856 | 18496 | 18327 | 17281 | 17736 | 19136 | 20335 | 20620 | 20086
4589 | 4589 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 5 | 13479 | 13954 | 13645 | 12937 | 13797 | 15260 | 15587 | 15943 | 15401 | 15357 | 16414 | 17554 | 18150 | 17581 | 16557 | 17480 | 18651 | 19759 | 19956 | 19137
4590 | 4590 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 6 | 14182 | 14748 | 13665 | 12773 | 14488 | 15950 | 16122 | 16493 | 15123 | 15812 | 16766 | 17853 | 18235 | 16923 | 15858 | 17664 | 18680 | 19622 | 19837 | 18302
4591 | 4591 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 7 | 15380 | 16001 | 13977 | 12990 | 15469 | 17014 | 17112 | 17531 | 15247 | 16660 | 17451 | 18648 | 18827 | 16716 | 15649 | 18247 | 19129 | 20065 | 20430 | 17992
4592 | 4592 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 8 | 16416 | 17310 | 14833 | 13860 | 16446 | 17971 | 18221 | 18857 | 16051 | 17656 | 18113 | 19470 | 19761 | 17453 | 16376 | 19124 | 19644 | 20965 | 21597 | 18738
4593 | 4593 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 9 | 17044 | 18290 | 15771 | 14712 | 17152 | 18590 | 19084 | 19927 | 16983 | 18379 | 18620 | 20039 | 20593 | 18416 | 17267 | 19835 | 20072 | 21816 | 22632 | 19722
4594 | 4594 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 10 | 17542 | 19049 | 16371 | 15374 | 17644 | 19160 | 19779 | 20763 | 17696 | 18977 | 19351 | 20725 | 21400 | 19240 | 18117 | 20512 | 20908 | 22686 | 23649 | 20622
4595 | 4595 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 11 | 17827 | 19583 | 16702 | 15779 | 18056 | 19532 | 20298 | 21386 | 18142 | 19487 | 19923 | 21230 | 22058 | 19783 | 18712 | 21116 | 21600 | 23408 | 24453 | 21254
4596 | 4596 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 12 | 18003 | 19880 | 16863 | 16008 | 18214 | 19865 | 20526 | 21745 | 18357 | 19695 | 20292 | 21668 | 22379 | 20049 | 19043 | 21371 | 22047 | 23775 | 24937 | 21554
4597 | 4597 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 13 | 18225 | 20183 | 16953 | 16177 | 18421 | 20128 | 20837 | 22096 | 18474 | 19926 | 20621 | 21958 | 22726 | 20200 | 19263 | 21624 | 22416 | 24139 | 25334 | 21714
4598 | 4598 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 14 | 18452 | 20388 | 17001 | 16398 | 18503 | 20386 | 21142 | 22277 | 18518 | 20015 | 20796 | 22226 | 22989 | 20236 | 19469 | 21707 | 22573 | 24385 | 25461 | 21745
4599 | 4599 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 15 | 18669 | 20586 | 17109 | 16708 | 18606 | 20576 | 21424 | 22458 | 18629 | 20141 | 21019 | 22425 | 23244 | 20351 | 19797 | 21843 | 22796 | 24621 | 25627 | 21867
4600 | 4600 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 16 | 18997 | 20784 | 17382 | 17125 | 18843 | 20928 | 21667 | 22609 | 18869 | 20346 | 21606 | 22715 | 23370 | 20542 | 20154 | 22008 | 23397 | 24674 | 25682 | 22042
4601 | 4601 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 17 | 19145 | 20907 | 17514 | 17563 | 19043 | 21056 | 21961 | 22785 | 19080 | 20594 | 21929 | 22923 | 23663 | 20787 | 20672 | 22262 | 23725 | 24991 | 25914 | 22307
4602 | 4602 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 18 | 19107 | 20618 | 17637 | 17817 | 18997 | 21029 | 22312 | 22819 | 19447 | 20715 | 21875 | 22995 | 24336 | 21444 | 21228 | 22546 | 23800 | 25779 | 26306 | 23048
4603 | 4603 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 19 | 18867 | 20446 | 17670 | 17655 | 19041 | 20970 | 22160 | 22799 | 19651 | 20840 | 22256 | 23241 | 24587 | 21925 | 21516 | 22985 | 24414 | 26177 | 26761 | 23628
4604 | 4604 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 20 | 18499 | 20086 | 17368 | 17545 | 19055 | 20722 | 21916 | 22547 | 19522 | 21013 | 22593 | 23367 | 24762 | 22086 | 21805 | 23452 | 25117 | 26547 | 27134 | 23890
4605 | 4605 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 21 | 17533 | 19483 | 16854 | 16982 | 18764 | 19902 | 21362 | 22171 | 19310 | 20929 | 22479 | 23018 | 24706 | 22292 | 21780 | 23690 | 25347 | 26776 | 27500 | 24304
4606 | 4606 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 22 | 16718 | 18571 | 16373 | 16452 | 17911 | 19193 | 20582 | 21404 | 18998 | 20196 | 21795 | 22602 | 24214 | 22177 | 21581 | 23156 | 24887 | 26425 | 27150 | 24301
4607 | 4607 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 23 | 15472 | 17236 | 15548 | 15581 | 16660 | 17917 | 19315 | 20058 | 18205 | 18966 | 20521 | 21385 | 23027 | 21420 | 20771 | 21948 | 23671 | 25289 | 25885 | 23579
4608 | 4608 | 192 | 7 | 11 | Summer | 7 | 10 | Summer | 24 | 14404 | 15919 | 14605 | 14660 | 15551 | 16717 | 18080 | 18641 | 17196 | 17818 | 19373 | 20172 | 21808 | 20389 | 19768 | 20785 | 22538 | 24079 | 24496 | 22522
4609 | 4609 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 1 | 13864 | 14391 | 13878 | 13955 | 14924 | 16052 | 16878 | 16882 | 16029 | 17392 | 18748 | 19536 | 20581 | 18719 | 18867 | 20630 | 21933 | 22842 | 22436 | 20580
4610 | 4610 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 2 | 13454 | 13863 | 13444 | 13568 | 14478 | 15581 | 16242 | 16251 | 15503 | 16831 | 18132 | 18926 | 19811 | 18080 | 18294 | 19947 | 21187 | 21990 | 21568 | 19869
4611 | 4611 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 3 | 13204 | 13508 | 13138 | 13386 | 14182 | 15274 | 15804 | 15809 | 15100 | 16439 | 17705 | 18459 | 19189 | 17556 | 17904 | 19411 | 20617 | 21277 | 20879 | 19272
4612 | 4612 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 4 | 13168 | 13294 | 12950 | 13364 | 14112 | 15132 | 15573 | 15398 | 14726 | 16139 | 17270 | 17979 | 18570 | 16926 | 17437 | 18806 | 19894 | 20444 | 19932 | 18486
4613 | 4613 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 5 | 13391 | 13187 | 12760 | 13610 | 14280 | 15219 | 15602 | 15045 | 14351 | 16025 | 17174 | 17690 | 18154 | 16224 | 17193 | 18342 | 19475 | 19781 | 18974 | 17613
4614 | 4614 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 6 | 14100 | 13220 | 12630 | 14344 | 15005 | 15800 | 16224 | 14862 | 14013 | 16450 | 17572 | 17871 | 18291 | 15573 | 17417 | 18417 | 19496 | 19682 | 18152 | 16807
4615 | 4615 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 7 | 15204 | 13571 | 12900 | 15368 | 16055 | 16837 | 17336 | 15079 | 14055 | 17228 | 18473 | 18550 | 19055 | 15415 | 18041 | 18916 | 20071 | 20302 | 17861 | 16572
4616 | 4616 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 8 | 16408 | 14508 | 13879 | 16438 | 16909 | 18028 | 18762 | 16006 | 14966 | 18016 | 19355 | 19599 | 20337 | 16233 | 18996 | 19550 | 20872 | 21550 | 18671 | 17405
4617 | 4617 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 9 | 17188 | 15417 | 14757 | 17142 | 17419 | 18871 | 19827 | 16964 | 15852 | 18549 | 20017 | 20437 | 21355 | 17114 | 19702 | 19980 | 21520 | 22570 | 19633 | 18309
4618 | 4618 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 10 | 17844 | 16058 | 15475 | 17689 | 18056 | 19608 | 20705 | 17725 | 16661 | 19318 | 20839 | 21289 | 22350 | 18011 | 20434 | 20853 | 22413 | 23638 | 20593 | 19268
4619 | 4619 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 11 | 18323 | 16452 | 15932 | 18143 | 18539 | 20162 | 21372 | 18207 | 17214 | 19931 | 21505 | 21981 | 23141 | 18652 | 21091 | 21582 | 23177 | 24500 | 21279 | 19973
4620 | 4620 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 12 | 18533 | 16641 | 16189 | 18325 | 18863 | 20414 | 21754 | 18446 | 17523 | 20327 | 22085 | 22322 | 23611 | 19011 | 21376 | 22056 | 23855 | 25008 | 21609 | 20368
4621 | 4621 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 13 | 18807 | 16692 | 16333 | 18513 | 19133 | 20701 | 22074 | 18539 | 17691 | 20634 | 22434 | 22647 | 23962 | 19210 | 21615 | 22396 | 24209 | 25378 | 21746 | 20585
4622 | 4622 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 14 | 18948 | 16603 | 16427 | 18476 | 19193 | 20883 | 22126 | 18465 | 17782 | 20693 | 22593 | 22797 | 23984 | 19293 | 21574 | 22435 | 24379 | 25377 | 21651 | 20662
4623 | 4623 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 15 | 19094 | 16562 | 16588 | 18444 | 19257 | 21019 | 22167 | 18436 | 17958 | 20764 | 22711 | 22916 | 24013 | 19477 | 21568 | 22512 | 24485 | 25396 | 21625 | 20858
4624 | 4624 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 16 | 19258 | 16677 | 16847 | 18525 | 19586 | 21123 | 22169 | 18529 | 18206 | 21189 | 22796 | 22902 | 23950 | 19684 | 21581 | 22957 | 24516 | 25292 | 21640 | 21061
4625 | 4625 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 17 | 19509 | 16821 | 17287 | 18751 | 19902 | 21432 | 22355 | 18762 | 18641 | 21521 | 22979 | 23210 | 24187 | 20216 | 21847 | 23309 | 24714 | 25539 | 21927 | 21613
4626 | 4626 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 18 | 19644 | 16939 | 17509 | 18708 | 19710 | 21791 | 22373 | 19096 | 19107 | 21469 | 23008 | 23867 | 24500 | 20796 | 22161 | 23388 | 24936 | 25963 | 22696 | 22250
4627 | 4627 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 19 | 19525 | 17058 | 17413 | 18819 | 19945 | 21712 | 22404 | 19339 | 19208 | 21888 | 23518 | 24143 | 24849 | 21148 | 22662 | 24075 | 25735 | 26507 | 23372 | 22688
4628 | 4628 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 20 | 19179 | 16784 | 17329 | 18859 | 20112 | 21500 | 22166 | 19192 | 19216 | 22187 | 23882 | 24307 | 25078 | 21453 | 23159 | 24799 | 26356 | 26939 | 23695 | 23046
4629 | 4629 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 21 | 18411 | 16253 | 16746 | 18543 | 19654 | 20898 | 21725 | 18902 | 18853 | 21989 | 23731 | 24169 | 25165 | 21383 | 23358 | 25001 | 26615 | 27291 | 24102 | 23117
4630 | 4630 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 22 | 17589 | 15788 | 16224 | 17674 | 18762 | 20101 | 20945 | 18549 | 18460 | 21277 | 23099 | 23633 | 24652 | 21170 | 22812 | 24536 | 26239 | 26943 | 24114 | 23004
4631 | 4631 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 23 | 16334 | 14978 | 15356 | 16433 | 17436 | 18830 | 19580 | 17732 | 17581 | 19993 | 21737 | 22415 | 23353 | 20357 | 21595 | 23329 | 24922 | 25688 | 23403 | 22227
4632 | 4632 | 193 | 7 | 12 | Summer | 7 | 11 | Summer | 24 | 15238 | 14078 | 14422 | 15336 | 16267 | 17605 | 18160 | 16710 | 16610 | 18833 | 20447 | 21204 | 21950 | 19362 | 20419 | 22164 | 23659 | 24292 | 22365 | 21217
4633 | 4633 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 1 | 14090 | 13348 | 13695 | 14645 | 15597 | 16364 | 16384 | 15581 | 15758 | 18145 | 19281 | 19911 | 19955 | 18410 | 20192 | 21507 | 22550 | 22189 | 20377 | 20212
4634 | 4634 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 2 | 13555 | 12924 | 13322 | 14202 | 15083 | 15740 | 15764 | 15063 | 15299 | 17544 | 18605 | 19159 | 19168 | 17845 | 19517 | 20768 | 21755 | 21321 | 19666 | 19594
4635 | 4635 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 3 | 13244 | 12628 | 13157 | 13929 | 14796 | 15327 | 15349 | 14692 | 15056 | 17150 | 18085 | 18578 | 18589 | 17477 | 19003 | 20225 | 21102 | 20646 | 19080 | 19159
4636 | 4636 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 4 | 13166 | 12449 | 13141 | 13869 | 14654 | 15126 | 14978 | 14353 | 14867 | 16764 | 17630 | 18014 | 17862 | 17037 | 18425 | 19523 | 20363 | 19709 | 18295 | 18571
4637 | 4637 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 5 | 13380 | 12292 | 13428 | 14081 | 14960 | 15221 | 14711 | 14050 | 14934 | 16759 | 17486 | 17688 | 17180 | 16858 | 18025 | 19158 | 19843 | 18800 | 17456 | 18228
4638 | 4638 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 6 | 14195 | 12173 | 14196 | 14841 | 15720 | 15888 | 14597 | 13787 | 15459 | 17234 | 17741 | 17914 | 16595 | 17125 | 18146 | 19227 | 19726 | 17998 | 16662 | 18354
4639 | 4639 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 7 | 15430 | 12417 | 15205 | 15888 | 16806 | 16973 | 14818 | 13850 | 16319 | 18148 | 18568 | 18701 | 16411 | 17726 | 18628 | 19799 | 20324 | 17664 | 16374 | 18889
4640 | 4640 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 8 | 16483 | 13081 | 15956 | 16428 | 17473 | 18065 | 15419 | 14454 | 17084 | 18747 | 19353 | 19689 | 16918 | 18365 | 18943 | 20280 | 21008 | 18136 | 16863 | 19539
4641 | 4641 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 9 | 17202 | 13728 | 16484 | 16736 | 17963 | 18909 | 16179 | 15153 | 17589 | 19224 | 20055 | 20498 | 17680 | 18861 | 19178 | 20711 | 21724 | 18897 | 17559 | 20056
4642 | 4642 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 10 | 17758 | 14171 | 16764 | 17101 | 18414 | 19512 | 16648 | 15692 | 17974 | 19771 | 20657 | 21225 | 18286 | 19318 | 19785 | 21341 | 22423 | 19575 | 18252 | 20576
4643 | 4643 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 11 | 18185 | 14441 | 17048 | 17407 | 18808 | 20004 | 16944 | 16069 | 18368 | 20261 | 21218 | 21836 | 18723 | 19802 | 20341 | 21928 | 23093 | 20081 | 18789 | 21127
4644 | 4644 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 12 | 18514 | 14725 | 17246 | 17747 | 19289 | 20395 | 17199 | 16391 | 18607 | 20853 | 21676 | 22311 | 19035 | 20103 | 20830 | 22615 | 23604 | 20431 | 19201 | 21465
4645 | 4645 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 13 | 18833 | 14907 | 17476 | 18067 | 19655 | 20757 | 17329 | 16603 | 18859 | 21246 | 22026 | 22703 | 19198 | 20385 | 21212 | 23028 | 23977 | 20608 | 19461 | 21768
4646 | 4646 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 14 | 19056 | 15131 | 17574 | 18269 | 19939 | 20953 | 17392 | 16837 | 18960 | 21540 | 22193 | 22866 | 19249 | 20483 | 21377 | 23329 | 24132 | 20649 | 19674 | 21863
4647 | 4647 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 15 | 19317 | 15485 | 17738 | 18534 | 20252 | 21193 | 17556 | 17212 | 19138 | 21860 | 22429 | 23102 | 19417 | 20674 | 21655 | 23643 | 24338 | 20815 | 20067 | 22076
4648 | 4648 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 16 | 19643 | 15991 | 18077 | 19090 | 20650 | 21461 | 17913 | 17715 | 19448 | 22208 | 22663 | 23302 | 19715 | 20939 | 22361 | 23925 | 24460 | 21072 | 20522 | 22345
4649 | 4649 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 17 | 19928 | 16590 | 18447 | 19566 | 20934 | 21808 | 18300 | 18296 | 19866 | 22552 | 22967 | 23693 | 20146 | 21362 | 22878 | 24275 | 24857 | 21519 | 21233 | 22799
4650 | 4650 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 18 | 19702 | 16830 | 18392 | 19438 | 20948 | 21864 | 18631 | 18770 | 20042 | 22616 | 23430 | 24032 | 20843 | 21727 | 23004 | 24541 | 25439 | 22339 | 21920 | 23206
4651 | 4651 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 19 | 19709 | 16819 | 18578 | 19749 | 21307 | 21955 | 18951 | 18927 | 20308 | 23158 | 23719 | 24412 | 21483 | 22296 | 23753 | 25411 | 26000 | 23135 | 22459 | 23856
4652 | 4652 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 20 | 19382 | 16684 | 18565 | 19875 | 21369 | 21674 | 18747 | 18880 | 20480 | 23398 | 24000 | 24562 | 21630 | 22728 | 24406 | 25993 | 26630 | 23438 | 22810 | 24345
4653 | 4653 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 21 | 18759 | 16126 | 18240 | 19383 | 20809 | 21198 | 18403 | 18462 | 20363 | 23164 | 23825 | 24568 | 21768 | 22899 | 24586 | 26217 | 26867 | 23842 | 22889 | 24651
4654 | 4654 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 22 | 17865 | 15605 | 17369 | 18481 | 19933 | 20378 | 18022 | 18039 | 19621 | 22488 | 23130 | 24007 | 21646 | 22327 | 24085 | 25826 | 26415 | 23853 | 22779 | 24180
4655 | 4655 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 23 | 16525 | 14718 | 16116 | 17145 | 18461 | 18995 | 17183 | 17138 | 18365 | 21100 | 21784 | 22668 | 20867 | 21085 | 22850 | 24500 | 25145 | 23115 | 21980 | 22975
4656 | 4656 | 194 | 7 | 13 | Summer | 7 | 12 | Summer | 24 | 15262 | 13831 | 15008 | 15976 | 17181 | 17585 | 16158 | 16148 | 17211 | 19790 | 20404 | 21259 | 19822 | 19919 | 21677 | 23230 | 23772 | 22064 | 20972 | 21781
4657 | 4657 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 1 | 13723 | 13115 | 14309 | 15296 | 15973 | 15837 | 15102 | 15303 | 16678 | 18600 | 18839 | 19293 | 18167 | 19633 | 21013 | 22107 | 22235 | 20103 | 19978 | 21632
4658 | 4658 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 2 | 13212 | 12780 | 13896 | 14799 | 15422 | 15241 | 14607 | 14870 | 16146 | 17953 | 18123 | 18541 | 17545 | 18984 | 20293 | 21336 | 21397 | 19407 | 19360 | 20910
4659 | 4659 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 3 | 12884 | 12644 | 13650 | 14533 | 15059 | 14857 | 14269 | 14655 | 15802 | 17476 | 17598 | 17999 | 17061 | 18503 | 19782 | 20702 | 20726 | 18842 | 18944 | 20355
4660 | 4660 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 4 | 12683 | 12660 | 13624 | 14421 | 14903 | 14542 | 13987 | 14518 | 15557 | 17100 | 17069 | 17341 | 16470 | 17982 | 19132 | 19996 | 19867 | 18089 | 18381 | 19665
4661 | 4661 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 5 | 12596 | 12945 | 13836 | 14740 | 15058 | 14305 | 13717 | 14623 | 15515 | 17016 | 16804 | 16714 | 15825 | 17612 | 18793 | 19496 | 19274 | 17253 | 18030 | 19102
4662 | 4662 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 6 | 12626 | 13716 | 14592 | 15514 | 15644 | 14216 | 13495 | 15200 | 15996 | 17343 | 16974 | 16190 | 15216 | 17765 | 18890 | 19400 | 19119 | 16457 | 18144 | 19077
4663 | 4663 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 7 | 12861 | 14666 | 15589 | 16544 | 16711 | 14377 | 13516 | 16035 | 16698 | 18154 | 17555 | 15987 | 14967 | 18197 | 19416 | 19936 | 19393 | 16085 | 18589 | 19385
4664 | 4664 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 8 | 13389 | 15343 | 16094 | 17146 | 17545 | 14901 | 14057 | 16748 | 17112 | 18902 | 18198 | 16442 | 15395 | 18459 | 19829 | 20551 | 19900 | 16493 | 19152 | 19607
4665 | 4665 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 9 | 14075 | 15860 | 16449 | 17666 | 18253 | 15672 | 14786 | 17298 | 17466 | 19645 | 18749 | 17231 | 16101 | 18722 | 20315 | 21287 | 20467 | 17207 | 19689 | 19877
4666 | 4666 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 10 | 14438 | 16176 | 16841 | 18120 | 18769 | 16141 | 15330 | 17689 | 17960 | 20255 | 19208 | 17836 | 16729 | 19342 | 20957 | 21995 | 21009 | 17914 | 20226 | 20575
4667 | 4667 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 11 | 14690 | 16456 | 17174 | 18523 | 19240 | 16445 | 15718 | 18091 | 18417 | 20826 | 19536 | 18277 | 17226 | 19913 | 21560 | 22677 | 21426 | 18471 | 20798 | 21223
4668 | 4668 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 12 | 14943 | 16702 | 17557 | 19057 | 19683 | 16741 | 16079 | 18380 | 18861 | 21323 | 19775 | 18639 | 17650 | 20438 | 22294 | 23239 | 21717 | 18927 | 21181 | 21797
4669 | 4669 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 13 | 15035 | 16925 | 17884 | 19430 | 20001 | 16876 | 16295 | 18640 | 19219 | 21683 | 19950 | 18810 | 17904 | 20828 | 22712 | 23619 | 21907 | 19192 | 21490 | 22215
4670 | 4670 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 14 | 15058 | 17007 | 18070 | 19699 | 20195 | 16922 | 16513 | 18727 | 19400 | 21857 | 20060 | 18850 | 18109 | 20994 | 22997 | 23763 | 22011 | 19389 | 21573 | 22375
4671 | 4671 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 15 | 15106 | 17073 | 18242 | 19922 | 20354 | 16995 | 16793 | 18814 | 19575 | 21997 | 20112 | 18930 | 18393 | 21189 | 23218 | 23881 | 22032 | 19687 | 21691 | 22572
4672 | 4672 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 16 | 15355 | 17291 | 18608 | 20216 | 20561 | 17239 | 17181 | 19014 | 20126 | 22132 | 20225 | 19124 | 18741 | 21769 | 23389 | 23896 | 22066 | 20021 | 21838 | 23156
4673 | 4673 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 17 | 15678 | 17673 | 19100 | 20521 | 20902 | 17652 | 17777 | 19448 | 20621 | 22456 | 20559 | 19579 | 19453 | 22309 | 23763 | 24312 | 22371 | 20754 | 22313 | 23711
4674 | 4674 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 18 | 15981 | 17765 | 19128 | 20697 | 21244 | 18120 | 18373 | 19750 | 20775 | 23040 | 21145 | 20392 | 20249 | 22595 | 24178 | 25054 | 23120 | 21619 | 22888 | 24061
4675 | 4675 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 19 | 16252 | 17953 | 19436 | 21070 | 21273 | 18453 | 18535 | 20002 | 21274 | 23291 | 21410 | 21010 | 20708 | 23320 | 25053 | 25621 | 23764 | 22180 | 23576 | 24925
4676 | 4676 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 20 | 15982 | 17976 | 19578 | 21110 | 21301 | 18278 | 18513 | 20149 | 21533 | 23505 | 21418 | 21117 | 20986 | 23970 | 25625 | 26247 | 24124 | 22589 | 24109 | 25682
4677 | 4677 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 21 | 15453 | 17628 | 19058 | 20509 | 20717 | 17879 | 18045 | 19967 | 21287 | 23241 | 21103 | 21183 | 20879 | 24086 | 25785 | 26442 | 24251 | 22657 | 24412 | 25969
4678 | 4678 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 22 | 14973 | 16725 | 18102 | 19576 | 19751 | 17434 | 17556 | 19152 | 20530 | 22459 | 20603 | 20970 | 20613 | 23517 | 25327 | 25925 | 23999 | 22501 | 23902 | 25524
4679 | 4679 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 23 | 14186 | 15523 | 16798 | 18148 | 18364 | 16624 | 16679 | 17916 | 19239 | 21127 | 19458 | 20201 | 19789 | 22296 | 24040 | 24680 | 22903 | 21728 | 22727 | 24346
4680 | 4680 | 195 | 7 | 14 | Summer | 7 | 13 | Summer | 24 | 13353 | 14463 | 15643 | 16885 | 17017 | 15625 | 15698 | 16761 | 18075 | 19743 | 18338 | 19167 | 18788 | 21136 | 22759 | 23313 | 21775 | 20731 | 21550 | 23183
4681 | 4681 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 1 | 12706 | 13818 | 15033 | 15719 | 15509 | 14694 | 14914 | 16223 | 17441 | 18218 | 17684 | 17654 | 17887 | 20516 | 21665 | 21825 | 20920 | 19787 | 21441 | 22554
4682 | 4682 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 2 | 12306 | 13419 | 14557 | 15175 | 14908 | 14212 | 14495 | 15707 | 16870 | 17523 | 17132 | 17050 | 17346 | 19812 | 20907 | 21000 | 20264 | 19175 | 20729 | 21782
4683 | 4683 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 3 | 12007 | 13157 | 14275 | 14793 | 14501 | 13859 | 14268 | 15354 | 16491 | 16999 | 16704 | 16560 | 16983 | 19291 | 20262 | 20314 | 19703 | 18736 | 20153 | 21184
4684 | 4684 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 4 | 11848 | 13124 | 14172 | 14660 | 14280 | 13600 | 14161 | 15160 | 16170 | 16528 | 16244 | 16017 | 16589 | 18675 | 19585 | 19489 | 18948 | 18179 | 19464 | 20396
4685 | 4685 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 5 | 11698 | 13356 | 14516 | 14850 | 14394 | 13379 | 14322 | 15186 | 16233 | 16349 | 15686 | 15437 | 16455 | 18394 | 19136 | 18941 | 18067 | 17854 | 18918 | 19917
4686 | 4686 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 6 | 11592 | 14151 | 15321 | 15494 | 14969 | 13214 | 14978 | 15751 | 16782 | 16630 | 15187 | 14916 | 16776 | 18566 | 19109 | 18841 | 17236 | 18003 | 18924 | 19892
4687 | 4687 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 7 | 11770 | 15176 | 16354 | 16586 | 15806 | 13254 | 15851 | 16517 | 17664 | 17281 | 15033 | 14720 | 17321 | 19135 | 19676 | 19143 | 16836 | 18447 | 19233 | 20311
4688 | 4688 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 8 | 12366 | 15701 | 16958 | 17421 | 16524 | 13781 | 16566 | 16970 | 18212 | 17954 | 15645 | 15163 | 17898 | 19579 | 20299 | 19643 | 17352 | 18997 | 19448 | 20700
4689 | 4689 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 9 | 12980 | 16048 | 17472 | 18111 | 17067 | 14482 | 17104 | 17334 | 18709 | 18504 | 16384 | 15857 | 18408 | 20058 | 21023 | 20190 | 18035 | 19512 | 19697 | 21164
4690 | 4690 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 10 | 13454 | 16430 | 17942 | 18648 | 17443 | 15020 | 17492 | 17848 | 19280 | 18964 | 16924 | 16501 | 18899 | 20707 | 21739 | 20756 | 18686 | 20057 | 20403 | 21874
4691 | 4691 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 11 | 13740 | 16760 | 18355 | 19120 | 17671 | 15404 | 17892 | 18306 | 19783 | 19290 | 17316 | 16997 | 19407 | 21300 | 22426 | 21180 | 19165 | 20636 | 21059 | 22544
4692 | 4692 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 12 | 14067 | 17117 | 18895 | 19556 | 17848 | 15756 | 18167 | 18741 | 20398 | 19515 | 17616 | 17416 | 19745 | 22016 | 22977 | 21463 | 19502 | 21010 | 21623 | 23313
4693 | 4693 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 13 | 14262 | 17451 | 19273 | 19881 | 18003 | 15974 | 18430 | 19103 | 20805 | 19701 | 17748 | 17671 | 20047 | 22441 | 23365 | 21659 | 19656 | 21324 | 22045 | 23756
4694 | 4694 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 14 | 14380 | 17540 | 19452 | 19991 | 18039 | 16104 | 18427 | 19201 | 20998 | 19732 | 17749 | 17795 | 20046 | 22640 | 23427 | 21678 | 19648 | 21317 | 22117 | 23967
4695 | 4695 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 15 | 14686 | 17754 | 19717 | 20203 | 18154 | 16425 | 18556 | 19431 | 21259 | 19829 | 17979 | 18132 | 20198 | 22910 | 23592 | 21757 | 19870 | 21476 | 22358 | 24238
4696 | 4696 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 16 | 15141 | 18159 | 20083 | 20499 | 18414 | 16889 | 18831 | 20016 | 21582 | 20032 | 18222 | 18566 | 20426 | 23164 | 23696 | 21873 | 20065 | 21692 | 23012 | 24467
4697 | 4697 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 17 | 15708 | 18576 | 20325 | 20777 | 18663 | 17429 | 19202 | 20465 | 21898 | 20307 | 18799 | 19218 | 20814 | 23481 | 24052 | 22121 | 20673 | 22108 | 23510 | 24792
4698 | 4698 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 18 | 16044 | 18556 | 20440 | 21035 | 18955 | 17946 | 19401 | 20531 | 22056 | 20797 | 19529 | 19910 | 21285 | 23822 | 24723 | 22801 | 21594 | 22626 | 23803 | 25219
4699 | 4699 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 19 | 16077 | 18880 | 20822 | 21056 | 19014 | 18136 | 19659 | 20999 | 22596 | 21030 | 19975 | 20352 | 21852 | 24678 | 25289 | 23438 | 22252 | 23343 | 24689 | 26219
4700 | 4700 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 20 | 15977 | 18986 | 20841 | 21058 | 18669 | 18108 | 19791 | 21207 | 22821 | 20941 | 19985 | 20571 | 22302 | 25208 | 25875 | 23775 | 22631 | 23909 | 25460 | 26874
4701 | 4701 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 21 | 15424 | 18479 | 20224 | 20445 | 17946 | 17618 | 19579 | 20892 | 22504 | 20539 | 19957 | 20398 | 22420 | 25316 | 26028 | 23857 | 22999 | 24214 | 25754 | 27200
4702 | 4702 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 22 | 14887 | 17556 | 19293 | 19478 | 17192 | 17135 | 18765 | 20107 | 21762 | 20005 | 19831 | 20112 | 21796 | 24843 | 25506 | 23593 | 23074 | 23719 | 25337 | 26874
4703 | 4703 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 23 | 14022 | 16235 | 17855 | 18078 | 15965 | 16231 | 17497 | 18781 | 20376 | 18821 | 19155 | 19264 | 20574 | 23518 | 24222 | 22470 | 22473 | 22512 | 24120 | 25587
4704 | 4704 | 196 | 7 | 15 | Summer | 7 | 14 | Summer | 24 | 13210 | 15115 | 16598 | 16751 | 14892 | 15271 | 16350 | 17616 | 19098 | 17701 | 18318 | 18276 | 19415 | 22248 | 22849 | 21360 | 21627 | 21347 | 22978 | 24316
4705 | 4705 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 1 | 12621 | 14596 | 15503 | 15313 | 14519 | 14569 | 15836 | 17032 | 18001 | 17152 | 17137 | 17451 | 19191 | 21210 | 21429 | 20591 | 19971 | 21287 | 22419 | 23319
4706 | 4706 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 2 | 12320 | 14142 | 14988 | 14731 | 14117 | 14174 | 15348 | 16487 | 17389 | 16633 | 16629 | 16937 | 18572 | 20477 | 20628 | 19947 | 19349 | 20585 | 21663 | 22519
4707 | 4707 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 3 | 12197 | 13895 | 14650 | 14364 | 13852 | 13990 | 15045 | 16157 | 16941 | 16262 | 16220 | 16624 | 18112 | 19883 | 19991 | 19425 | 18829 | 20040 | 21105 | 21840
4708 | 4708 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 4 | 12220 | 13817 | 14535 | 14165 | 13693 | 13914 | 14896 | 15888 | 16618 | 15859 | 15763 | 16276 | 17631 | 19250 | 19206 | 18714 | 18127 | 19368 | 20326 | 21047
4709 | 4709 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 5 | 12522 | 14152 | 14759 | 14310 | 13488 | 14122 | 14988 | 16012 | 16615 | 15378 | 15288 | 16198 | 17324 | 18865 | 18713 | 17869 | 17379 | 18853 | 19865 | 20471
4710 | 4710 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 6 | 13295 | 14933 | 15403 | 14888 | 13352 | 14776 | 15575 | 16591 | 17008 | 14921 | 14886 | 16548 | 17522 | 18856 | 18616 | 17035 | 16666 | 18841 | 19815 | 20275
4711 | 4711 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 7 | 14267 | 15977 | 16543 | 15768 | 13530 | 15672 | 16401 | 17531 | 17882 | 14843 | 14729 | 17154 | 18005 | 19469 | 18950 | 16670 | 16241 | 19165 | 20242 | 20779
4712 | 4712 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 8 | 14969 | 16620 | 17426 | 16526 | 14229 | 16406 | 16914 | 18143 | 18681 | 15529 | 15258 | 17786 | 18325 | 20134 | 19509 | 17228 | 16729 | 19420 | 20670 | 21434
4713 | 4713 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 9 | 15410 | 17109 | 18136 | 17056 | 14930 | 16911 | 17271 | 18643 | 19399 | 16275 | 15861 | 18288 | 18576 | 20843 | 20044 | 17899 | 17335 | 19648 | 21107 | 22165
4714 | 4714 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 10 | 15745 | 17561 | 18665 | 17409 | 15343 | 17272 | 17755 | 19194 | 20009 | 16796 | 16597 | 18757 | 19201 | 21536 | 20593 | 18529 | 18151 | 20337 | 21808 | 22910
4715 | 4715 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 11 | 16002 | 17964 | 19128 | 17634 | 15603 | 17655 | 18193 | 19697 | 20557 | 17177 | 17161 | 19262 | 19759 | 22209 | 21010 | 19009 | 18755 | 20984 | 22477 | 23651
4716 | 4716 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 12 | 16224 | 18433 | 19541 | 17788 | 15838 | 17902 | 18596 | 20284 | 21027 | 17451 | 17632 | 19574 | 20258 | 22737 | 21268 | 19325 | 19266 | 21522 | 23216 | 24210
4717 | 4717 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 13 | 16424 | 18788 | 19836 | 17917 | 15923 | 18140 | 18930 | 20665 | 21360 | 17560 | 17913 | 19848 | 20635 | 23098 | 21442 | 19453 | 19568 | 21917 | 23637 | 24603
4718 | 4718 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 14 | 16476 | 19024 | 20016 | 18020 | 16001 | 18202 | 19094 | 20923 | 21505 | 17633 | 18135 | 19914 | 20776 | 23234 | 21531 | 19512 | 19767 | 22054 | 23911 | 24718
4719 | 4719 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 15 | 16541 | 19267 | 20203 | 18110 | 16192 | 18304 | 19295 | 21168 | 21664 | 17843 | 18397 | 20039 | 20973 | 23378 | 21588 | 19704 | 19993 | 22273 | 24164 | 24852
4720 | 4720 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 16 | 16886 | 19706 | 20568 | 18446 | 16539 | 18654 | 19916 | 21560 | 21947 | 18167 | 18883 | 20345 | 21682 | 23564 | 21782 | 19968 | 20428 | 22993 | 24455 | 24988
4721 | 4721 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 17 | 17282 | 20030 | 20905 | 18762 | 17147 | 19092 | 20432 | 21941 | 22286 | 18805 | 19596 | 20787 | 22241 | 23996 | 22099 | 20641 | 21191 | 23565 | 24854 | 25446
4722 | 4722 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 18 | 17280 | 20127 | 21062 | 18984 | 17550 | 19262 | 20479 | 22052 | 22742 | 19483 | 20300 | 21182 | 22430 | 24614 | 22749 | 21520 | 22089 | 23834 | 25261 | 26163
4723 | 4723 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 19 | 17399 | 20389 | 20986 | 18949 | 17668 | 19417 | 20818 | 22468 | 22903 | 19763 | 20787 | 21636 | 23065 | 25068 | 23261 | 22081 | 22826 | 24636 | 26166 | 26733
4724 | 4724 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 20 | 17396 | 20335 | 20906 | 18520 | 17451 | 19499 | 20951 | 22581 | 23034 | 19634 | 20837 | 21974 | 23647 | 25555 | 23505 | 22385 | 23091 | 25365 | 26782 | 27342
4725 | 4725 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 21 | 17057 | 19691 | 20245 | 17749 | 17013 | 19247 | 20575 | 22190 | 22679 | 19517 | 20877 | 22043 | 23701 | 25633 | 23528 | 22712 | 23478 | 25649 | 27092 | 27632
4726 | 4726 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 22 | 16193 | 18755 | 19264 | 16992 | 16654 | 18407 | 19741 | 21411 | 21890 | 19334 | 20522 | 21392 | 23126 | 25077 | 23234 | 22779 | 23327 | 25213 | 26758 | 27215
4727 | 4727 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 23 | 14987 | 17326 | 17874 | 15767 | 15924 | 17142 | 18408 | 20000 | 20529 | 18646 | 19615 | 20150 | 21862 | 23796 | 22114 | 22157 | 22469 | 24001 | 25466 | 25986
4728 | 4728 | 197 | 7 | 16 | Summer | 7 | 15 | Summer | 24 | 13971 | 16102 | 16526 | 14694 | 15092 | 16004 | 17236 | 18692 | 19140 | 17795 | 18726 | 18982 | 20706 | 22424 | 20987 | 21315 | 21611 | 22845 | 24209 | 24608
4729 | 4729 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 1 | 13237 | 14873 | 14940 | 14187 | 14283 | 15296 | 16488 | 17419 | 17509 | 16545 | 17994 | 18536 | 19971 | 20811 | 20078 | 19548 | 20790 | 22122 | 23050 | 23001
4730 | 4730 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 2 | 12870 | 14367 | 14383 | 13795 | 13888 | 14829 | 15963 | 16826 | 16854 | 16062 | 17440 | 17941 | 19301 | 20032 | 19454 | 18934 | 20142 | 21376 | 22256 | 22145
4731 | 4731 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 3 | 12631 | 14019 | 14005 | 13517 | 13570 | 14517 | 15629 | 16378 | 16371 | 15651 | 17068 | 17482 | 18811 | 19391 | 18925 | 18394 | 19661 | 20803 | 21559 | 21417
4732 | 4732 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 4 | 12622 | 13948 | 13861 | 13408 | 13381 | 14437 | 15439 | 16139 | 15982 | 15274 | 16752 | 17086 | 18261 | 18686 | 18270 | 17748 | 19093 | 20073 | 20793 | 20528
4733 | 4733 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 5 | 12879 | 14186 | 14038 | 13246 | 13222 | 14583 | 15629 | 16219 | 15894 | 14860 | 16722 | 16859 | 18049 | 18257 | 17476 | 17041 | 18771 | 19642 | 20234 | 19890
4734 | 4734 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 6 | 13695 | 14900 | 14686 | 13179 | 13175 | 15250 | 16303 | 16731 | 16264 | 14557 | 17140 | 17157 | 18293 | 18258 | 16720 | 16390 | 18931 | 19648 | 20080 | 19702
4735 | 4735 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 7 | 14878 | 16174 | 15725 | 13511 | 13348 | 16231 | 17405 | 17797 | 17098 | 14576 | 18105 | 17827 | 19035 | 18753 | 16507 | 16104 | 19714 | 20210 | 20703 | 20091
4736 | 4736 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 8 | 15553 | 17190 | 16618 | 14323 | 14050 | 16871 | 18151 | 18744 | 17931 | 15250 | 19182 | 18301 | 19645 | 19433 | 17186 | 16704 | 20714 | 20738 | 21468 | 20753
4737 | 4737 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 9 | 15943 | 17917 | 17241 | 15084 | 14751 | 17284 | 18717 | 19539 | 18525 | 15931 | 20091 | 18623 | 20184 | 20025 | 17925 | 17366 | 21599 | 21240 | 22251 | 21372
4738 | 4738 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 10 | 16285 | 18449 | 17602 | 15487 | 15388 | 17753 | 19259 | 20137 | 18953 | 16673 | 20926 | 19231 | 20814 | 20571 | 18554 | 18180 | 22485 | 21943 | 23002 | 21976
4739 | 4739 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 11 | 16621 | 18906 | 17836 | 15772 | 15906 | 18183 | 19761 | 20705 | 19296 | 17247 | 21637 | 19806 | 21443 | 20993 | 19041 | 18817 | 23272 | 22623 | 23753 | 22453
4740 | 4740 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 12 | 16833 | 19196 | 17876 | 15888 | 16227 | 18465 | 20229 | 21051 | 19390 | 17599 | 22098 | 20177 | 22017 | 21136 | 19246 | 19208 | 23789 | 23246 | 24201 | 22628
4741 | 4741 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 13 | 16994 | 19370 | 17861 | 15828 | 16337 | 18650 | 20463 | 21232 | 19408 | 17738 | 22451 | 20406 | 22278 | 21167 | 19230 | 19367 | 24148 | 23522 | 24447 | 22677
4742 | 4742 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 14 | 17014 | 19423 | 17837 | 15789 | 16439 | 18689 | 20585 | 21273 | 19380 | 17838 | 22675 | 20433 | 22417 | 21133 | 19167 | 19448 | 24363 | 23664 | 24437 | 22642
4743 | 4743 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 15 | 17107 | 19494 | 17816 | 15888 | 16622 | 18778 | 20722 | 21343 | 19366 | 17997 | 22935 | 20530 | 22576 | 21083 | 19249 | 19587 | 24623 | 23803 | 24460 | 22589
4744 | 4744 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 16 | 17467 | 19752 | 18043 | 16145 | 17055 | 19280 | 21013 | 21547 | 19557 | 18380 | 23279 | 21137 | 22818 | 21182 | 19409 | 19930 | 24941 | 23983 | 24493 | 22655
4745 | 4745 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 17 | 17990 | 20110 | 18384 | 16775 | 17700 | 19830 | 21428 | 21901 | 19939 | 19115 | 23804 | 21725 | 23252 | 21538 | 20125 | 20718 | 25558 | 24425 | 24987 | 23031
4746 | 4746 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 18 | 18021 | 20310 | 18605 | 17216 | 18309 | 19939 | 21591 | 22365 | 20444 | 19847 | 24380 | 21969 | 23623 | 22241 | 21057 | 21697 | 26233 | 24899 | 25770 | 23805
4747 | 4747 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 19 | 18311 | 20284 | 18626 | 17386 | 18650 | 20342 | 22057 | 22550 | 20602 | 20352 | 24610 | 22626 | 24414 | 22794 | 21668 | 22478 | 26673 | 25880 | 26422 | 24501
4748 | 4748 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 20 | 18354 | 20213 | 18189 | 17146 | 18509 | 20481 | 22164 | 22626 | 20397 | 20355 | 24481 | 23146 | 24845 | 23006 | 21954 | 22722 | 26753 | 26522 | 27057 | 24843
4749 | 4749 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 21 | 17827 | 19536 | 17378 | 16655 | 18193 | 20056 | 21701 | 22176 | 19890 | 20316 | 24184 | 23110 | 24855 | 22951 | 22216 | 23058 | 26765 | 26803 | 27328 | 25003
4750 | 4750 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 22 | 16904 | 18553 | 16608 | 16272 | 17630 | 19192 | 20881 | 21332 | 19304 | 19929 | 23351 | 22480 | 24321 | 22618 | 22253 | 22876 | 26107 | 26452 | 26907 | 24810
4751 | 4751 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 23 | 15609 | 17139 | 15385 | 15549 | 16666 | 17854 | 19449 | 19942 | 18107 | 19011 | 21811 | 21195 | 22988 | 21473 | 21620 | 22008 | 24623 | 25158 | 25668 | 23706
4752 | 4752 | 198 | 7 | 17 | Summer | 7 | 16 | Summer | 24 | 14505 | 15826 | 14285 | 14732 | 15783 | 16675 | 18129 | 18530 | 16975 | 18114 | 20406 | 20023 | 21700 | 20337 | 20761 | 21155 | 23224 | 23893 | 24293 | 22580
4753 | 4753 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 1 | 13921 | 14335 | 13884 | 14047 | 15233 | 15993 | 16908 | 16966 | 16376 | 17470 | 19960 | 19347 | 20547 | 19525 | 19122 | 20403 | 23051 | 22794 | 22771 | 21650
4754 | 4754 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 2 | 13497 | 13811 | 13523 | 13667 | 14786 | 15492 | 16343 | 16338 | 15896 | 16945 | 19216 | 18708 | 19847 | 18935 | 18537 | 19772 | 22200 | 22018 | 21931 | 20978
4755 | 4755 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 3 | 13228 | 13437 | 13255 | 13350 | 14517 | 15171 | 15913 | 15871 | 15525 | 16592 | 18697 | 18236 | 19246 | 18429 | 18014 | 19305 | 21556 | 21326 | 21207 | 20388
4756 | 4756 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 4 | 13185 | 13310 | 13152 | 13181 | 14430 | 15008 | 15708 | 15543 | 15201 | 16311 | 18196 | 17746 | 18684 | 17805 | 17387 | 18765 | 20778 | 20573 | 20316 | 19587
4757 | 4757 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 5 | 13530 | 13497 | 13012 | 13045 | 14645 | 15244 | 15841 | 15528 | 14799 | 16333 | 18032 | 17603 | 18370 | 17062 | 16714 | 18473 | 20345 | 20023 | 19691 | 18655
4758 | 4758 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 6 | 14357 | 14194 | 12997 | 13036 | 15327 | 15988 | 16441 | 15995 | 14448 | 16835 | 18363 | 17928 | 18465 | 16378 | 16120 | 18669 | 20380 | 19907 | 19530 | 17793
4759 | 4759 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 7 | 15432 | 15133 | 13247 | 13117 | 16453 | 17007 | 17439 | 16786 | 14445 | 17739 | 19122 | 18606 | 19139 | 16085 | 15742 | 19363 | 20842 | 20412 | 19801 | 17388
4760 | 4760 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 8 | 16147 | 15971 | 14033 | 13775 | 17563 | 17708 | 18351 | 17612 | 15219 | 18797 | 20058 | 19207 | 19910 | 16723 | 16297 | 20323 | 21595 | 21120 | 20403 | 18024
4761 | 4761 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 9 | 16652 | 16544 | 14800 | 14458 | 18438 | 18249 | 19127 | 18205 | 15999 | 19703 | 20853 | 19734 | 20650 | 17439 | 16942 | 21190 | 22327 | 21872 | 20994 | 18752
4762 | 4762 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 10 | 17095 | 16859 | 15176 | 15080 | 19161 | 18749 | 19695 | 18610 | 16495 | 20507 | 21710 | 20345 | 21328 | 18032 | 17727 | 22062 | 23274 | 22600 | 21568 | 19425
4763 | 4763 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 11 | 17388 | 16957 | 15335 | 15456 | 19680 | 19111 | 20127 | 18801 | 16758 | 21094 | 22457 | 20828 | 21893 | 18387 | 18239 | 22710 | 24112 | 23228 | 21920 | 19848
4764 | 4764 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 12 | 17772 | 17072 | 15529 | 15850 | 20185 | 19645 | 20544 | 18966 | 16990 | 21640 | 23122 | 21467 | 22376 | 18671 | 18710 | 23285 | 24817 | 23751 | 22182 | 20153
4765 | 4765 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 13 | 18047 | 17152 | 15541 | 16036 | 20592 | 19949 | 20803 | 19055 | 17019 | 22068 | 23689 | 21792 | 22666 | 18730 | 18943 | 23721 | 25394 | 24064 | 22305 | 20227
4766 | 4766 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 14 | 18239 | 17196 | 15591 | 16227 | 20906 | 20163 | 20935 | 19121 | 17061 | 22380 | 24146 | 22020 | 22773 | 18761 | 19116 | 24026 | 25835 | 24143 | 22355 | 20243
4767 | 4767 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 15 | 18462 | 17264 | 15782 | 16487 | 21268 | 20390 | 21096 | 19184 | 17252 | 22731 | 24578 | 22256 | 22911 | 18939 | 19351 | 24363 | 26243 | 24266 | 22389 | 20422
4768 | 4768 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 16 | 18793 | 17486 | 16038 | 16902 | 21661 | 20693 | 21314 | 19371 | 17471 | 23085 | 25372 | 22496 | 23008 | 19110 | 19699 | 24667 | 27051 | 24298 | 22455 | 20573
4769 | 4769 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 17 | 19147 | 17832 | 16648 | 17537 | 22197 | 21100 | 21654 | 19722 | 18120 | 23597 | 25949 | 22921 | 23468 | 19820 | 20483 | 25286 | 27603 | 24784 | 22814 | 21311
4770 | 4770 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 18 | 19307 | 18005 | 17013 | 18107 | 22545 | 21247 | 22065 | 20153 | 18822 | 24134 | 26279 | 23270 | 24126 | 20726 | 21440 | 25943 | 28055 | 25562 | 23577 | 22300
4771 | 4771 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 19 | 19620 | 18012 | 17127 | 18412 | 22504 | 21665 | 22181 | 20259 | 19121 | 24275 | 26287 | 23987 | 24580 | 21273 | 22170 | 26350 | 28401 | 26180 | 24256 | 22958
4772 | 4772 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 20 | 19567 | 17557 | 16853 | 18268 | 22176 | 21744 | 22218 | 20011 | 18956 | 24072 | 26041 | 24366 | 25027 | 21508 | 22384 | 26428 | 28449 | 26822 | 24599 | 23295
4773 | 4773 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 21 | 18905 | 16721 | 16346 | 17948 | 21568 | 21244 | 21721 | 19438 | 18753 | 23716 | 25462 | 24327 | 25043 | 21725 | 22690 | 26431 | 28244 | 27099 | 24767 | 23722
4774 | 4774 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 22 | 17954 | 15941 | 15943 | 17370 | 20544 | 20376 | 20824 | 18803 | 18521 | 22838 | 24594 | 23738 | 24445 | 21716 | 22474 | 25751 | 27590 | 26654 | 24563 | 23839
4775 | 4775 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 23 | 16545 | 14728 | 15223 | 16412 | 18981 | 18940 | 19419 | 17581 | 17826 | 21279 | 22934 | 22368 | 23136 | 21079 | 21595 | 24247 | 26004 | 25421 | 23479 | 23245
4776 | 4776 | 199 | 7 | 18 | Summer | 7 | 17 | Summer | 24 | 15341 | 13645 | 14394 | 15525 | 17592 | 17614 | 17996 | 16417 | 16974 | 19870 | 21598 | 21059 | 21728 | 20217 | 20735 | 22830 | 24707 | 24041 | 22340 | 22376
4777 | 4777 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 1 | 14303 | 13372 | 13866 | 15089 | 16997 | 16494 | 16536 | 15951 | 15993 | 19471 | 21118 | 19991 | 20277 | 18748 | 20086 | 22727 | 24319 | 22599 | 21519 | 20623
4778 | 4778 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 2 | 13811 | 13021 | 13501 | 14645 | 16333 | 15939 | 15920 | 15485 | 15536 | 18741 | 20290 | 19308 | 19519 | 18169 | 19468 | 21884 | 23395 | 21762 | 20848 | 19975
4779 | 4779 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 3 | 13479 | 12784 | 13202 | 14394 | 15913 | 15534 | 15483 | 15145 | 15153 | 18255 | 19675 | 18744 | 18906 | 17665 | 19012 | 21262 | 22657 | 21054 | 20269 | 19409
4780 | 4780 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 4 | 13417 | 12672 | 13046 | 14320 | 15722 | 15361 | 15201 | 14874 | 14828 | 17805 | 19181 | 18238 | 18257 | 17072 | 18499 | 20511 | 21895 | 20178 | 19480 | 18664
4781 | 4781 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 5 | 13663 | 12561 | 12932 | 14558 | 15883 | 15543 | 15252 | 14541 | 14468 | 17714 | 18968 | 17995 | 17894 | 16443 | 18242 | 20113 | 21344 | 19580 | 18553 | 17879
4782 | 4782 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 6 | 14386 | 12548 | 12938 | 15277 | 16483 | 16174 | 15775 | 14282 | 14210 | 18105 | 19297 | 18180 | 17950 | 15875 | 18456 | 20186 | 21306 | 19414 | 17683 | 17164
4783 | 4783 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 7 | 15592 | 12870 | 13089 | 16446 | 17562 | 17231 | 16654 | 14370 | 14193 | 18970 | 20268 | 18942 | 18415 | 15566 | 19207 | 20699 | 22020 | 19726 | 17314 | 16761
4784 | 4784 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 8 | 16516 | 13612 | 13722 | 17498 | 18621 | 18087 | 17441 | 15109 | 14791 | 19891 | 21404 | 19686 | 19029 | 16082 | 20129 | 21416 | 23048 | 20276 | 17891 | 17277
4785 | 4785 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 9 | 17116 | 14290 | 14372 | 18323 | 19469 | 18794 | 17986 | 15867 | 15411 | 20665 | 22301 | 20383 | 19558 | 16678 | 20948 | 22117 | 23862 | 20805 | 18559 | 17875
4786 | 4786 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 10 | 17605 | 14625 | 14959 | 18995 | 20249 | 19315 | 18344 | 16307 | 16095 | 21474 | 23252 | 21007 | 20045 | 17417 | 21782 | 23006 | 24904 | 21338 | 19186 | 18669
4787 | 4787 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 11 | 17979 | 14830 | 15374 | 19544 | 20901 | 19772 | 18562 | 16594 | 16589 | 22254 | 23989 | 21586 | 20382 | 17964 | 22470 | 23870 | 25734 | 21727 | 19645 | 19253
4788 | 4788 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 12 | 18345 | 15026 | 15782 | 20068 | 21462 | 20200 | 18738 | 16845 | 17028 | 22935 | 24688 | 22088 | 20618 | 18450 | 23062 | 24602 | 26495 | 22004 | 19972 | 19761
4789 | 4789 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 13 | 18608 | 15044 | 15987 | 20510 | 21888 | 20475 | 18843 | 16902 | 17245 | 23516 | 25056 | 22399 | 20732 | 18706 | 23524 | 25204 | 26858 | 22144 | 20067 | 20035
4790 | 4790 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 14 | 18780 | 15125 | 16205 | 20853 | 22185 | 20639 | 18942 | 16982 | 17460 | 24016 | 25329 | 22534 | 20817 | 18904 | 23842 | 25667 | 27100 | 22213 | 20105 | 20226
4791 | 4791 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 15 | 18942 | 15281 | 16452 | 21209 | 22446 | 20792 | 18992 | 17161 | 17709 | 24433 | 25549 | 22668 | 20845 | 19134 | 24178 | 26064 | 27315 | 22237 | 20274 | 20450
4792 | 4792 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 16 | 19240 | 15586 | 16925 | 21663 | 23061 | 21085 | 19247 | 17450 | 18139 | 25293 | 25799 | 22845 | 20997 | 19547 | 24546 | 26937 | 27475 | 22362 | 20480 | 20842
4793 | 4793 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 17 | 19548 | 16140 | 17506 | 22158 | 23440 | 21384 | 19560 | 18057 | 18812 | 25817 | 26220 | 23255 | 21297 | 20283 | 25118 | 27443 | 27920 | 22680 | 21164 | 21601
4794 | 4794 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 18 | 19737 | 16505 | 18017 | 22489 | 23644 | 21774 | 19942 | 18703 | 19533 | 26117 | 26467 | 23879 | 21965 | 21242 | 25784 | 27896 | 28323 | 23447 | 22159 | 22621
4795 | 4795 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 19 | 19625 | 16585 | 18253 | 22383 | 23631 | 21830 | 19960 | 18911 | 19941 | 26028 | 26719 | 24241 | 22427 | 21901 | 26118 | 28188 | 28833 | 24085 | 22789 | 23382
4796 | 4796 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 20 | 19544 | 16265 | 18075 | 22028 | 23334 | 21838 | 19668 | 18677 | 19893 | 25672 | 26738 | 24619 | 22585 | 22074 | 26167 | 28204 | 29265 | 24430 | 23132 | 23628
4797 | 4797 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 21 | 18855 | 15733 | 17719 | 21391 | 22594 | 21288 | 19024 | 18388 | 19790 | 25007 | 26576 | 24540 | 22457 | 22322 | 26126 | 27956 | 29519 | 24583 | 23546 | 24054
4798 | 4798 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 22 | 17873 | 15336 | 17150 | 20382 | 21540 | 20375 | 18362 | 18128 | 19365 | 24103 | 25747 | 23904 | 22085 | 22093 | 25440 | 27298 | 28937 | 24385 | 23679 | 23952
4799 | 4799 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 23 | 16452 | 14630 | 16188 | 18810 | 19907 | 18957 | 17122 | 17402 | 18436 | 22434 | 24147 | 22573 | 20934 | 21209 | 23918 | 25697 | 27395 | 23281 | 23078 | 23094
4800 | 4800 | 200 | 7 | 19 | Summer | 7 | 18 | Summer | 24 | 15212 | 13866 | 15331 | 17460 | 18556 | 17572 | 15981 | 16567 | 17552 | 21111 | 22682 | 21186 | 19803 | 20366 | 22521 | 24409 | 25961 | 22164 | 22240 | 22261
4801 | 4801 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 1 | 13748 | 13300 | 14826 | 16751 | 17890 | 16017 | 15455 | 15576 | 16937 | 20512 | 21418 | 19626 | 19030 | 19632 | 22288 | 23907 | 24651 | 21267 | 20425 | 21479
4802 | 4802 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 2 | 13232 | 12911 | 14389 | 16084 | 17176 | 15407 | 14992 | 15122 | 16422 | 19692 | 20575 | 18881 | 18443 | 19010 | 21444 | 22980 | 23703 | 20590 | 19770 | 20796
4803 | 4803 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 3 | 12873 | 12629 | 14148 | 15674 | 16687 | 14988 | 14671 | 14757 | 16097 | 19104 | 19943 | 18295 | 17959 | 18569 | 20837 | 22250 | 22917 | 20017 | 19202 | 20292
4804 | 4804 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 4 | 12769 | 12488 | 14089 | 15488 | 16489 | 14745 | 14448 | 14461 | 15870 | 18667 | 19379 | 17694 | 17391 | 18092 | 20120 | 21503 | 22042 | 19248 | 18467 | 19670
4805 | 4805 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 5 | 12976 | 12402 | 14344 | 15681 | 16627 | 14840 | 14178 | 14162 | 15955 | 18522 | 19199 | 17407 | 16718 | 17875 | 19764 | 20992 | 21461 | 18352 | 17691 | 19303
4806 | 4806 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 6 | 13704 | 12419 | 15092 | 16338 | 17366 | 15405 | 13986 | 14001 | 16531 | 18926 | 19450 | 17570 | 16107 | 18129 | 19880 | 21013 | 21298 | 17500 | 16985 | 19423
4807 | 4807 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 7 | 14709 | 12605 | 16328 | 17487 | 18673 | 16338 | 14160 | 14079 | 17535 | 19991 | 20409 | 18133 | 15927 | 18940 | 20461 | 21805 | 21861 | 17170 | 16613 | 20159
4808 | 4808 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 8 | 15526 | 13327 | 17464 | 18627 | 19929 | 17195 | 14975 | 14756 | 18598 | 21236 | 21488 | 18836 | 16577 | 19939 | 21265 | 22917 | 22805 | 17802 | 17187 | 21153
4809 | 4809 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 9 | 16071 | 14107 | 18404 | 19558 | 20904 | 17805 | 15829 | 15474 | 19531 | 22238 | 22467 | 19442 | 17334 | 20843 | 22057 | 23815 | 23765 | 18551 | 17866 | 22057
4810 | 4810 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 10 | 16397 | 14721 | 19131 | 20368 | 21798 | 18205 | 16297 | 16191 | 20352 | 23227 | 23351 | 19956 | 17926 | 21722 | 22993 | 24889 | 24826 | 19217 | 18709 | 22990
4811 | 4811 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 11 | 16522 | 15145 | 19680 | 21003 | 22427 | 18415 | 16566 | 16672 | 20968 | 23962 | 24053 | 20278 | 18303 | 22408 | 23856 | 25712 | 25809 | 19670 | 19297 | 23715
4812 | 4812 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 12 | 16584 | 15482 | 20136 | 21502 | 22977 | 18515 | 16748 | 17046 | 21465 | 24587 | 24562 | 20443 | 18548 | 22923 | 24519 | 26405 | 26606 | 19933 | 19731 | 24257
4813 | 4813 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 13 | 16708 | 15709 | 20587 | 21955 | 23345 | 18626 | 16809 | 17286 | 21928 | 24967 | 24893 | 20583 | 18642 | 23396 | 25132 | 26795 | 27282 | 20034 | 20012 | 24735
4814 | 4814 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 14 | 16884 | 16030 | 21044 | 22369 | 23719 | 18840 | 17005 | 17629 | 22392 | 25362 | 25098 | 20778 | 18815 | 23843 | 25713 | 27152 | 27581 | 20186 | 20319 | 25183
4815 | 4815 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 15 | 16962 | 16298 | 21414 | 22652 | 23965 | 18915 | 17199 | 17891 | 22757 | 25605 | 25245 | 20840 | 18999 | 24201 | 26133 | 27384 | 27809 | 20361 | 20561 | 25533
4816 | 4816 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 16 | 17249 | 16748 | 21870 | 23260 | 24303 | 19177 | 17493 | 18344 | 23183 | 25862 | 25365 | 21026 | 19248 | 24578 | 27005 | 27570 | 28055 | 20572 | 20962 | 25893
4817 | 4817 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 17 | 17530 | 17280 | 22318 | 23609 | 24695 | 19451 | 18051 | 18976 | 23625 | 26244 | 25632 | 21289 | 19879 | 25114 | 27486 | 27983 | 28350 | 21227 | 21685 | 26452
4818 | 4818 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 18 | 17562 | 17627 | 22442 | 23669 | 24625 | 19682 | 18501 | 19491 | 24005 | 26325 | 25850 | 21791 | 20630 | 25631 | 27787 | 28237 | 28678 | 22079 | 22575 | 27037
4819 | 4819 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 19 | 17388 | 17719 | 22191 | 23501 | 24477 | 19544 | 18563 | 19724 | 23930 | 26387 | 26239 | 22052 | 20971 | 25815 | 27923 | 28586 | 28981 | 22593 | 23210 | 27306
4820 | 4820 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 20 | 16903 | 17527 | 21807 | 23158 | 24237 | 19228 | 18300 | 19620 | 23645 | 26314 | 26390 | 22122 | 21129 | 25823 | 27895 | 28974 | 29122 | 22940 | 23459 | 27375
4821 | 4821 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 21 | 16027 | 17120 | 21111 | 22352 | 23628 | 18504 | 17916 | 19425 | 23199 | 26029 | 26294 | 21880 | 21249 | 25697 | 27559 | 29153 | 29319 | 23305 | 23846 | 27414
4822 | 4822 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 22 | 15239 | 16524 | 20063 | 21254 | 22513 | 17784 | 17598 | 18943 | 22282 | 25125 | 25468 | 21434 | 21198 | 24958 | 26847 | 28524 | 28618 | 23405 | 23703 | 26778
4823 | 4823 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 23 | 14034 | 15565 | 18510 | 19636 | 20831 | 16546 | 16873 | 18000 | 20714 | 23517 | 23937 | 20259 | 20543 | 23437 | 25233 | 26977 | 27178 | 22807 | 22855 | 25290
4824 | 4824 | 201 | 7 | 20 | Summer | 7 | 19 | Summer | 24 | 13026 | 14715 | 17150 | 18292 | 19342 | 15419 | 16034 | 17110 | 19323 | 22039 | 22410 | 19127 | 19702 | 22038 | 23943 | 25532 | 25581 | 21969 | 22026 | 23900
4825 | 4825 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 1 | 12762 | 14287 | 16499 | 17676 | 18134 | 14993 | 15183 | 16564 | 18849 | 20823 | 20734 | 18450 | 18281 | 21818 | 23494 | 24272 | 24151 | 20239 | 21313 | 23839
4826 | 4826 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 2 | 12422 | 13884 | 15870 | 16976 | 17415 | 14563 | 14761 | 16071 | 18130 | 20017 | 19893 | 17894 | 17714 | 21007 | 22594 | 23350 | 23181 | 19607 | 20656 | 22969
4827 | 4827 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 3 | 12214 | 13663 | 15489 | 16514 | 16940 | 14274 | 14428 | 15780 | 17656 | 19428 | 19264 | 17453 | 17243 | 20432 | 21896 | 22596 | 22408 | 19061 | 20169 | 22322
4828 | 4828 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 4 | 12087 | 13601 | 15305 | 16315 | 16655 | 14075 | 14159 | 15574 | 17263 | 18915 | 18711 | 16921 | 16673 | 19743 | 21170 | 21730 | 21538 | 18328 | 19542 | 21473
4829 | 4829 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 5 | 11971 | 13853 | 15488 | 16453 | 16832 | 13825 | 13880 | 15682 | 17210 | 18786 | 18504 | 16288 | 16071 | 19406 | 20678 | 21159 | 20932 | 17543 | 19156 | 20956
4830 | 4830 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 6 | 11964 | 14612 | 16155 | 17195 | 17468 | 13673 | 13772 | 16300 | 17634 | 19124 | 18741 | 15731 | 15554 | 19569 | 20741 | 21001 | 20788 | 16848 | 19278 | 20936
4831 | 4831 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 7 | 12388 | 15915 | 17386 | 18586 | 18722 | 13918 | 13942 | 17419 | 18626 | 20197 | 19583 | 15671 | 15362 | 20230 | 21616 | 21640 | 21398 | 16525 | 20055 | 21469
4832 | 4832 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 8 | 13350 | 17218 | 18721 | 20039 | 20047 | 14889 | 14787 | 18693 | 19822 | 21468 | 20540 | 16527 | 16114 | 21213 | 22904 | 22784 | 22252 | 17251 | 21199 | 22397
4833 | 4833 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 9 | 14031 | 18086 | 19622 | 20967 | 20957 | 15679 | 15457 | 19596 | 20640 | 22407 | 21375 | 17239 | 16755 | 21954 | 23762 | 23696 | 23121 | 17872 | 22045 | 23127
4834 | 4834 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 10 | 14357 | 18769 | 20385 | 21793 | 21691 | 16073 | 16108 | 20352 | 21501 | 23225 | 22066 | 17763 | 17486 | 22833 | 24772 | 24691 | 23906 | 18657 | 22922 | 24064
4835 | 4835 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 11 | 14540 | 19305 | 21014 | 22415 | 22266 | 16315 | 16568 | 20959 | 22223 | 23903 | 22569 | 18126 | 18017 | 23679 | 25575 | 25664 | 24501 | 19233 | 23636 | 24960
4836 | 4836 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 12 | 14792 | 19881 | 21646 | 23089 | 22832 | 16622 | 17067 | 21575 | 22893 | 24528 | 23006 | 18490 | 18568 | 24463 | 26402 | 26579 | 24998 | 19802 | 24311 | 25766
4837 | 4837 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 13 | 14911 | 20426 | 22190 | 23538 | 23219 | 16771 | 17392 | 22121 | 23468 | 24951 | 23309 | 18671 | 18937 | 25169 | 26882 | 27340 | 25329 | 20166 | 24881 | 26485
4838 | 4838 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 14 | 15004 | 20776 | 22525 | 23827 | 23338 | 16873 | 17639 | 22494 | 23786 | 25070 | 23404 | 18756 | 19151 | 25659 | 27148 | 27550 | 25376 | 20378 | 25232 | 26970
4839 | 4839 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 15 | 15047 | 21044 | 22714 | 23971 | 23388 | 16961 | 17796 | 22759 | 23937 | 25120 | 23381 | 18841 | 19286 | 25982 | 27273 | 27678 | 25324 | 20514 | 25479 | 27281
4840 | 4840 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 16 | 15182 | 21346 | 23111 | 24156 | 23449 | 17112 | 18105 | 23037 | 24485 | 25113 | 23428 | 18941 | 19543 | 26711 | 27317 | 27772 | 25289 | 20759 | 25682 | 27997
4841 | 4841 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 17 | 15607 | 21689 | 23379 | 24460 | 23548 | 17590 | 18651 | 23380 | 24752 | 25306 | 23550 | 19472 | 20158 | 27104 | 27643 | 27974 | 25494 | 21395 | 26150 | 28408
4842 | 4842 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 18 | 15802 | 21786 | 23424 | 24369 | 23545 | 18004 | 19108 | 23687 | 24857 | 25468 | 23877 | 20164 | 20961 | 27383 | 27860 | 28273 | 25963 | 22268 | 26720 | 28754
4843 | 4843 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 19 | 15884 | 21633 | 23328 | 24330 | 23795 | 18162 | 19428 | 23699 | 24888 | 25903 | 24165 | 20580 | 21565 | 27584 | 28297 | 28682 | 26543 | 23021 | 27110 | 29093
4844 | 4844 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 20 | 15562 | 21230 | 22942 | 24059 | 23675 | 17883 | 19303 | 23385 | 24786 | 25953 | 24067 | 20690 | 21707 | 27516 | 28641 | 28809 | 26791 | 23289 | 27194 | 29140
4845 | 4845 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 21 | 15005 | 20533 | 22113 | 23414 | 23181 | 17471 | 19078 | 22887 | 24273 | 25780 | 23858 | 20735 | 21885 | 27149 | 28787 | 28971 | 27009 | 23689 | 27254 | 28980
4846 | 4846 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 22 | 14596 | 19462 | 20996 | 22276 | 22134 | 17121 | 18561 | 21932 | 23356 | 24909 | 23157 | 20632 | 21613 | 26399 | 28124 | 28243 | 26564 | 23534 | 26614 | 28364
4847 | 4847 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 23 | 13922 | 17943 | 19380 | 20622 | 20516 | 16402 | 17621 | 20366 | 21770 | 23363 | 21821 | 19976 | 20718 | 24779 | 26580 | 26810 | 25301 | 22688 | 25138 | 26805
4848 | 4848 | 202 | 7 | 21 | Summer | 7 | 20 | Summer | 24 | 13199 | 16622 | 18037 | 19135 | 19006 | 15573 | 16727 | 18962 | 20431 | 21820 | 20481 | 19127 | 19870 | 23485 | 25132 | 25204 | 23963 | 21857 | 23754 | 25538
4849 | 4849 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 1 | 12743 | 15964 | 17412 | 17908 | 17362 | 14787 | 16182 | 18416 | 19887 | 20125 | 19229 | 17790 | 19205 | 23010 | 23958 | 23761 | 22471 | 21135 | 23669 | 25123
4850 | 4850 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 2 | 12368 | 15347 | 16732 | 17202 | 16639 | 14376 | 15700 | 17717 | 19095 | 19304 | 18514 | 17247 | 18606 | 22123 | 23036 | 22809 | 21624 | 20481 | 22799 | 24173
4851 | 4851 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 3 | 12112 | 14968 | 16275 | 16729 | 16153 | 14048 | 15417 | 17254 | 18548 | 18695 | 17982 | 16788 | 18197 | 21434 | 22299 | 22042 | 20961 | 19991 | 22150 | 23411
4852 | 4852 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 4 | 11981 | 14812 | 16106 | 16484 | 15930 | 13825 | 15264 | 16930 | 18167 | 18224 | 17380 | 16286 | 17759 | 20766 | 21504 | 21217 | 20058 | 19394 | 21326 | 22576
4853 | 4853 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 5 | 11883 | 15004 | 16259 | 16685 | 16055 | 13583 | 15414 | 16929 | 18067 | 18093 | 16850 | 15739 | 17562 | 20326 | 21026 | 20647 | 19227 | 19026 | 20818 | 21933
4854 | 4854 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 6 | 11888 | 15681 | 16988 | 17339 | 16617 | 13485 | 16064 | 17393 | 18521 | 18395 | 16328 | 15270 | 17844 | 20424 | 20920 | 20521 | 18391 | 19142 | 20794 | 21832
4855 | 4855 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 7 | 12019 | 16831 | 18259 | 18506 | 17670 | 13561 | 17109 | 18339 | 19572 | 19191 | 16254 | 15019 | 18617 | 21225 | 21569 | 21036 | 17994 | 19800 | 21205 | 22479
4856 | 4856 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 8 | 12669 | 17953 | 19473 | 19597 | 18516 | 14158 | 18150 | 19345 | 20758 | 19945 | 17055 | 15548 | 19546 | 22286 | 22539 | 21670 | 18661 | 20688 | 21883 | 23480
4857 | 4857 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 9 | 13389 | 18824 | 20376 | 20469 | 19297 | 14796 | 19028 | 20153 | 21689 | 20760 | 18006 | 16168 | 20375 | 23121 | 23476 | 22496 | 19609 | 21499 | 22582 | 24294
4858 | 4858 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 10 | 13978 | 19608 | 21235 | 21227 | 19915 | 15458 | 19800 | 21040 | 22649 | 21464 | 18756 | 16922 | 21233 | 24156 | 24411 | 23311 | 20468 | 22405 | 23548 | 25390
4859 | 4859 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 11 | 14450 | 20282 | 21926 | 21860 | 20366 | 15964 | 20457 | 21818 | 23416 | 22011 | 19335 | 17508 | 21964 | 25009 | 25240 | 23958 | 21146 | 23175 | 24499 | 26296
4860 | 4860 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 12 | 14830 | 20814 | 22531 | 22343 | 20651 | 16376 | 20983 | 22398 | 24071 | 22352 | 19708 | 17972 | 22524 | 25744 | 25845 | 24366 | 21565 | 23763 | 25222 | 27071
4861 | 4861 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 13 | 15108 | 21327 | 22979 | 22679 | 20877 | 16660 | 21500 | 22924 | 24494 | 22622 | 19892 | 18292 | 23052 | 26182 | 26255 | 24650 | 21760 | 24299 | 25900 | 27516
4862 | 4862 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 14 | 15312 | 21636 | 23263 | 22785 | 20959 | 16879 | 21839 | 23218 | 24772 | 22692 | 20032 | 18503 | 23389 | 26434 | 26305 | 24692 | 21886 | 24632 | 26369 | 27775
4863 | 4863 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 15 | 15544 | 21916 | 23489 | 22922 | 21029 | 17101 | 22173 | 23450 | 24977 | 22746 | 20188 | 18715 | 23718 | 26625 | 26399 | 24718 | 22036 | 24940 | 26745 | 27964
4864 | 4864 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 16 | 15916 | 22364 | 23768 | 23084 | 21237 | 17494 | 22530 | 24051 | 25189 | 22891 | 20462 | 19069 | 24033 | 26757 | 26374 | 24777 | 22277 | 25220 | 27536 | 28060
4865 | 4865 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 17 | 16461 | 22760 | 24187 | 23295 | 21486 | 18150 | 22979 | 24432 | 25593 | 23121 | 21041 | 19784 | 24585 | 27193 | 26718 | 25089 | 22831 | 25796 | 28058 | 28507
4866 | 4866 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 18 | 16890 | 22937 | 24217 | 23387 | 21691 | 18722 | 23383 | 24655 | 25753 | 23552 | 21854 | 20655 | 25190 | 27522 | 27290 | 25672 | 23831 | 26494 | 28533 | 28924
4867 | 4867 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 19 | 17128 | 22827 | 24159 | 23646 | 21692 | 19069 | 23404 | 24678 | 25928 | 23803 | 22093 | 21268 | 25498 | 27949 | 28042 | 26264 | 24420 | 26921 | 28902 | 29500
4868 | 4868 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 20 | 16942 | 22375 | 23822 | 23479 | 21318 | 18940 | 23075 | 24505 | 25794 | 23612 | 21972 | 21347 | 25481 | 28246 | 28395 | 26474 | 24632 | 27025 | 28957 | 29941
4869 | 4869 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 21 | 16530 | 21504 | 23114 | 22934 | 20677 | 18661 | 22516 | 23906 | 25437 | 23294 | 21926 | 21448 | 25316 | 28318 | 28635 | 26641 | 24990 | 27066 | 28780 | 30249
4870 | 4870 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 22 | 15940 | 20381 | 21980 | 21867 | 19737 | 18135 | 21546 | 22943 | 24502 | 22558 | 21581 | 21132 | 24562 | 27629 | 27995 | 26169 | 24866 | 26432 | 28173 | 29714
4871 | 4871 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 23 | 15004 | 18770 | 20324 | 20265 | 18362 | 17194 | 19974 | 21353 | 22901 | 21205 | 20720 | 20231 | 23051 | 26072 | 26530 | 24900 | 24074 | 24947 | 26612 | 28207
4872 | 4872 | 203 | 7 | 22 | Summer | 7 | 21 | Summer | 24 | 14158 | 17427 | 18816 | 18752 | 17036 | 16289 | 18551 | 19982 | 21413 | 19836 | 19682 | 19362 | 21634 | 24607 | 25006 | 23544 | 23021 | 23546 | 25334 | 26759
4873 | 4873 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 1 | 13640 | 16721 | 17526 | 17027 | 15962 | 15679 | 17880 | 19326 | 20085 | 18552 | 18012 | 18619 | 21264 | 23355 | 23217 | 22000 | 20872 | 23365 | 24826 | 25411
4874 | 4874 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 2 | 13262 | 16064 | 16850 | 16331 | 15371 | 15220 | 17205 | 18568 | 19310 | 17870 | 17317 | 18054 | 20476 | 22450 | 22290 | 21183 | 20083 | 22510 | 23888 | 24451
4875 | 4875 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 3 | 13042 | 15622 | 16389 | 15844 | 14969 | 14947 | 16757 | 18030 | 18742 | 17361 | 16819 | 17654 | 19920 | 21730 | 21538 | 20525 | 19472 | 21867 | 23130 | 23637
4876 | 4876 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 4 | 13026 | 15479 | 16187 | 15669 | 14696 | 14849 | 16501 | 17727 | 18328 | 16842 | 16286 | 17288 | 19316 | 21004 | 20777 | 19679 | 18690 | 21080 | 22330 | 22730
4877 | 4877 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 5 | 13308 | 15664 | 16434 | 15847 | 14539 | 15060 | 16578 | 17710 | 18291 | 16404 | 15814 | 17169 | 19053 | 20598 | 20279 | 18906 | 17954 | 20616 | 21726 | 22091
4878 | 4878 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 6 | 14067 | 16421 | 17138 | 16458 | 14403 | 15756 | 17113 | 18236 | 18693 | 15974 | 15300 | 17528 | 19265 | 20568 | 20205 | 18119 | 17153 | 20624 | 21650 | 21848
4879 | 4879 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 7 | 15278 | 17717 | 18348 | 17553 | 14620 | 16828 | 18125 | 19347 | 19719 | 15981 | 15222 | 18362 | 19865 | 21266 | 20761 | 17757 | 16889 | 21055 | 22309 | 22342
4880 | 4880 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 8 | 16409 | 19003 | 19511 | 18470 | 15587 | 17919 | 19221 | 20629 | 20853 | 16894 | 15966 | 19370 | 20702 | 22308 | 21470 | 18498 | 17578 | 21804 | 23382 | 23293
4881 | 4881 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 9 | 17306 | 20016 | 20507 | 19341 | 16668 | 18878 | 20134 | 21666 | 21847 | 17961 | 17057 | 20298 | 21515 | 23343 | 22391 | 19535 | 18652 | 22594 | 24282 | 24296
4882 | 4882 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 10 | 18158 | 21005 | 21395 | 20074 | 17415 | 19766 | 21138 | 22745 | 22801 | 18834 | 18024 | 21279 | 22546 | 24395 | 23330 | 20514 | 19699 | 23681 | 25511 | 25491
4883 | 4883 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 11 | 18843 | 21779 | 22097 | 20589 | 17959 | 20484 | 21976 | 23568 | 23612 | 19474 | 18809 | 22075 | 23537 | 25283 | 24044 | 21262 | 20570 | 24703 | 26491 | 26638
4884 | 4884 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 12 | 19417 | 22465 | 22683 | 20958 | 18365 | 21095 | 22639 | 24303 | 24235 | 19929 | 19351 | 22721 | 24321 | 25971 | 24531 | 21762 | 21138 | 25511 | 27346 | 27590
4885 | 4885 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 13 | 19891 | 22901 | 23016 | 21157 | 18489 | 21579 | 23128 | 24701 | 24578 | 20081 | 19641 | 23221 | 24957 | 26344 | 24783 | 21928 | 21442 | 26162 | 27761 | 28313
4886 | 4886 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 14 | 20239 | 23214 | 23171 | 21257 | 18660 | 21945 | 23451 | 24991 | 24697 | 20252 | 19829 | 23589 | 25463 | 26425 | 24854 | 22082 | 21631 | 26655 | 28043 | 28529
4887 | 4887 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 15 | 20664 | 23563 | 23417 | 21422 | 18914 | 22377 | 23781 | 25294 | 24906 | 20508 | 20094 | 24010 | 25947 | 26615 | 24987 | 22322 | 21884 | 27128 | 28331 | 28813
4888 | 4888 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 16 | 21109 | 23941 | 23672 | 21701 | 19296 | 22811 | 24418 | 25578 | 25057 | 20864 | 20504 | 24396 | 26815 | 26672 | 25119 | 22625 | 22248 | 27985 | 28493 | 29025
4889 | 4889 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 17 | 21477 | 24321 | 23810 | 21898 | 19764 | 23191 | 24733 | 25928 | 25273 | 21371 | 21097 | 24886 | 27240 | 26950 | 25364 | 23122 | 22889 | 28442 | 28877 | 29295
4890 | 4890 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 18 | 21376 | 24036 | 23502 | 21766 | 20002 | 23261 | 24631 | 25785 | 25215 | 21825 | 21491 | 25145 | 27315 | 27184 | 25618 | 23808 | 23440 | 28600 | 28982 | 29456
4891 | 4891 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 19 | 21027 | 23698 | 23500 | 21522 | 19823 | 23060 | 24410 | 25682 | 25430 | 21782 | 21797 | 25182 | 27289 | 27696 | 25964 | 24148 | 23929 | 28754 | 29335 | 29742
4892 | 4892 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 20 | 20554 | 23197 | 23183 | 21024 | 19298 | 22653 | 24124 | 25409 | 25342 | 21487 | 21760 | 25037 | 27094 | 27920 | 26059 | 24246 | 24184 | 28738 | 29702 | 29821
4893 | 4893 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 21 | 19802 | 22417 | 22562 | 20325 | 18827 | 22040 | 23445 | 24959 | 25052 | 21342 | 21861 | 24788 | 26633 | 28078 | 26153 | 24546 | 24604 | 28529 | 29984 | 30053
4894 | 4894 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 22 | 18754 | 21283 | 21510 | 19396 | 18272 | 21073 | 22466 | 24000 | 24180 | 20972 | 21405 | 24015 | 25875 | 27428 | 25673 | 24424 | 24323 | 27932 | 29464 | 29425
4895 | 4895 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 23 | 17215 | 19592 | 19862 | 17984 | 17298 | 19453 | 20821 | 22326 | 22589 | 20054 | 20337 | 22442 | 24217 | 25921 | 24356 | 23574 | 23295 | 26329 | 27916 | 27984
4896 | 4896 | 204 | 7 | 23 | Summer | 7 | 22 | Summer | 24 | 15951 | 18123 | 18354 | 16680 | 16308 | 18061 | 19464 | 20839 | 21046 | 19016 | 19221 | 21034 | 22917 | 24416 | 23013 | 22528 | 22163 | 25045 | 26486 | 26371
4897 | 4897 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 1 | 15306 | 16957 | 16755 | 15730 | 15215 | 17445 | 18882 | 19596 | 19362 | 17533 | 18619 | 20698 | 22423 | 22704 | 21584 | 20524 | 21335 | 24621 | 25231 | 24922
4898 | 4898 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 2 | 14697 | 16273 | 16062 | 15130 | 14627 | 16768 | 18120 | 18819 | 18560 | 16840 | 18009 | 19920 | 21549 | 21777 | 20765 | 19728 | 20604 | 23681 | 24258 | 23922
4899 | 4899 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 3 | 14330 | 15841 | 15611 | 14757 | 14247 | 16356 | 17623 | 18294 | 17981 | 16386 | 17589 | 19398 | 20882 | 21068 | 20146 | 19149 | 20058 | 22949 | 23473 | 23128
4900 | 4900 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 4 | 14180 | 15653 | 15443 | 14490 | 13940 | 16121 | 17351 | 17920 | 17573 | 15886 | 17215 | 18834 | 20259 | 20340 | 19322 | 18378 | 19427 | 22148 | 22561 | 22224
4901 | 4901 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 5 | 14392 | 15873 | 15617 | 14334 | 13731 | 16211 | 17361 | 17924 | 17533 | 15435 | 17212 | 18607 | 19888 | 19867 | 18562 | 17641 | 19191 | 21536 | 21901 | 21546
4902 | 4902 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 6 | 15106 | 16618 | 16267 | 14241 | 13554 | 16796 | 17951 | 18420 | 17927 | 14989 | 17682 | 18893 | 20062 | 19860 | 17823 | 16876 | 19369 | 21485 | 21670 | 21358
4903 | 4903 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 7 | 16362 | 17888 | 17469 | 14556 | 13816 | 17912 | 19172 | 19583 | 18856 | 15035 | 18677 | 19625 | 20985 | 20514 | 17564 | 16693 | 20131 | 22226 | 22228 | 21906
4904 | 4904 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 8 | 17578 | 19049 | 18410 | 15537 | 14608 | 19030 | 20479 | 20744 | 19711 | 15829 | 19807 | 20497 | 22144 | 21250 | 18331 | 17393 | 21231 | 23314 | 23190 | 22614
4905 | 4905 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 9 | 18419 | 19904 | 19192 | 16503 | 15509 | 19822 | 21403 | 21650 | 20501 | 16817 | 20802 | 21211 | 22964 | 22050 | 19258 | 18341 | 22270 | 24101 | 24063 | 23449
4906 | 4906 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 10 | 19091 | 20550 | 19691 | 17016 | 16137 | 20572 | 22231 | 22369 | 21087 | 17548 | 21601 | 22004 | 23897 | 22742 | 19992 | 19158 | 23160 | 25090 | 25025 | 24206
4907 | 4907 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 11 | 19695 | 21163 | 20092 | 17423 | 16703 | 21283 | 22938 | 23038 | 21565 | 18217 | 22399 | 22855 | 24694 | 23338 | 20625 | 19907 | 24014 | 25954 | 26057 | 24856
4908 | 4908 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 12 | 20216 | 21677 | 20379 | 17743 | 17120 | 21859 | 23587 | 23569 | 21895 | 18672 | 23021 | 23552 | 25420 | 23744 | 21047 | 20388 | 24677 | 26729 | 26922 | 25310
4909 | 4909 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 13 | 20705 | 22048 | 20574 | 17871 | 17398 | 22349 | 23984 | 23908 | 22142 | 18962 | 23599 | 24190 | 25847 | 23993 | 21212 | 20697 | 25293 | 27141 | 27639 | 25588
4910 | 4910 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 14 | 21069 | 22222 | 20681 | 18049 | 17594 | 22681 | 24279 | 24033 | 22260 | 19159 | 24090 | 24706 | 26153 | 24077 | 21376 | 20892 | 25790 | 27421 | 27862 | 25666
4911 | 4911 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 15 | 21391 | 22409 | 20774 | 18238 | 17800 | 22951 | 24511 | 24173 | 22348 | 19361 | 24518 | 25130 | 26386 | 24137 | 21547 | 21083 | 26215 | 27636 | 28074 | 25719
4912 | 4912 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 16 | 21803 | 22617 | 20975 | 18548 | 18163 | 23500 | 24723 | 24265 | 22486 | 19699 | 24996 | 25911 | 26510 | 24202 | 21775 | 21374 | 26645 | 27718 | 28209 | 25751
4913 | 4913 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 17 | 22163 | 22749 | 21184 | 19039 | 18726 | 23840 | 25096 | 24515 | 22665 | 20308 | 25636 | 26369 | 26901 | 24475 | 22295 | 22031 | 27318 | 28128 | 28501 | 26032
4914 | 4914 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 18 | 22315 | 22683 | 21275 | 19539 | 19141 | 24029 | 25229 | 24692 | 23044 | 20969 | 26130 | 26717 | 27192 | 25008 | 23251 | 22881 | 28032 | 28521 | 28954 | 26634
4915 | 4915 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 19 | 22175 | 22833 | 21205 | 19543 | 19431 | 23986 | 25295 | 25064 | 23230 | 21413 | 26202 | 26844 | 27553 | 25509 | 23763 | 23552 | 28337 | 29073 | 29446 | 27276
4916 | 4916 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 20 | 21675 | 22523 | 20737 | 19052 | 19339 | 23743 | 25044 | 24978 | 22955 | 21365 | 25685 | 26647 | 27776 | 25617 | 23883 | 23854 | 27984 | 29506 | 29595 | 27501
4917 | 4917 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 21 | 20766 | 21882 | 20016 | 18555 | 19126 | 23021 | 24535 | 24620 | 22540 | 21401 | 25187 | 26122 | 27766 | 25655 | 24138 | 24251 | 27817 | 29777 | 29829 | 27758
4918 | 4918 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 22 | 19641 | 20785 | 19055 | 17969 | 18451 | 21989 | 23514 | 23680 | 21770 | 20877 | 24245 | 25296 | 27036 | 25117 | 23966 | 23935 | 27051 | 29220 | 29180 | 27356
4919 | 4919 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 23 | 18041 | 19185 | 17680 | 17039 | 17384 | 20361 | 21858 | 22097 | 20400 | 19831 | 22583 | 23649 | 25462 | 23822 | 23137 | 22927 | 25414 | 27697 | 27772 | 26091
4920 | 4920 | 205 | 7 | 24 | Summer | 7 | 23 | Summer | 24 | 16726 | 17720 | 16351 | 16043 | 16285 | 18994 | 20352 | 20527 | 19042 | 18696 | 21076 | 22324 | 23993 | 22463 | 22072 | 21784 | 23891 | 26256 | 26163 | 24730
4921 | 4921 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 1 | 16144 | 16179 | 15460 | 15028 | 15975 | 18416 | 19119 | 18864 | 17934 | 18158 | 20708 | 21832 | 22717 | 21086 | 20149 | 21020 | 23719 | 25009 | 24738 | 23211
4922 | 4922 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 2 | 15499 | 15511 | 14892 | 14455 | 15495 | 17679 | 18370 | 18088 | 17275 | 17580 | 19859 | 20987 | 21850 | 20296 | 19378 | 20313 | 22733 | 24061 | 23751 | 22343
4923 | 4923 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 3 | 15090 | 15074 | 14536 | 14104 | 15181 | 17201 | 17870 | 17554 | 16815 | 17182 | 19274 | 20357 | 21167 | 19691 | 18815 | 19794 | 21999 | 23287 | 22966 | 21669
4924 | 4924 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 4 | 14942 | 14912 | 14294 | 13828 | 15062 | 16969 | 17545 | 17220 | 16348 | 16858 | 18770 | 19807 | 20467 | 18917 | 18080 | 19203 | 21190 | 22389 | 22071 | 20714
4925 | 4925 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 5 | 15103 | 15092 | 14156 | 13619 | 15360 | 17023 | 17600 | 17229 | 15946 | 16907 | 18639 | 19480 | 20048 | 18213 | 17374 | 18975 | 20666 | 21742 | 21403 | 19803
4926 | 4926 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 6 | 15869 | 15764 | 14090 | 13467 | 16118 | 17656 | 18158 | 17707 | 15587 | 17432 | 19011 | 19724 | 20059 | 17521 | 16639 | 19172 | 20688 | 21521 | 21215 | 18924
4927 | 4927 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 7 | 17220 | 16956 | 14422 | 13736 | 17279 | 18891 | 19349 | 18691 | 15697 | 18466 | 19874 | 20681 | 20731 | 17281 | 16460 | 19933 | 21231 | 22053 | 21738 | 18554
4928 | 4928 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 8 | 18584 | 17983 | 15506 | 14602 | 18513 | 20278 | 20601 | 19645 | 16719 | 19707 | 20896 | 21945 | 21815 | 18136 | 17243 | 21110 | 22070 | 23094 | 22517 | 19391
4929 | 4929 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 9 | 19576 | 18819 | 16602 | 15602 | 19574 | 21296 | 21606 | 20557 | 17764 | 20818 | 21750 | 22877 | 22770 | 19158 | 18291 | 22245 | 22842 | 24055 | 23442 | 20428
4930 | 4930 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 10 | 20506 | 19496 | 17291 | 16399 | 20420 | 22285 | 22497 | 21305 | 18564 | 21776 | 22737 | 23968 | 23856 | 20059 | 19279 | 23290 | 24034 | 25192 | 24367 | 21412
4931 | 4931 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 11 | 21163 | 19861 | 17675 | 16959 | 21113 | 22954 | 23134 | 21769 | 19064 | 22551 | 23530 | 24755 | 24816 | 20662 | 20005 | 24149 | 25137 | 26208 | 25001 | 22092
4932 | 4932 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 12 | 21731 | 20119 | 17976 | 17363 | 21687 | 23573 | 23632 | 22082 | 19422 | 23150 | 24108 | 25452 | 25615 | 21063 | 20469 | 24789 | 26008 | 27041 | 25428 | 22522
4933 | 4933 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 13 | 22215 | 20360 | 18145 | 17671 | 22276 | 24017 | 24002 | 22353 | 19607 | 23772 | 24541 | 25915 | 26344 | 21271 | 20822 | 25440 | 26786 | 27796 | 25742 | 22743
4934 | 4934 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 14 | 22458 | 20389 | 18246 | 17779 | 22685 | 24240 | 24057 | 22387 | 19702 | 24192 | 24656 | 26134 | 26507 | 21363 | 20942 | 25849 | 27017 | 27943 | 25745 | 22833
4935 | 4935 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 15 | 22611 | 20356 | 18299 | 17844 | 22976 | 24342 | 24076 | 22335 | 19751 | 24484 | 24794 | 26228 | 26602 | 21404 | 21001 | 26130 | 27243 | 28025 | 25660 | 22871
4936 | 4936 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 16 | 22847 | 20477 | 18535 | 18140 | 23430 | 24498 | 24108 | 22417 | 19967 | 24903 | 25296 | 26301 | 26739 | 21563 | 21220 | 26490 | 27938 | 28088 | 25617 | 23021
4937 | 4937 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 17 | 23236 | 20654 | 18976 | 18664 | 23932 | 24846 | 24316 | 22560 | 20463 | 25495 | 25636 | 26664 | 26979 | 22037 | 21838 | 27133 | 28329 | 28343 | 25866 | 23525
4938 | 4938 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 18 | 23231 | 20692 | 19392 | 19033 | 24251 | 24953 | 24433 | 22857 | 21170 | 25940 | 25753 | 26925 | 27314 | 22972 | 22664 | 27828 | 28336 | 28784 | 26446 | 24533
4939 | 4939 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 19 | 23033 | 20564 | 19321 | 19258 | 24099 | 24936 | 24710 | 22952 | 21240 | 25917 | 25883 | 27183 | 27599 | 23397 | 23264 | 28074 | 28418 | 29225 | 27055 | 25086
4940 | 4940 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 20 | 22518 | 20075 | 18776 | 19125 | 23369 | 24639 | 24571 | 22589 | 20911 | 25296 | 25903 | 27314 | 27536 | 23447 | 23509 | 27677 | 28477 | 29364 | 27263 | 25251
4941 | 4941 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 21 | 21699 | 19287 | 18231 | 18869 | 22541 | 24050 | 24133 | 22072 | 20669 | 24707 | 25740 | 27198 | 27469 | 23625 | 23849 | 27454 | 28544 | 29566 | 27491 | 25638
4942 | 4942 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 22 | 20546 | 18351 | 17646 | 18191 | 21425 | 23000 | 23162 | 21265 | 20249 | 23739 | 24873 | 26423 | 26662 | 23429 | 23523 | 26681 | 27767 | 28914 | 27099 | 25565
4943 | 4943 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 23 | 18901 | 16991 | 16723 | 17140 | 19726 | 21341 | 21560 | 19884 | 19354 | 22074 | 23337 | 24847 | 25178 | 22589 | 22515 | 25044 | 26287 | 27498 | 25849 | 24778
4944 | 4944 | 206 | 7 | 25 | Summer | 7 | 24 | Summer | 24 | 17460 | 15728 | 15733 | 16069 | 18300 | 19858 | 20015 | 18527 | 18324 | 20598 | 21952 | 23387 | 23565 | 21559 | 21395 | 23554 | 24790 | 25922 | 24526 | 23729
4945 | 4945 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 1 | 16158 | 14699 | 14568 | 15599 | 17428 | 18443 | 18176 | 17263 | 16783 | 19972 | 20883 | 21909 | 21973 | 19517 | 20471 | 23145 | 24142 | 24317 | 22826 | 21413
4946 | 4946 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 2 | 15521 | 14167 | 14048 | 15141 | 16752 | 17737 | 17445 | 16644 | 16147 | 19165 | 20015 | 21077 | 21099 | 18786 | 19804 | 22196 | 23145 | 23363 | 21992 | 20618
4947 | 4947 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 3 | 15114 | 13815 | 13712 | 14813 | 16315 | 17256 | 16934 | 16211 | 15732 | 18607 | 19415 | 20426 | 20430 | 18242 | 19294 | 21491 | 22415 | 22588 | 21324 | 20007
4948 | 4948 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 4 | 14959 | 13607 | 13468 | 14738 | 16120 | 16979 | 16661 | 15808 | 15300 | 18172 | 18859 | 19796 | 19774 | 17556 | 18748 | 20724 | 21556 | 21721 | 20392 | 19169
4949 | 4949 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 5 | 15178 | 13474 | 13278 | 15055 | 16283 | 17078 | 16733 | 15475 | 14895 | 18107 | 18678 | 19450 | 19354 | 16892 | 18553 | 20236 | 21084 | 21075 | 19496 | 18353
4950 | 4950 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 6 | 15966 | 13452 | 13179 | 15840 | 16982 | 17704 | 17304 | 15225 | 14527 | 18575 | 19085 | 19573 | 19434 | 16226 | 18808 | 20319 | 21167 | 20928 | 18651 | 17537
4951 | 4951 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 7 | 17224 | 13800 | 13481 | 17028 | 18185 | 18921 | 18344 | 15419 | 14605 | 19503 | 20050 | 20324 | 20127 | 16079 | 19595 | 20883 | 21838 | 21464 | 18286 | 17306
4952 | 4952 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 8 | 18401 | 14839 | 14331 | 18238 | 19326 | 20125 | 19269 | 16437 | 15447 | 20525 | 21142 | 21373 | 20910 | 16828 | 20715 | 21679 | 22770 | 22181 | 19081 | 18064
4953 | 4953 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 9 | 19317 | 15908 | 15372 | 19310 | 20223 | 21115 | 20193 | 17522 | 16542 | 21409 | 22010 | 22347 | 21829 | 17882 | 21863 | 22468 | 23579 | 23108 | 20116 | 19136
4954 | 4954 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 10 | 20050 | 16527 | 16088 | 20129 | 20966 | 21912 | 20841 | 18227 | 17353 | 22301 | 22781 | 23337 | 22597 | 18778 | 22828 | 23572 | 24428 | 23947 | 21010 | 20102
4955 | 4955 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 11 | 20687 | 16955 | 16676 | 20802 | 21663 | 22571 | 21317 | 18738 | 18035 | 23115 | 23562 | 24320 | 23205 | 19527 | 23717 | 24691 | 25298 | 24609 | 21715 | 20906
4956 | 4956 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 12 | 20969 | 17040 | 16867 | 21088 | 21953 | 22857 | 21413 | 18869 | 18261 | 23478 | 24167 | 24886 | 23383 | 19778 | 24150 | 25335 | 26024 | 24827 | 21935 | 21173
4957 | 4957 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 13 | 21282 | 17095 | 17050 | 21439 | 22234 | 23108 | 21560 | 18936 | 18476 | 23790 | 24654 | 25497 | 23561 | 20009 | 24680 | 25993 | 26533 | 25014 | 22034 | 21419
4958 | 4958 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 14 | 21371 | 17153 | 17135 | 21643 | 22347 | 23149 | 21573 | 19021 | 18575 | 23891 | 24999 | 25655 | 23555 | 20111 | 25071 | 26221 | 26901 | 24998 | 22102 | 21528
4959 | 4959 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 15 | 21529 | 17312 | 17309 | 21886 | 22584 | 23284 | 21633 | 19186 | 18739 | 24144 | 25327 | 25869 | 23580 | 20283 | 25463 | 26557 | 27211 | 25022 | 22249 | 21700
4960 | 4960 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 16 | 21804 | 17673 | 17745 | 22347 | 23134 | 23476 | 21870 | 19544 | 19131 | 24787 | 25713 | 26159 | 23708 | 20655 | 25970 | 27393 | 27518 | 25120 | 22538 | 22060
4961 | 4961 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 17 | 22013 | 18253 | 18391 | 22835 | 23643 | 23819 | 22144 | 20160 | 19817 | 25268 | 26207 | 26523 | 24065 | 21403 | 26746 | 27914 | 27949 | 25503 | 23177 | 22850
4962 | 4962 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 18 | 21939 | 18656 | 18726 | 23131 | 23715 | 23943 | 22427 | 20838 | 20474 | 25397 | 26422 | 26843 | 24591 | 22251 | 27470 | 27949 | 28339 | 26122 | 24220 | 23758
4963 | 4963 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 19 | 21989 | 18546 | 18899 | 23109 | 23524 | 24173 | 22459 | 20823 | 20807 | 25424 | 26380 | 27040 | 24996 | 22796 | 27657 | 27972 | 28598 | 26700 | 24742 | 24397
4964 | 4964 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 20 | 21652 | 17989 | 18740 | 22662 | 23305 | 24008 | 22057 | 20442 | 20706 | 25361 | 26000 | 26919 | 25034 | 23010 | 27235 | 28012 | 28563 | 26914 | 24913 | 24668
4965 | 4965 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 21 | 21007 | 17462 | 18498 | 22092 | 22831 | 23557 | 21527 | 20162 | 20703 | 25163 | 25698 | 26805 | 25017 | 23343 | 27014 | 28079 | 28689 | 27172 | 25333 | 25163
4966 | 4966 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 22 | 19887 | 16852 | 17785 | 20970 | 21720 | 22525 | 20645 | 19670 | 20128 | 24224 | 24781 | 25926 | 24421 | 22955 | 26189 | 27256 | 27977 | 26744 | 25230 | 24880
4967 | 4967 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 23 | 18311 | 15946 | 16750 | 19389 | 20128 | 20925 | 19262 | 18765 | 19096 | 22659 | 23143 | 24428 | 23121 | 21945 | 24559 | 25782 | 26377 | 25499 | 24457 | 23898
4968 | 4968 | 207 | 7 | 26 | Summer | 7 | 25 | Summer | 24 | 16935 | 14987 | 15675 | 17974 | 18758 | 19397 | 17905 | 17729 | 17993 | 21270 | 21703 | 22827 | 21791 | 20826 | 23062 | 24294 | 24975 | 24170 | 23422 | 22777
4969 | 4969 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 1 | 15548 | 14201 | 15552 | 17418 | 18051 | 17887 | 17006 | 16592 | 17641 | 20613 | 20273 | 21542 | 20581 | 20252 | 22945 | 23956 | 23576 | 22813 | 21442 | 22033
4970 | 4970 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 2 | 14897 | 13677 | 15100 | 16735 | 17269 | 17155 | 16383 | 15952 | 17088 | 19747 | 19447 | 20673 | 19810 | 19579 | 21997 | 22956 | 22627 | 21968 | 20631 | 21293
4971 | 4971 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 3 | 14464 | 13333 | 14766 | 16273 | 16762 | 16642 | 15952 | 15524 | 16706 | 19122 | 18873 | 19999 | 19228 | 19073 | 21281 | 22203 | 21917 | 21288 | 20006 | 20726
4972 | 4972 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 4 | 14291 | 13075 | 14669 | 16057 | 16478 | 16371 | 15560 | 15098 | 16415 | 18593 | 18375 | 19368 | 18486 | 18524 | 20511 | 21341 | 21125 | 20337 | 19139 | 20026
4973 | 4973 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 5 | 14504 | 12920 | 15029 | 16285 | 16683 | 16514 | 15317 | 14781 | 16539 | 18524 | 18099 | 19063 | 17861 | 18397 | 20097 | 20945 | 20480 | 19494 | 18360 | 19752
4974 | 4974 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 6 | 15181 | 12807 | 15803 | 16978 | 17350 | 17087 | 15096 | 14446 | 17107 | 18914 | 18258 | 19192 | 17221 | 18652 | 20181 | 21027 | 20264 | 18630 | 17512 | 19878
4975 | 4975 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 7 | 16442 | 13173 | 17085 | 18277 | 18609 | 18208 | 15408 | 14641 | 18242 | 19993 | 19100 | 20003 | 17096 | 19521 | 20842 | 21787 | 20885 | 18333 | 17337 | 20689
4976 | 4976 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 8 | 17522 | 14137 | 18397 | 19533 | 19908 | 19227 | 16534 | 15609 | 19555 | 21231 | 20164 | 20901 | 18031 | 20757 | 21758 | 22829 | 21895 | 19214 | 18181 | 21925
4977 | 4977 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 9 | 18261 | 15077 | 19438 | 20370 | 20757 | 20071 | 17569 | 16659 | 20616 | 22038 | 21024 | 21754 | 19027 | 21830 | 22484 | 23577 | 22763 | 20185 | 19188 | 23017
4978 | 4978 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 10 | 18871 | 15801 | 20270 | 21118 | 21485 | 20729 | 18267 | 17480 | 21495 | 22876 | 21777 | 22533 | 19845 | 22809 | 23586 | 24441 | 23609 | 21081 | 20165 | 24062
4979 | 4979 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 11 | 19217 | 16355 | 20903 | 21759 | 22052 | 21158 | 18717 | 18105 | 22250 | 23552 | 22328 | 23082 | 20424 | 23645 | 24668 | 25246 | 24252 | 21737 | 20927 | 24950
4980 | 4980 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 12 | 19341 | 16632 | 21284 | 22140 | 22609 | 21338 | 18938 | 18418 | 22727 | 24212 | 22655 | 23339 | 20706 | 24170 | 25397 | 26058 | 24654 | 22051 | 21289 | 25510
4981 | 4981 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 13 | 19532 | 16885 | 21718 | 22496 | 23003 | 21555 | 19077 | 18702 | 23294 | 24644 | 22999 | 23588 | 20863 | 24775 | 26136 | 26632 | 25038 | 22225 | 21612 | 26137
4982 | 4982 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 14 | 19606 | 17029 | 21989 | 22669 | 23232 | 21625 | 19219 | 18857 | 23759 | 24870 | 23204 | 23644 | 21005 | 25226 | 26421 | 27057 | 25225 | 22348 | 21776 | 26590
4983 | 4983 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 15 | 19738 | 17236 | 22274 | 22950 | 23438 | 21718 | 19411 | 19068 | 24204 | 25065 | 23428 | 23723 | 21202 | 25652 | 26788 | 27415 | 25437 | 22521 | 21978 | 27014
4984 | 4984 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 16 | 20025 | 17683 | 22750 | 23508 | 23786 | 21978 | 19788 | 19502 | 24798 | 25340 | 23604 | 23902 | 21541 | 26180 | 27653 | 27766 | 25533 | 22822 | 22349 | 27532
4985 | 4985 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 17 | 20203 | 18171 | 23088 | 23895 | 24018 | 22108 | 20249 | 20044 | 25378 | 25548 | 23911 | 24121 | 22014 | 26805 | 28025 | 28068 | 25893 | 23307 | 22983 | 28192
4986 | 4986 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 18 | 20089 | 18296 | 23141 | 23789 | 23925 | 22200 | 20695 | 20465 | 25672 | 25550 | 24274 | 24429 | 22775 | 27342 | 27876 | 28268 | 26460 | 24168 | 23716 | 28792
4987 | 4987 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 19 | 19860 | 18421 | 23053 | 23542 | 23771 | 22174 | 20630 | 20726 | 25509 | 25562 | 24465 | 24733 | 23086 | 27475 | 27845 | 28472 | 26840 | 24679 | 24332 | 29017
4988 | 4988 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 20 | 19384 | 18263 | 22578 | 23274 | 23363 | 21770 | 20229 | 20581 | 24859 | 25408 | 24288 | 24701 | 23083 | 27034 | 27855 | 28409 | 27029 | 24871 | 24630 | 28622
4989 | 4989 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 21 | 18589 | 18000 | 21937 | 22727 | 22850 | 21147 | 19845 | 20477 | 24215 | 25225 | 24194 | 24563 | 23195 | 26726 | 27832 | 28449 | 27379 | 25237 | 25085 | 28486
4990 | 4990 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 22 | 17643 | 17264 | 20811 | 21599 | 21717 | 20234 | 19322 | 19868 | 23197 | 24290 | 23397 | 23924 | 22947 | 25884 | 26986 | 27718 | 26800 | 25130 | 24803 | 27730
4991 | 4991 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 23 | 16283 | 16235 | 19224 | 20010 | 20075 | 18849 | 18401 | 18813 | 21519 | 22708 | 21947 | 22593 | 22086 | 24236 | 25496 | 26091 | 25387 | 24339 | 23827 | 26102
4992 | 4992 | 208 | 7 | 27 | Summer | 7 | 26 | Summer | 24 | 15077 | 15200 | 17811 | 18658 | 18639 | 17515 | 17371 | 17702 | 20063 | 21282 | 20651 | 21261 | 21053 | 22753 | 24023 | 24695 | 24074 | 23320 | 22713 | 24603
4993 | 4993 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 1 | 14168 | 14872 | 16977 | 17682 | 16896 | 16397 | 16054 | 17127 | 19455 | 19533 | 18943 | 19846 | 19170 | 22320 | 23396 | 23042 | 22197 | 21104 | 21737 | 24368
4994 | 4994 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 2 | 13630 | 14422 | 16330 | 16914 | 16206 | 15791 | 15427 | 16594 | 18665 | 18730 | 18181 | 19104 | 18433 | 21394 | 22411 | 22116 | 21293 | 20301 | 21004 | 23346
4995 | 4995 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 3 | 13283 | 14139 | 15910 | 16433 | 15793 | 15402 | 15042 | 16246 | 18129 | 18212 | 17600 | 18564 | 17902 | 20718 | 21705 | 21437 | 20551 | 19707 | 20461 | 22588
4996 | 4996 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 4 | 13054 | 14059 | 15716 | 16164 | 15592 | 15053 | 14659 | 15994 | 17716 | 17782 | 17186 | 17877 | 17220 | 19995 | 20879 | 20670 | 19827 | 18860 | 19775 | 21687
4997 | 4997 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 5 | 12948 | 14424 | 15952 | 16400 | 15666 | 14852 | 14384 | 16172 | 17737 | 17581 | 16991 | 17323 | 16623 | 19621 | 20522 | 20066 | 19273 | 18093 | 19503 | 21127
4998 | 4998 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 6 | 12924 | 15253 | 16681 | 17126 | 16260 | 14702 | 14132 | 16836 | 18257 | 17855 | 17302 | 16792 | 15993 | 19783 | 20675 | 19914 | 19193 | 17286 | 19659 | 21110
4999 | 4999 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 7 | 13256 | 16469 | 17920 | 18326 | 17333 | 14954 | 14283 | 17944 | 19209 | 18676 | 18028 | 16648 | 15852 | 20392 | 21381 | 20474 | 19636 | 17024 | 20375 | 21614
5000 | 5000 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 8 | 14222 | 17594 | 19020 | 19449 | 18266 | 15898 | 15080 | 19094 | 20181 | 19594 | 18654 | 17424 | 16543 | 21154 | 22266 | 21300 | 20225 | 17679 | 21424 | 22341
5001 | 5001 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 9 | 15169 | 18587 | 19856 | 20270 | 19049 | 16903 | 16117 | 20149 | 20992 | 20457 | 19021 | 18395 | 17520 | 21870 | 23003 | 22128 | 20623 | 18667 | 22494 | 23070
5002 | 5002 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 10 | 15796 | 19397 | 20587 | 20968 | 19692 | 17556 | 16897 | 20995 | 21864 | 21169 | 19445 | 19177 | 18418 | 22926 | 23835 | 22939 | 21168 | 19606 | 23506 | 24217
5003 | 5003 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 11 | 16221 | 20063 | 21292 | 21577 | 20175 | 18034 | 17556 | 21788 | 22663 | 21751 | 19690 | 19791 | 19163 | 24046 | 24682 | 23633 | 21502 | 20410 | 24438 | 25404
5004 | 5004 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 12 | 16499 | 20566 | 21803 | 22250 | 20524 | 18368 | 17986 | 22382 | 23202 | 22185 | 19893 | 20189 | 19610 | 24888 | 25606 | 24154 | 21756 | 20890 | 25114 | 26289
5005 | 5005 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 13 | 16623 | 21010 | 22182 | 22659 | 20795 | 18503 | 18264 | 22954 | 23579 | 22530 | 20045 | 20352 | 19914 | 25621 | 26182 | 24540 | 21932 | 21210 | 25740 | 27051
5006 | 5006 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 14 | 16723 | 21294 | 22383 | 22887 | 21008 | 18651 | 18421 | 23418 | 23738 | 22750 | 20105 | 20496 | 20071 | 25918 | 26611 | 24727 | 21970 | 21378 | 26198 | 27334
5007 | 5007 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 15 | 16891 | 21582 | 22677 | 23070 | 21240 | 18840 | 18627 | 23847 | 24002 | 22974 | 20100 | 20679 | 20266 | 26285 | 26966 | 24923 | 21939 | 21574 | 26620 | 27705
5008 | 5008 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 16 | 17216 | 22027 | 23156 | 23382 | 21473 | 19192 | 19034 | 24405 | 24622 | 23138 | 20203 | 20986 | 20617 | 27129 | 27294 | 24987 | 21978 | 21912 | 27102 | 28513
5009 | 5009 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 17 | 17740 | 22440 | 23630 | 23694 | 21816 | 19742 | 19658 | 25060 | 25045 | 23524 | 20584 | 21540 | 21317 | 27591 | 27687 | 25421 | 22416 | 22634 | 27848 | 28985
5010 | 5010 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 18 | 17986 | 22531 | 23576 | 23653 | 21913 | 20221 | 20094 | 25349 | 25039 | 23903 | 20993 | 22302 | 22017 | 27497 | 27930 | 26032 | 23052 | 23426 | 28508 | 28944
5011 | 5011 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 19 | 17885 | 22418 | 23282 | 23525 | 21901 | 20145 | 20336 | 25194 | 25032 | 24040 | 21278 | 22603 | 22528 | 27428 | 28111 | 26435 | 23661 | 24060 | 28747 | 29008
5012 | 5012 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 20 | 17321 | 21912 | 22945 | 23070 | 21485 | 19721 | 20162 | 24491 | 24908 | 23757 | 21092 | 22528 | 22701 | 27382 | 27995 | 26591 | 23728 | 24358 | 28353 | 29071
5013 | 5013 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 21 | 16757 | 21262 | 22367 | 22533 | 20981 | 19309 | 20029 | 23803 | 24617 | 23585 | 21151 | 22574 | 22956 | 27326 | 28001 | 26910 | 24203 | 24824 | 28233 | 29210
5014 | 5014 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 22 | 16144 | 20100 | 21214 | 21360 | 19937 | 18750 | 19382 | 22731 | 23637 | 22734 | 20477 | 22259 | 22529 | 26440 | 27232 | 26295 | 23724 | 24527 | 27469 | 28430
5015 | 5015 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 23 | 15283 | 18546 | 19629 | 19760 | 18467 | 17845 | 18344 | 21081 | 22095 | 21293 | 19218 | 21411 | 21541 | 24960 | 25618 | 24916 | 22504 | 23557 | 25868 | 26994
5016 | 5016 | 209 | 7 | 28 | Summer | 7 | 27 | Summer | 24 | 14360 | 17150 | 18247 | 18312 | 17146 | 16801 | 17204 | 19587 | 20709 | 19950 | 18171 | 20355 | 20408 | 23454 | 24185 | 23580 | 21488 | 22424 | 24342 | 25472
5017 | 5017 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 1 | 13469 | 16469 | 17491 | 16708 | 15842 | 15728 | 16838 | 19063 | 19929 | 18436 | 17422 | 18711 | 19758 | 22997 | 22687 | 21867 | 20529 | 21632 | 24257 | 25048
5018 | 5018 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 2 | 12972 | 15842 | 16752 | 16031 | 15216 | 15117 | 16324 | 18298 | 19095 | 17703 | 16893 | 17997 | 19107 | 22037 | 21780 | 20985 | 19866 | 20910 | 23250 | 24007
5019 | 5019 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 3 | 12670 | 15429 | 16280 | 15636 | 14782 | 14741 | 15988 | 17790 | 18520 | 17146 | 16524 | 17496 | 18637 | 21338 | 21115 | 20266 | 19358 | 20377 | 22494 | 23230
5020 | 5020 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 4 | 12445 | 15239 | 16020 | 15454 | 14679 | 14383 | 15771 | 17425 | 18062 | 16790 | 16068 | 16858 | 18142 | 20549 | 20379 | 19570 | 18624 | 19701 | 21605 | 22272
5021 | 5021 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 5 | 12294 | 15491 | 16276 | 15564 | 14872 | 14147 | 15994 | 17513 | 18061 | 16673 | 15683 | 16322 | 18057 | 20245 | 19817 | 19059 | 17892 | 19445 | 21054 | 21773
5022 | 5022 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 6 | 12208 | 16222 | 16992 | 16187 | 15541 | 13916 | 16701 | 18089 | 18536 | 17059 | 15293 | 15751 | 18376 | 20438 | 19700 | 19005 | 17172 | 19601 | 21031 | 21770
5023 | 5023 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 7 | 12468 | 17464 | 18169 | 17269 | 16477 | 14060 | 17824 | 19080 | 19556 | 17815 | 15132 | 15643 | 19159 | 21160 | 20251 | 19428 | 16796 | 20278 | 21499 | 22341
5024 | 5024 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 8 | 13280 | 18589 | 19318 | 18217 | 17199 | 14871 | 19000 | 20108 | 20667 | 18491 | 15706 | 16364 | 20255 | 22092 | 21118 | 20037 | 17292 | 21347 | 22250 | 23216
5025 | 5025 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 9 | 14140 | 19405 | 20131 | 18990 | 17552 | 15882 | 20038 | 20931 | 21444 | 18856 | 16276 | 17334 | 21301 | 22827 | 21935 | 20429 | 17855 | 22397 | 22957 | 23949
5026 | 5026 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 10 | 14883 | 20188 | 20872 | 19666 | 17921 | 16698 | 20923 | 21833 | 22284 | 19322 | 16780 | 18260 | 22295 | 23700 | 22804 | 21014 | 18462 | 23458 | 24160 | 24889
5027 | 5027 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 11 | 15488 | 20885 | 21487 | 20151 | 18060 | 17345 | 21710 | 22626 | 22999 | 19554 | 17113 | 19004 | 23172 | 24548 | 23491 | 21353 | 18906 | 24391 | 25343 | 25802
5028 | 5028 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 12 | 15871 | 21386 | 22159 | 20499 | 18178 | 17760 | 22280 | 23159 | 23746 | 19731 | 17335 | 19456 | 23811 | 25439 | 23985 | 21605 | 19179 | 25053 | 26205 | 26753
5029 | 5029 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 13 | 16262 | 21950 | 22738 | 20935 | 18426 | 18196 | 23010 | 23698 | 24323 | 20045 | 17488 | 19925 | 24560 | 26176 | 24530 | 21945 | 19336 | 25834 | 27126 | 27505
5030 | 5030 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 14 | 16561 | 22339 | 23119 | 21310 | 18634 | 18503 | 23621 | 24021 | 24702 | 20271 | 17579 | 20246 | 25166 | 26762 | 24874 | 22147 | 19416 | 26432 | 27562 | 28104
5031 | 5031 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 15 | 16752 | 22670 | 23311 | 21548 | 18634 | 18699 | 24048 | 24291 | 24870 | 20266 | 17609 | 20442 | 25582 | 27108 | 25064 | 22119 | 19444 | 26852 | 27927 | 28458
5032 | 5032 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 16 | 17159 | 23142 | 23626 | 21787 | 18794 | 19103 | 24600 | 24864 | 25127 | 20375 | 17767 | 20801 | 26085 | 27441 | 25129 | 22161 | 19577 | 27326 | 28725 | 28763
5033 | 5033 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 17 | 17604 | 23480 | 23816 | 22003 | 18958 | 19597 | 25110 | 25147 | 25300 | 20637 | 18108 | 21355 | 26668 | 27708 | 25436 | 22465 | 20013 | 27943 | 29072 | 29029
5034 | 5034 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 18 | 17641 | 23268 | 23636 | 21939 | 19048 | 19875 | 25226 | 25006 | 25216 | 20865 | 18716 | 21886 | 27125 | 27800 | 25898 | 22962 | 20743 | 28468 | 28900 | 29211
5035 | 5035 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 19 | 17700 | 22836 | 23414 | 21812 | 18993 | 20042 | 24980 | 24869 | 25125 | 21015 | 19083 | 22276 | 27165 | 27878 | 26203 | 23453 | 21366 | 28645 | 28897 | 29424
5036 | 5036 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 20 | 17518 | 22418 | 22889 | 21350 | 18537 | 19845 | 24251 | 24683 | 24878 | 20718 | 19406 | 22382 | 26665 | 27685 | 26300 | 23473 | 22001 | 28250 | 28947 | 29355
5037 | 5037 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 21 | 17274 | 21799 | 22315 | 20815 | 18200 | 19668 | 23523 | 24326 | 24635 | 20675 | 19617 | 22567 | 26319 | 27613 | 26554 | 23905 | 22612 | 28111 | 29074 | 29527
5038 | 5038 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 22 | 16533 | 20655 | 21142 | 19763 | 17314 | 19014 | 22435 | 23332 | 23660 | 19974 | 19348 | 22118 | 25444 | 26824 | 25924 | 23427 | 22495 | 27356 | 28310 | 28865
5039 | 5039 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 23 | 15516 | 19044 | 19505 | 18249 | 15970 | 17939 | 20732 | 21717 | 22078 | 18673 | 18670 | 21077 | 23800 | 25160 | 24505 | 22158 | 21878 | 25711 | 26837 | 27244
5040 | 5040 | 210 | 7 | 29 | Summer | 7 | 28 | Summer | 24 | 14523 | 17691 | 18062 | 16945 | 14944 | 16824 | 19249 | 20324 | 20633 | 17621 | 17852 | 19942 | 22310 | 23751 | 23178 | 21147 | 21036 | 24208 | 25340 | 25830
5041 | 5041 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 1 | 14335 | 16903 | 16433 | 15626 | 14360 | 16449 | 18621 | 19484 | 18969 | 16883 | 16547 | 19289 | 22049 | 22179 | 21445 | 20181 | 19153 | 24048 | 24866 | 24302
5042 | 5042 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 2 | 13902 | 16163 | 15757 | 14993 | 13949 | 15929 | 17860 | 18649 | 18189 | 16353 | 16046 | 18639 | 21125 | 21267 | 20556 | 19514 | 18560 | 23025 | 23813 | 23319
5043 | 5043 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 3 | 13630 | 15700 | 15374 | 14565 | 13715 | 15604 | 17371 | 18092 | 17697 | 16013 | 15695 | 18186 | 20467 | 20621 | 19853 | 19028 | 18098 | 22275 | 23037 | 22587
5044 | 5044 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 4 | 13557 | 15470 | 15224 | 14480 | 13553 | 15430 | 17066 | 17681 | 17324 | 15621 | 15334 | 17734 | 19806 | 19943 | 19207 | 18318 | 17498 | 21419 | 22102 | 21737
5045 | 5045 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 5 | 13926 | 15743 | 15365 | 14706 | 13469 | 15695 | 17214 | 17747 | 17200 | 15305 | 14964 | 17705 | 19531 | 19446 | 18748 | 17622 | 16902 | 20901 | 21620 | 21045
5046 | 5046 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 6 | 14742 | 16472 | 16034 | 15420 | 13372 | 16444 | 17860 | 18296 | 17533 | 14995 | 14495 | 18095 | 19754 | 19393 | 18747 | 16939 | 16187 | 20906 | 21637 | 20810
5047 | 5047 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 7 | 16012 | 17734 | 17219 | 16450 | 13584 | 17645 | 18968 | 19425 | 18444 | 14958 | 14387 | 18989 | 20546 | 20045 | 19271 | 16642 | 15864 | 21439 | 22267 | 21373
5048 | 5048 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 8 | 17099 | 18856 | 18133 | 17134 | 14213 | 18763 | 19972 | 20521 | 19347 | 15533 | 14915 | 20064 | 21360 | 20864 | 19832 | 17107 | 16281 | 22141 | 23096 | 22183
5049 | 5049 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 9 | 17958 | 19592 | 18855 | 17417 | 14707 | 19712 | 20722 | 21237 | 20116 | 16050 | 15528 | 21043 | 22054 | 21605 | 20153 | 17598 | 16875 | 22769 | 23744 | 22959
5050 | 5050 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 10 | 18745 | 20269 | 19455 | 17706 | 15004 | 20502 | 21527 | 22005 | 20790 | 16474 | 16189 | 21956 | 22999 | 22387 | 20648 | 18133 | 17610 | 23890 | 24609 | 23796
5051 | 5051 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 11 | 19413 | 20871 | 19934 | 17835 | 15208 | 21271 | 22307 | 22706 | 21365 | 16788 | 16731 | 22828 | 23915 | 23059 | 20979 | 18559 | 18235 | 25063 | 25521 | 24528
5052 | 5052 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 12 | 20033 | 21638 | 20408 | 18081 | 15507 | 21968 | 22963 | 23575 | 21902 | 17137 | 17251 | 23582 | 24662 | 23678 | 21358 | 18960 | 18799 | 26048 | 26595 | 25206
5053 | 5053 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 13 | 20536 | 22110 | 20728 | 18229 | 15528 | 22581 | 23383 | 24053 | 22293 | 17173 | 17497 | 24230 | 25137 | 24105 | 21582 | 19015 | 19057 | 26851 | 27234 | 25683
5054 | 5054 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 14 | 20805 | 22343 | 20945 | 18282 | 15451 | 23037 | 23549 | 24271 | 22502 | 17109 | 17644 | 24687 | 25275 | 24294 | 21632 | 18938 | 19184 | 27127 | 27670 | 25858
5055 | 5055 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 15 | 21009 | 22465 | 21090 | 18201 | 15397 | 23374 | 23722 | 24365 | 22633 | 17059 | 17855 | 25024 | 25455 | 24408 | 21521 | 18885 | 19397 | 27404 | 27939 | 25959
5056 | 5056 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 16 | 21423 | 22763 | 21311 | 18347 | 15573 | 23910 | 24254 | 24612 | 22792 | 17199 | 18206 | 25508 | 26059 | 24470 | 21553 | 18989 | 19739 | 28186 | 28226 | 25970
5057 | 5057 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 17 | 21762 | 23016 | 21575 | 18571 | 15990 | 24471 | 24599 | 24833 | 23098 | 17583 | 18824 | 26146 | 26485 | 24831 | 21921 | 19486 | 20338 | 28595 | 28556 | 26375
5058 | 5058 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 18 | 21899 | 23056 | 21653 | 18836 | 16568 | 24786 | 24666 | 24941 | 23516 | 18372 | 19671 | 26764 | 26612 | 25494 | 22613 | 20415 | 21353 | 28642 | 28959 | 27122
5059 | 5059 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 19 | 21756 | 22845 | 21560 | 18818 | 16713 | 24589 | 24557 | 24852 | 23595 | 18736 | 20005 | 26822 | 26826 | 25819 | 23135 | 21085 | 21950 | 28696 | 29221 | 27562
5060 | 5060 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 20 | 21243 | 22307 | 21085 | 18340 | 16803 | 23878 | 24350 | 24572 | 23243 | 18985 | 20093 | 26279 | 26989 | 25881 | 23131 | 21690 | 22303 | 28768 | 29172 | 27737
5061 | 5061 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 21 | 20555 | 21683 | 20509 | 17942 | 16619 | 23098 | 23932 | 24242 | 22967 | 19112 | 20276 | 25855 | 26996 | 26060 | 23499 | 22249 | 22820 | 28875 | 29327 | 28156
5062 | 5062 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 22 | 19406 | 20505 | 19459 | 17051 | 16172 | 21995 | 22900 | 23233 | 22109 | 18809 | 19871 | 24956 | 26199 | 25414 | 22998 | 22139 | 22548 | 28112 | 28670 | 27618
5063 | 5063 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 23 | 17839 | 18865 | 17954 | 15725 | 15470 | 20318 | 21284 | 21630 | 20637 | 18131 | 19026 | 23311 | 24662 | 23989 | 21735 | 21517 | 21713 | 26642 | 27059 | 26217
5064 | 5064 | 211 | 7 | 30 | Summer | 7 | 29 | Summer | 24 | 16504 | 17442 | 16626 | 14695 | 14691 | 18841 | 19892 | 20161 | 19301 | 17306 | 18079 | 21809 | 23270 | 22666 | 20714 | 20663 | 20724 | 25142 | 25648 | 24873
5065 | 5065 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 1 | 15678 | 15765 | 15248 | 14042 | 13892 | 18074 | 18944 | 18395 | 17702 | 15995 | 17465 | 21384 | 22407 | 20858 | 19677 | 18743 | 20008 | 24568 | 24059 | 22927
5066 | 5066 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 2 | 15078 | 15121 | 14649 | 13630 | 13497 | 17338 | 18133 | 17627 | 16983 | 15517 | 16965 | 20478 | 21454 | 19991 | 19038 | 18153 | 19444 | 23542 | 23081 | 21983
5067 | 5067 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 3 | 14665 | 14726 | 14231 | 13397 | 13237 | 16857 | 17588 | 17146 | 16444 | 15180 | 16666 | 19842 | 20736 | 19300 | 18552 | 17693 | 19034 | 22761 | 22342 | 21205
5068 | 5068 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 4 | 14506 | 14595 | 14178 | 13275 | 13111 | 16600 | 17234 | 16847 | 16170 | 14873 | 16413 | 19254 | 20033 | 18711 | 17889 | 17136 | 18550 | 21850 | 21511 | 20440
5069 | 5069 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 5 | 14766 | 14771 | 14423 | 13211 | 12997 | 16783 | 17349 | 16790 | 16127 | 14545 | 16472 | 19043 | 19781 | 18295 | 17225 | 16563 | 18406 | 21375 | 20818 | 19828
5070 | 5070 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 6 | 15521 | 15467 | 15174 | 13169 | 12816 | 17479 | 17962 | 17227 | 16606 | 14138 | 16869 | 19345 | 20022 | 18349 | 16585 | 15893 | 18593 | 21416 | 20590 | 19698
5071 | 5071 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 7 | 16800 | 16638 | 16210 | 13368 | 12854 | 18586 | 19102 | 18168 | 17441 | 14049 | 17682 | 20153 | 20789 | 18870 | 16281 | 15538 | 19222 | 22029 | 21115 | 20125
5072 | 5072 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 8 | 17917 | 17598 | 16940 | 14045 | 13464 | 19632 | 20247 | 19145 | 18127 | 14649 | 18611 | 21047 | 21755 | 19484 | 16793 | 16005 | 20044 | 22894 | 21950 | 20724
5073 | 5073 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 9 | 18754 | 18389 | 17348 | 14655 | 14235 | 20482 | 21071 | 20046 | 18529 | 15394 | 19300 | 21866 | 22541 | 19914 | 17400 | 16710 | 20689 | 23643 | 22818 | 21178
5074 | 5074 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 10 | 19532 | 19048 | 17725 | 15036 | 14880 | 21349 | 21908 | 20793 | 18986 | 16137 | 19976 | 22886 | 23487 | 20487 | 18013 | 17533 | 21436 | 24590 | 23725 | 21822
5075 | 5075 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 11 | 20222 | 19542 | 17847 | 15227 | 15329 | 22106 | 22595 | 21355 | 19203 | 16671 | 20520 | 23783 | 24295 | 20806 | 18430 | 18148 | 22050 | 25496 | 24458 | 22207
5076 | 5076 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 12 | 20837 | 19982 | 18078 | 15512 | 15791 | 22747 | 23446 | 21871 | 19491 | 17177 | 20986 | 24507 | 25245 | 21169 | 18819 | 18697 | 22557 | 26557 | 25120 | 22616
5077 | 5077 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 13 | 21362 | 20388 | 18296 | 15593 | 16097 | 23235 | 23990 | 22316 | 19758 | 17492 | 21414 | 25035 | 25820 | 21475 | 18943 | 19017 | 23014 | 27263 | 25670 | 22943
5078 | 5078 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 14 | 21707 | 20680 | 18442 | 15617 | 16351 | 23501 | 24303 | 22633 | 19922 | 17737 | 21606 | 25281 | 26152 | 21617 | 18962 | 19245 | 23219 | 27788 | 25941 | 23094
5079 | 5079 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 15 | 22229 | 21094 | 18626 | 15831 | 16819 | 23948 | 24655 | 23031 | 20090 | 18216 | 21917 | 25730 | 26505 | 21777 | 19176 | 19724 | 23518 | 28321 | 26302 | 23245
5080 | 5080 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 16 | 22649 | 21299 | 18750 | 15982 | 17165 | 24455 | 24888 | 23175 | 20159 | 18551 | 22094 | 26299 | 26664 | 21795 | 19261 | 20039 | 23657 | 28583 | 26299 | 23238
5081 | 5081 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 17 | 22891 | 21400 | 18802 | 16237 | 17599 | 24649 | 24960 | 23316 | 20309 | 19003 | 22294 | 26571 | 26706 | 21990 | 19600 | 20490 | 23848 | 28761 | 26543 | 23466
5082 | 5082 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 18 | 22615 | 21150 | 18712 | 16506 | 17920 | 24431 | 24772 | 23397 | 20434 | 19524 | 22443 | 26409 | 26682 | 22391 | 20231 | 21217 | 24150 | 28875 | 27005 | 23943
5083 | 5083 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 19 | 22074 | 20913 | 18528 | 16500 | 17989 | 24161 | 24520 | 23301 | 20440 | 19672 | 22598 | 26440 | 26813 | 22732 | 20735 | 21671 | 24504 | 28998 | 27317 | 24428
5084 | 5084 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 20 | 21613 | 20370 | 17975 | 16518 | 17778 | 23883 | 24149 | 22839 | 20084 | 19636 | 22527 | 26490 | 26847 | 22640 | 21257 | 21952 | 24719 | 28910 | 27448 | 24434
5085 | 5085 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 21 | 20957 | 19758 | 17539 | 16297 | 17625 | 23407 | 23743 | 22476 | 19960 | 19737 | 22520 | 26414 | 26939 | 22933 | 21756 | 22429 | 25015 | 29033 | 27841 | 24956
5086 | 5086 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 22 | 19797 | 18647 | 16603 | 15807 | 17034 | 22310 | 22660 | 21543 | 19211 | 19269 | 21703 | 25554 | 26130 | 22368 | 21596 | 22116 | 24338 | 28331 | 27270 | 24494
5087 | 5087 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 23 | 18215 | 17173 | 15290 | 15123 | 16157 | 20694 | 21051 | 20058 | 17909 | 18421 | 20397 | 24012 | 24567 | 21098 | 20974 | 21278 | 23040 | 26720 | 25882 | 23245
5088 | 5088 | 212 | 7 | 31 | Summer | 7 | 30 | Summer | 24 | 16882 | 15892 | 14276 | 14363 | 15278 | 19318 | 19586 | 18719 | 16855 | 17483 | 19222 | 22619 | 23138 | 20083 | 20118 | 20304 | 21857 | 25324 | 24571 | 22227
5089 | 5089 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 1 | 16228 | 14759 | 13826 | 13817 | 14974 | 18553 | 17992 | 17321 | 16250 | 16529 | 19013 | 21901 | 21637 | 19263 | 18467 | 19243 | 21945 | 23879 | 22793 | 21279
5090 | 5090 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 2 | 15519 | 14191 | 13450 | 13433 | 14596 | 17770 | 17256 | 16627 | 15759 | 16045 | 18341 | 20980 | 20758 | 18647 | 17899 | 18658 | 21135 | 22937 | 21878 | 20597
5091 | 5091 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 3 | 15083 | 13817 | 13249 | 13206 | 14417 | 17261 | 16815 | 16132 | 15461 | 15631 | 17887 | 20320 | 20145 | 18210 | 17490 | 18126 | 20551 | 22232 | 21133 | 20069
5092 | 5092 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 4 | 14872 | 13732 | 13145 | 13098 | 14392 | 16948 | 16564 | 15919 | 15137 | 15351 | 17486 | 19681 | 19525 | 17594 | 16961 | 17601 | 19869 | 21419 | 20380 | 19282
5093 | 5093 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 5 | 15150 | 14015 | 13107 | 13007 | 14715 | 17118 | 16570 | 15947 | 14887 | 15115 | 17448 | 19500 | 19095 | 16985 | 16425 | 17097 | 19550 | 20749 | 19786 | 18483
5094 | 5094 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 6 | 15871 | 14787 | 13088 | 12846 | 15420 | 17779 | 17072 | 16500 | 14639 | 14770 | 17783 | 19809 | 19103 | 16396 | 15789 | 16479 | 19556 | 20540 | 19676 | 17727
5095 | 5095 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 7 | 17118 | 15856 | 13333 | 12921 | 16498 | 18967 | 18072 | 17417 | 14633 | 14642 | 18494 | 20651 | 19777 | 16138 | 15465 | 16169 | 19972 | 21074 | 20105 | 17372
5096 | 5096 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 8 | 18288 | 16606 | 14045 | 13554 | 17429 | 20132 | 19079 | 18153 | 15273 | 15233 | 19205 | 21658 | 20679 | 16673 | 15956 | 16672 | 20572 | 21930 | 20708 | 17905
5097 | 5097 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 9 | 19122 | 17005 | 14670 | 14317 | 18066 | 20947 | 19970 | 18560 | 15902 | 15969 | 19847 | 22441 | 21528 | 17267 | 16660 | 17327 | 21220 | 22771 | 21149 | 18517
5098 | 5098 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 10 | 19677 | 17166 | 14836 | 14751 | 18420 | 21553 | 20497 | 18794 | 16184 | 16548 | 20590 | 23162 | 22173 | 17656 | 17270 | 17980 | 22051 | 23477 | 21571 | 18992
5099 | 5099 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 11 | 20212 | 17257 | 14966 | 15127 | 18834 | 22165 | 20988 | 18939 | 16417 | 17086 | 21233 | 23899 | 22784 | 18003 | 17816 | 18601 | 22773 | 24157 | 21895 | 19417
5100 | 5100 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 12 | 20830 | 17374 | 15148 | 15485 | 19167 | 22904 | 21393 | 19118 | 16655 | 17459 | 21775 | 24738 | 23290 | 18292 | 18268 | 19016 | 23374 | 24711 | 22205 | 19742
5101 | 5101 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 13 | 21221 | 17433 | 15082 | 15640 | 19424 | 23302 | 21684 | 19231 | 16605 | 17633 | 22243 | 25155 | 23637 | 18271 | 18442 | 19184 | 23865 | 25099 | 22384 | 19735
5102 | 5102 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 14 | 21443 | 17459 | 14987 | 15771 | 19502 | 23495 | 21885 | 19272 | 16517 | 17649 | 22482 | 25368 | 23808 | 18178 | 18558 | 19164 | 24094 | 25254 | 22414 | 19643
5103 | 5103 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 15 | 21640 | 17450 | 15022 | 16063 | 19612 | 23674 | 22113 | 19271 | 16527 | 17738 | 22728 | 25549 | 23984 | 18215 | 18862 | 19222 | 24291 | 25442 | 22391 | 19690
5104 | 5104 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 16 | 22020 | 17675 | 15271 | 16503 | 19939 | 24012 | 22373 | 19454 | 16744 | 18192 | 23444 | 25819 | 24142 | 18398 | 19265 | 19634 | 25005 | 25530 | 22477 | 19870
5105 | 5105 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 17 | 22358 | 17955 | 15755 | 17173 | 20349 | 24336 | 22744 | 19839 | 17204 | 18928 | 23884 | 26087 | 24589 | 18971 | 19959 | 20419 | 25484 | 26004 | 22939 | 20455
5106 | 5106 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 18 | 22361 | 18074 | 16205 | 17717 | 20481 | 24384 | 23027 | 20161 | 17931 | 19632 | 23980 | 26295 | 25194 | 19852 | 20932 | 21348 | 25753 | 26720 | 23658 | 21406
5107 | 5107 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 19 | 22163 | 18040 | 16334 | 17940 | 20624 | 24269 | 23051 | 20282 | 18283 | 19570 | 24114 | 26541 | 25500 | 20473 | 21510 | 21473 | 26171 | 27186 | 24302 | 22134
5108 | 5108 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 20 | 21592 | 17514 | 16346 | 17706 | 20459 | 23891 | 22581 | 19862 | 18449 | 19376 | 23897 | 26510 | 25477 | 20969 | 21775 | 21641 | 26186 | 27351 | 24342 | 22733
5109 | 5109 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 21 | 20905 | 17016 | 16082 | 17510 | 20115 | 23416 | 22136 | 19625 | 18460 | 19757 | 24117 | 26500 | 25537 | 21399 | 22204 | 22379 | 26761 | 27717 | 24841 | 23374
5110 | 5110 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 22 | 19715 | 16107 | 15604 | 16923 | 19179 | 22315 | 21172 | 18849 | 18131 | 19190 | 23199 | 25660 | 24864 | 21228 | 21897 | 21980 | 26032 | 27155 | 24403 | 23279
5111 | 5111 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 23 | 18068 | 14805 | 14915 | 16059 | 17838 | 20679 | 19665 | 17527 | 17451 | 18255 | 21755 | 24087 | 23423 | 20589 | 21052 | 21072 | 24657 | 25750 | 23157 | 22667
5112 | 5112 | 213 | 8 | 1 | Summer | 7 | 31 | Summer | 24 | 16688 | 13787 | 14160 | 15200 | 16683 | 19224 | 18331 | 16472 | 16640 | 17376 | 20539 | 22646 | 22100 | 19745 | 20080 | 20158 | 23455 | 24448 | 22146 | 21795
5113 | 5113 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 1 | 15150 | 13241 | 13544 | 14218 | 16067 | 17486 | 16846 | 15768 | 15534 | 18464 | 19785 | 20994 | 20363 | 18044 | 18868 | 21547 | 22783 | 22586 | 21081 | 19749
5114 | 5114 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 2 | 14541 | 12867 | 13177 | 13835 | 15510 | 16760 | 16168 | 15296 | 15086 | 17807 | 19112 | 20140 | 19530 | 17486 | 18289 | 20771 | 22017 | 21665 | 20387 | 19126
5115 | 5115 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 3 | 14173 | 12664 | 12958 | 13511 | 15181 | 16335 | 15689 | 15013 | 14795 | 17372 | 18611 | 19550 | 18890 | 17076 | 17767 | 20204 | 21393 | 20916 | 19862 | 18654
5116 | 5116 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 4 | 14058 | 12568 | 12859 | 13423 | 15062 | 16118 | 15522 | 14746 | 14539 | 17022 | 18170 | 18994 | 18360 | 16581 | 17270 | 19557 | 20684 | 20178 | 19083 | 18020
5117 | 5117 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 5 | 14258 | 12547 | 12777 | 13417 | 15353 | 16167 | 15609 | 14554 | 14264 | 17044 | 18072 | 18632 | 18013 | 16083 | 16797 | 19263 | 20237 | 19596 | 18297 | 17362
5118 | 5118 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 6 | 14971 | 12538 | 12631 | 13345 | 15999 | 16704 | 16218 | 14382 | 13899 | 17438 | 18471 | 18729 | 18128 | 15480 | 16203 | 19304 | 20318 | 19495 | 17543 | 16628
5119 | 5119 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 7 | 16174 | 12800 | 12734 | 13433 | 16980 | 17732 | 17191 | 14446 | 13864 | 18215 | 19332 | 19465 | 18711 | 15183 | 15914 | 19740 | 20966 | 19937 | 17186 | 16267
5120 | 5120 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 8 | 17110 | 13481 | 13353 | 13942 | 17797 | 18700 | 17908 | 15089 | 14474 | 18937 | 20243 | 20357 | 19333 | 15650 | 16392 | 20318 | 21745 | 20507 | 17675 | 16732
5121 | 5121 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 9 | 17842 | 14113 | 14171 | 14644 | 18483 | 19602 | 18340 | 15756 | 15225 | 19627 | 20965 | 21226 | 19767 | 16380 | 17080 | 20978 | 22394 | 20964 | 18306 | 17463
5122 | 5122 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 10 | 18311 | 14297 | 14631 | 15141 | 19134 | 20143 | 18577 | 16050 | 15782 | 20388 | 21744 | 21883 | 20138 | 17008 | 17754 | 21829 | 23266 | 21404 | 18799 | 18155
5123 | 5123 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 11 | 18763 | 14448 | 15013 | 15584 | 19678 | 20628 | 18714 | 16279 | 16250 | 21028 | 22480 | 22489 | 20406 | 17552 | 18376 | 22553 | 24090 | 21732 | 19223 | 18756
5124 | 5124 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 12 | 19045 | 14588 | 15329 | 15878 | 20110 | 20988 | 18848 | 16469 | 16609 | 21522 | 23186 | 22945 | 20624 | 17964 | 18751 | 23110 | 24871 | 22002 | 19509 | 19197
5125 | 5125 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 13 | 19285 | 14471 | 15454 | 16018 | 20531 | 21235 | 18921 | 16393 | 16759 | 21959 | 23650 | 23261 | 20753 | 18109 | 18889 | 23571 | 25368 | 22144 | 19470 | 19345
5126 | 5126 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 14 | 19492 | 14411 | 15630 | 16096 | 20813 | 21481 | 19004 | 16352 | 16929 | 22247 | 24018 | 23486 | 20827 | 18273 | 18921 | 23840 | 25741 | 22215 | 19422 | 19504
5127 | 5127 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 15 | 19707 | 14436 | 15901 | 16180 | 21058 | 21687 | 18977 | 16362 | 17200 | 22478 | 24267 | 23662 | 20780 | 18557 | 18967 | 24044 | 25995 | 22163 | 19443 | 19797
5128 | 5128 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 16 | 20020 | 14697 | 16349 | 16677 | 21691 | 21971 | 19182 | 16597 | 17637 | 23195 | 24657 | 23843 | 20914 | 18974 | 19393 | 24778 | 26327 | 22263 | 19628 | 20218
5129 | 5129 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 17 | 20358 | 15186 | 17006 | 17399 | 22069 | 22331 | 19556 | 17052 | 18326 | 23628 | 25005 | 24272 | 21346 | 19660 | 20166 | 25238 | 26765 | 22718 | 20208 | 20927
5130 | 5130 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 18 | 20370 | 15610 | 17506 | 17840 | 22158 | 22616 | 19855 | 17735 | 19096 | 23719 | 25163 | 24849 | 22003 | 20643 | 21103 | 25519 | 27020 | 23459 | 21183 | 21986
5131 | 5131 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 19 | 20271 | 15729 | 17675 | 17615 | 22050 | 22593 | 19914 | 18009 | 19364 | 23757 | 25146 | 25070 | 22460 | 21165 | 21182 | 25881 | 27317 | 24077 | 21892 | 22603
5132 | 5132 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 20 | 19704 | 15675 | 17394 | 17310 | 21559 | 22092 | 19438 | 18095 | 19259 | 23445 | 24979 | 24972 | 22302 | 21371 | 21293 | 25852 | 27487 | 24099 | 22469 | 22891
5133 | 5133 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 21 | 19056 | 15388 | 17171 | 17421 | 21410 | 21593 | 19136 | 18038 | 19276 | 23580 | 25197 | 24956 | 22500 | 21742 | 21991 | 26401 | 28121 | 24574 | 23102 | 23446
5134 | 5134 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 22 | 17964 | 14942 | 16589 | 16731 | 20295 | 20611 | 18333 | 17677 | 18805 | 22637 | 24284 | 24222 | 21930 | 21429 | 21584 | 25664 | 27401 | 24142 | 23028 | 23200
5135 | 5135 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 23 | 16496 | 14268 | 15738 | 15802 | 18778 | 19110 | 17014 | 16984 | 17958 | 21189 | 22811 | 22782 | 20658 | 20592 | 20681 | 24285 | 25977 | 22903 | 22430 | 22374
5136 | 5136 | 214 | 8 | 2 | Summer | 8 | 1 | Summer | 24 | 15251 | 13519 | 14859 | 14968 | 17545 | 17772 | 15946 | 16149 | 17033 | 19941 | 21452 | 21440 | 19639 | 19605 | 19748 | 23067 | 24652 | 21886 | 21566 | 21366
5137 | 5137 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 1 | 13963 | 12888 | 13842 | 15716 | 16640 | 16236 | 15179 | 15045 | 15883 | 19090 | 20376 | 19652 | 18610 | 18334 | 20996 | 22302 | 23595 | 20735 | 19458 | 20028
5138 | 5138 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 2 | 13431 | 12544 | 13497 | 15181 | 16079 | 15595 | 14742 | 14625 | 15422 | 18455 | 19616 | 18856 | 18016 | 17785 | 20253 | 21552 | 22708 | 20066 | 18858 | 19421
5139 | 5139 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 3 | 13067 | 12331 | 13184 | 14851 | 15696 | 15131 | 14478 | 14344 | 15024 | 17979 | 19033 | 18226 | 17583 | 17279 | 19696 | 20933 | 22000 | 19547 | 18387 | 18854
5140 | 5140 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 4 | 12986 | 12235 | 13107 | 14751 | 15541 | 15004 | 14263 | 14126 | 14795 | 17597 | 18561 | 17754 | 17024 | 16816 | 19090 | 20251 | 21224 | 18786 | 17765 | 18254
5141 | 5141 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 5 | 13289 | 12155 | 13095 | 15057 | 15734 | 15116 | 14112 | 13890 | 14600 | 17548 | 18404 | 17465 | 16464 | 16363 | 18821 | 19826 | 20765 | 18009 | 17109 | 17657
5142 | 5142 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 6 | 14091 | 12026 | 13041 | 15735 | 16446 | 15763 | 14004 | 13593 | 14322 | 18014 | 18582 | 17660 | 15953 | 15802 | 18901 | 19940 | 20687 | 17270 | 16378 | 16978
5143 | 5143 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 7 | 15196 | 12156 | 13177 | 16775 | 17612 | 16778 | 14139 | 13636 | 14250 | 18955 | 19381 | 18320 | 15759 | 15551 | 19393 | 20633 | 21231 | 16934 | 16032 | 16680
5144 | 5144 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 8 | 16001 | 12886 | 13788 | 17692 | 18745 | 17583 | 14877 | 14357 | 14917 | 19990 | 20564 | 19060 | 16370 | 16133 | 20073 | 21517 | 22274 | 17504 | 16579 | 17263
5145 | 5145 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 9 | 16474 | 13749 | 14581 | 18456 | 19549 | 18061 | 15604 | 15207 | 15744 | 20790 | 21576 | 19574 | 17056 | 16883 | 20797 | 22251 | 23288 | 18185 | 17364 | 17999
5146 | 5146 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 10 | 16614 | 14147 | 15039 | 19046 | 20179 | 18246 | 15834 | 15709 | 16306 | 21522 | 22406 | 19888 | 17421 | 17513 | 21592 | 23070 | 24158 | 18624 | 18008 | 18688
5147 | 5147 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 11 | 16702 | 14528 | 15469 | 19575 | 20790 | 18369 | 16038 | 16159 | 16807 | 22244 | 23222 | 20137 | 17741 | 18116 | 22315 | 23880 | 25094 | 19038 | 18602 | 19349
5148 | 5148 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 12 | 16743 | 14811 | 15734 | 19984 | 21362 | 18465 | 16192 | 16491 | 17111 | 22915 | 23810 | 20321 | 17964 | 18461 | 22842 | 24640 | 25825 | 19293 | 19014 | 19722
5149 | 5149 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 13 | 16753 | 14948 | 15878 | 20400 | 21788 | 18536 | 16118 | 16634 | 17241 | 23384 | 24316 | 20442 | 17898 | 18611 | 23310 | 25127 | 26479 | 19258 | 19169 | 19870
5150 | 5150 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 14 | 16799 | 15078 | 15921 | 20652 | 22114 | 18579 | 16039 | 16773 | 17284 | 23716 | 24541 | 20485 | 17829 | 18612 | 23543 | 25462 | 26882 | 19171 | 19291 | 19852
5151 | 5151 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 15 | 16815 | 15368 | 16042 | 20928 | 22415 | 18589 | 16076 | 17078 | 17411 | 23997 | 24771 | 20483 | 17897 | 18695 | 23773 | 25741 | 27276 | 19219 | 19612 | 19928
5152 | 5152 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 16 | 17028 | 15818 | 16526 | 21538 | 22834 | 18795 | 16306 | 17513 | 17849 | 24393 | 25004 | 20626 | 18074 | 19114 | 24516 | 26072 | 27541 | 19393 | 20021 | 20340
5153 | 5153 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 17 | 17290 | 16485 | 17251 | 21920 | 23243 | 19175 | 16761 | 18198 | 18581 | 24751 | 25393 | 21063 | 18637 | 19888 | 24990 | 26515 | 28043 | 19986 | 20735 | 21137
5154 | 5154 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 18 | 17358 | 16886 | 17567 | 21949 | 23231 | 19400 | 17341 | 18845 | 19222 | 24824 | 25834 | 21606 | 19461 | 20756 | 25185 | 26696 | 28718 | 20887 | 21719 | 22082
5155 | 5155 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 19 | 17252 | 17033 | 17291 | 21765 | 22877 | 19399 | 17554 | 19022 | 19066 | 24710 | 25705 | 21941 | 19981 | 20777 | 25483 | 26911 | 28693 | 21570 | 22310 | 22180
5156 | 5156 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 20 | 16690 | 16693 | 16945 | 21244 | 22405 | 18903 | 17607 | 18866 | 18776 | 24450 | 25580 | 21719 | 20396 | 20842 | 25418 | 27046 | 28591 | 22162 | 22602 | 22322
5157 | 5157 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 21 | 16150 | 16431 | 17026 | 21035 | 22206 | 18533 | 17470 | 18803 | 19089 | 24563 | 25896 | 21813 | 20740 | 21480 | 25888 | 27615 | 29090 | 22750 | 23128 | 23139
5158 | 5158 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 22 | 15258 | 15840 | 16326 | 19903 | 21060 | 17694 | 17077 | 18308 | 18515 | 23603 | 24894 | 21212 | 20560 | 21049 | 25128 | 26883 | 28242 | 22668 | 22886 | 22778
5159 | 5159 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 23 | 13976 | 14997 | 15404 | 18394 | 19504 | 16372 | 16376 | 17449 | 17584 | 22094 | 23410 | 19915 | 19915 | 20138 | 23739 | 25453 | 26672 | 22068 | 22069 | 21886
5160 | 5160 | 215 | 8 | 3 | Summer | 8 | 2 | Summer | 24 | 12953 | 14161 | 14567 | 17168 | 18148 | 15318 | 15552 | 16510 | 16696 | 20736 | 22019 | 18880 | 19050 | 19213 | 22532 | 24096 | 25306 | 21210 | 21077 | 20950
5161 | 5161 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 1 | 12470 | 13349 | 15475 | 16434 | 17255 | 14765 | 14720 | 15541 | 17755 | 19823 | 21252 | 18063 | 17514 | 20581 | 21928 | 23224 | 24361 | 19317 | 19909 | 22481
5162 | 5162 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 2 | 12137 | 13002 | 14959 | 15884 | 16610 | 14343 | 14309 | 15098 | 17143 | 19080 | 20393 | 17500 | 16989 | 19842 | 21182 | 22355 | 23394 | 18718 | 19302 | 21669
5163 | 5163 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 3 | 11925 | 12718 | 14633 | 15508 | 16165 | 14084 | 14035 | 14713 | 16723 | 18518 | 19738 | 17085 | 16586 | 19290 | 20577 | 21659 | 22588 | 18244 | 18731 | 21045
5164 | 5164 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 4 | 11841 | 12637 | 14551 | 15370 | 15980 | 13910 | 13859 | 14522 | 16439 | 18112 | 19216 | 16581 | 16135 | 18728 | 19933 | 20911 | 21724 | 17640 | 18142 | 20315
5165 | 5165 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 5 | 11822 | 12649 | 14880 | 15594 | 16171 | 13821 | 13680 | 14382 | 16512 | 18043 | 19041 | 16094 | 15674 | 18517 | 19561 | 20482 | 21087 | 17014 | 17565 | 19932
5166 | 5166 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 6 | 11816 | 12645 | 15583 | 16333 | 16721 | 13772 | 13457 | 14167 | 16979 | 18326 | 19267 | 15654 | 15130 | 18662 | 19738 | 20436 | 20890 | 16315 | 16908 | 19916
5167 | 5167 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 7 | 12128 | 12833 | 16683 | 17552 | 17780 | 13961 | 13567 | 14179 | 17859 | 19211 | 20078 | 15551 | 14910 | 19215 | 20482 | 21017 | 21371 | 15992 | 16628 | 20354
5168 | 5168 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 8 | 12986 | 13522 | 17718 | 18781 | 19102 | 14783 | 14383 | 14955 | 18783 | 20504 | 21388 | 16278 | 15571 | 20006 | 21476 | 22160 | 22532 | 16622 | 17287 | 21094
5169 | 5169 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 9 | 13791 | 14442 | 18644 | 19723 | 20280 | 15637 | 15378 | 15941 | 19680 | 21668 | 22537 | 17108 | 16511 | 20874 | 22357 | 23313 | 23614 | 17541 | 18159 | 21952
5170 | 5170 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 10 | 14020 | 15000 | 19338 | 20443 | 21123 | 15938 | 15967 | 16591 | 20477 | 22583 | 23490 | 17546 | 17190 | 21761 | 23272 | 24283 | 24749 | 18280 | 18946 | 22901
5171 | 5171 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 11 | 14101 | 15326 | 19792 | 20985 | 21755 | 16048 | 16324 | 17023 | 21036 | 23319 | 24193 | 17795 | 17652 | 22396 | 23997 | 25151 | 25761 | 18790 | 19525 | 23598
5172 | 5172 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 12 | 14127 | 15509 | 20120 | 21469 | 22189 | 16115 | 16567 | 17241 | 21420 | 23806 | 24698 | 17930 | 17958 | 22835 | 24671 | 25793 | 26489 | 19118 | 19815 | 24068
5173 | 5173 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 13 | 14020 | 15650 | 20549 | 21929 | 22636 | 16054 | 16723 | 17407 | 21870 | 24331 | 25075 | 17901 | 18125 | 23311 | 25168 | 26477 | 27193 | 19288 | 19979 | 24573
5174 | 5174 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 14 | 13898 | 15668 | 20778 | 22218 | 22858 | 15953 | 16841 | 17420 | 22100 | 24545 | 25224 | 17802 | 18237 | 23531 | 25483 | 26844 | 27474 | 19388 | 19942 | 24796
5175 | 5175 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 15 | 13858 | 15699 | 20945 | 22396 | 23008 | 15878 | 17037 | 17422 | 22260 | 24677 | 25301 | 17739 | 18452 | 23659 | 25659 | 27119 | 27640 | 19600 | 19913 | 24904
5176 | 5176 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 16 | 14058 | 16100 | 21417 | 22773 | 23280 | 16051 | 17405 | 17817 | 22912 | 24867 | 25412 | 17881 | 18799 | 24346 | 25930 | 27344 | 27884 | 19937 | 20255 | 25570
5177 | 5177 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 17 | 14480 | 16747 | 21726 | 23116 | 23559 | 16431 | 18009 | 18472 | 23267 | 25175 | 25681 | 18372 | 19416 | 24741 | 26298 | 27778 | 28220 | 20576 | 20978 | 25981
5178 | 5178 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 18 | 14802 | 17009 | 21734 | 23087 | 23727 | 16981 | 18598 | 19042 | 23264 | 25565 | 25978 | 19138 | 20292 | 24914 | 26451 | 28429 | 28530 | 21546 | 21912 | 26222
5179 | 5179 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 19 | 14912 | 16731 | 21548 | 22735 | 23449 | 17200 | 18769 | 18865 | 23237 | 25389 | 25982 | 19643 | 20775 | 25191 | 26651 | 28403 | 28428 | 22161 | 22027 | 26633
5180 | 5180 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 20 | 14834 | 16377 | 21005 | 22229 | 22969 | 17235 | 18592 | 18538 | 22860 | 25171 | 25712 | 19983 | 20931 | 25082 | 26743 | 28279 | 28229 | 22465 | 22185 | 26630
5181 | 5181 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 21 | 14504 | 16459 | 20777 | 21992 | 22887 | 17055 | 18483 | 18794 | 22903 | 25399 | 26005 | 20240 | 21219 | 25502 | 27264 | 28732 | 28806 | 22976 | 22993 | 27258
5182 | 5182 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 22 | 14050 | 15730 | 19612 | 20809 | 21661 | 16616 | 17942 | 18162 | 21907 | 24333 | 25098 | 19998 | 20859 | 24683 | 26484 | 27842 | 28005 | 22706 | 22616 | 26540
5183 | 5183 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 23 | 13392 | 14823 | 18108 | 19267 | 20111 | 15915 | 17082 | 17231 | 20450 | 22839 | 23626 | 19345 | 20022 | 23289 | 25048 | 26280 | 26596 | 21893 | 21734 | 25200
5184 | 5184 | 216 | 8 | 4 | Summer | 8 | 3 | Summer | 24 | 12705 | 14022 | 16887 | 17933 | 18737 | 15112 | 16153 | 16347 | 19209 | 21441 | 22326 | 18496 | 19048 | 22089 | 23715 | 24923 | 25222 | 20907 | 20807 | 24007
5185 | 5185 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 1 | 12228 | 14872 | 16089 | 16968 | 17980 | 14282 | 15128 | 17296 | 18434 | 20618 | 20509 | 16986 | 17883 | 21376 | 22736 | 23914 | 23502 | 19670 | 22264 | 23344
5186 | 5186 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 2 | 11883 | 14352 | 15539 | 16305 | 17228 | 13864 | 14680 | 16671 | 17803 | 19741 | 19665 | 16454 | 17329 | 20633 | 21862 | 22940 | 22526 | 19049 | 21428 | 22534
5187 | 5187 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 3 | 11674 | 14038 | 15170 | 15871 | 16727 | 13603 | 14311 | 16274 | 17346 | 19117 | 19053 | 16071 | 16835 | 20039 | 21185 | 22150 | 21787 | 18492 | 20834 | 21873
5188 | 5188 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 4 | 11566 | 13952 | 15038 | 15698 | 16495 | 13445 | 14146 | 16026 | 17014 | 18642 | 18423 | 15656 | 16402 | 19428 | 20463 | 21309 | 20872 | 17907 | 20101 | 21102
5189 | 5189 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 5 | 11504 | 14282 | 15280 | 15928 | 16633 | 13308 | 14055 | 16166 | 17052 | 18499 | 17965 | 15258 | 16012 | 19111 | 20094 | 20721 | 20102 | 17350 | 19730 | 20596
5190 | 5190 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 6 | 11384 | 14996 | 16016 | 16520 | 17203 | 13112 | 13886 | 16696 | 17600 | 18763 | 17592 | 14781 | 15509 | 19335 | 20072 | 20562 | 19376 | 16699 | 19713 | 20636
5191 | 5191 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 7 | 11586 | 16179 | 17302 | 17675 | 18385 | 13301 | 14000 | 17706 | 18678 | 19685 | 17717 | 14675 | 15372 | 20190 | 20747 | 21127 | 19191 | 16476 | 20197 | 21353
5192 | 5192 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 8 | 12536 | 17358 | 18640 | 19113 | 19886 | 14221 | 14891 | 18791 | 19943 | 21143 | 18734 | 15473 | 16177 | 21309 | 22016 | 22412 | 20140 | 17239 | 21050 | 22409
5193 | 5193 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 9 | 13457 | 18242 | 19531 | 20227 | 20986 | 15150 | 15829 | 19654 | 20830 | 22288 | 19874 | 16360 | 17020 | 22141 | 23109 | 23435 | 21271 | 18056 | 21863 | 23228
5194 | 5194 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 10 | 13806 | 18779 | 20103 | 20924 | 21713 | 15583 | 16325 | 20312 | 21499 | 23095 | 20754 | 16892 | 17603 | 22902 | 23933 | 24434 | 22239 | 18699 | 22676 | 24056
5195 | 5195 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 11 | 14419 | 19529 | 20951 | 21838 | 22635 | 16229 | 17045 | 21152 | 22442 | 24103 | 21651 | 17640 | 18427 | 23928 | 25095 | 25731 | 23226 | 19575 | 23661 | 25144
5196 | 5196 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 12 | 14657 | 19882 | 21484 | 22303 | 23090 | 16506 | 17298 | 21566 | 23055 | 24610 | 22100 | 17978 | 18732 | 24630 | 25770 | 26492 | 23715 | 19903 | 24169 | 25886
5197 | 5197 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 13 | 14717 | 20199 | 21838 | 22656 | 23328 | 16557 | 17362 | 21912 | 23440 | 24886 | 22333 | 18044 | 18804 | 25030 | 26347 | 27093 | 23968 | 19966 | 24567 | 26307
5198 | 5198 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 14 | 14904 | 20530 | 22221 | 22980 | 23586 | 16770 | 17473 | 22236 | 23828 | 25148 | 22445 | 18252 | 18871 | 25438 | 26813 | 27468 | 24054 | 20024 | 24881 | 26732
5199 | 5199 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 15 | 15100 | 20709 | 22405 | 23141 | 23712 | 16978 | 17491 | 22411 | 24006 | 25257 | 22549 | 18475 | 18867 | 25622 | 27106 | 27646 | 24149 | 20009 | 25012 | 26935
5200 | 5200 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 16 | 15529 | 21182 | 22837 | 23470 | 23933 | 17395 | 17937 | 23063 | 24392 | 25422 | 22740 | 18877 | 19269 | 25958 | 27390 | 27942 | 24300 | 20395 | 25714 | 27249
5201 | 5201 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 17 | 16031 | 21383 | 23075 | 23638 | 24126 | 17890 | 18482 | 23306 | 24575 | 25633 | 22918 | 19376 | 19871 | 26214 | 27712 | 28166 | 24524 | 21008 | 26018 | 27512
5202 | 5202 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 18 | 16228 | 21227 | 22873 | 23605 | 23946 | 18286 | 18833 | 23122 | 24444 | 25706 | 23108 | 20049 | 20526 | 26173 | 28175 | 28302 | 24943 | 21766 | 26092 | 27561
5203 | 5203 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 19 | 16317 | 20953 | 22437 | 23248 | 23593 | 18384 | 18572 | 22996 | 24217 | 25570 | 23087 | 20437 | 20457 | 26267 | 28059 | 28117 | 25169 | 21832 | 26438 | 27797
5204 | 5204 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 20 | 15944 | 20357 | 21888 | 22715 | 23030 | 18177 | 18201 | 22541 | 23881 | 25143 | 22971 | 20508 | 20471 | 26293 | 27872 | 27864 | 25331 | 21975 | 26411 | 27966
5205 | 5205 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 21 | 15678 | 20112 | 21621 | 22609 | 22938 | 18029 | 18403 | 22524 | 23919 | 25351 | 23197 | 20738 | 21065 | 26741 | 28271 | 28402 | 25962 | 22775 | 27039 | 28652
5206 | 5206 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 22 | 15059 | 18931 | 20411 | 21340 | 21805 | 17460 | 17737 | 21477 | 22892 | 24395 | 22618 | 20336 | 20580 | 25917 | 27349 | 27568 | 25565 | 22381 | 26316 | 27942
5207 | 5207 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 23 | 14243 | 17478 | 18891 | 19819 | 20313 | 16616 | 16818 | 20026 | 21396 | 22931 | 21622 | 19497 | 19686 | 24486 | 25796 | 26174 | 24629 | 21511 | 24994 | 26556
5208 | 5208 | 217 | 8 | 5 | Summer | 8 | 4 | Summer | 24 | 13472 | 16283 | 17577 | 18474 | 18976 | 15720 | 15955 | 18786 | 20062 | 21627 | 20607 | 18544 | 18778 | 23174 | 24451 | 24816 | 23646 | 20602 | 23819 | 25231
5209 | 5209 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 1 | 12714 | 15563 | 16741 | 17805 | 17599 | 14799 | 16934 | 18052 | 19163 | 20023 | 18394 | 17476 | 20114 | 22298 | 23529 | 23218 | 20976 | 22119 | 23219 | 24363
5210 | 5210 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 2 | 12373 | 15040 | 16117 | 17075 | 16883 | 14381 | 16342 | 17450 | 18437 | 19214 | 17694 | 16953 | 19383 | 21451 | 22590 | 22265 | 20172 | 21314 | 22434 | 23445
5211 | 5211 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 3 | 12118 | 14681 | 15702 | 16584 | 16404 | 14026 | 15966 | 17013 | 17914 | 18635 | 17149 | 16479 | 18858 | 20769 | 21821 | 21542 | 19526 | 20721 | 21774 | 22707
5212 | 5212 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 4 | 12004 | 14566 | 15545 | 16372 | 16048 | 13888 | 15762 | 16729 | 17547 | 18055 | 16623 | 16087 | 18318 | 20107 | 21018 | 20652 | 18757 | 20004 | 21008 | 21862
5213 | 5213 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 5 | 12031 | 14838 | 15802 | 16539 | 15958 | 13836 | 15956 | 16829 | 17563 | 17663 | 16218 | 15749 | 18168 | 19791 | 20480 | 19918 | 18074 | 19655 | 20518 | 21358
5214 | 5214 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 6 | 12026 | 15551 | 16431 | 17148 | 15934 | 13699 | 16542 | 17440 | 17917 | 17360 | 15699 | 15306 | 18359 | 19795 | 20359 | 19222 | 17289 | 19655 | 20566 | 21228
5215 | 5215 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 7 | 12208 | 16786 | 17556 | 18296 | 16229 | 13757 | 17538 | 18499 | 18847 | 17479 | 15565 | 15149 | 18946 | 20418 | 20882 | 19003 | 16991 | 20076 | 21216 | 21770
5216 | 5216 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 8 | 12715 | 17843 | 18713 | 19506 | 17040 | 14347 | 18359 | 19499 | 19984 | 18255 | 16187 | 15683 | 19595 | 21436 | 21903 | 19663 | 17531 | 20649 | 21994 | 22754
5217 | 5217 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 9 | 13402 | 18598 | 19700 | 20469 | 18074 | 15118 | 19076 | 20250 | 20936 | 19267 | 17088 | 16381 | 20276 | 22378 | 22775 | 20645 | 18429 | 21303 | 22656 | 23722
5218 | 5218 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 10 | 13905 | 19257 | 20474 | 21278 | 18929 | 15679 | 19800 | 20997 | 21795 | 20227 | 17838 | 17044 | 21115 | 23336 | 23844 | 21701 | 19267 | 22193 | 23562 | 24675
5219 | 5219 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 11 | 14293 | 19850 | 21160 | 21960 | 19478 | 16157 | 20399 | 21700 | 22572 | 20879 | 18393 | 17629 | 21809 | 24216 | 24904 | 22452 | 19887 | 22943 | 24419 | 25663
5220 | 5220 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 12 | 14560 | 20387 | 21670 | 22462 | 19933 | 16455 | 20858 | 22355 | 23137 | 21374 | 18781 | 17978 | 22333 | 24870 | 25712 | 22982 | 20309 | 23498 | 25210 | 26435
5221 | 5221 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 13 | 14722 | 20863 | 22148 | 22827 | 20276 | 16649 | 21329 | 22860 | 23674 | 21735 | 18993 | 18175 | 22838 | 25448 | 26443 | 23357 | 20530 | 24024 | 25754 | 27188
5222 | 5222 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 14 | 14841 | 21230 | 22497 | 23116 | 20402 | 16775 | 21666 | 23273 | 23997 | 21863 | 19164 | 18270 | 23158 | 25736 | 26835 | 23468 | 20688 | 24346 | 26183 | 27659
5223 | 5223 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 15 | 14920 | 21452 | 22680 | 23261 | 20543 | 16810 | 21854 | 23466 | 24164 | 21982 | 19292 | 18285 | 23336 | 25876 | 27031 | 23581 | 20810 | 24498 | 26398 | 27961
5224 | 5224 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 16 | 15332 | 21845 | 23001 | 23467 | 20748 | 17239 | 22452 | 23843 | 24381 | 22158 | 19663 | 18677 | 24031 | 26013 | 27314 | 23708 | 21135 | 25174 | 26687 | 28184
5225 | 5225 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 17 | 16013 | 22212 | 23304 | 23786 | 20973 | 17927 | 22836 | 24157 | 24703 | 22472 | 20196 | 19402 | 24446 | 26339 | 27677 | 24059 | 21751 | 25617 | 27092 | 28669
5226 | 5226 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 18 | 16268 | 22193 | 23387 | 23746 | 21179 | 18442 | 22833 | 24187 | 25078 | 22810 | 20712 | 20200 | 24629 | 26937 | 27984 | 24659 | 22371 | 25877 | 27322 | 29382
5227 | 5227 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 19 | 16017 | 21836 | 23074 | 23457 | 21015 | 18250 | 22754 | 24010 | 24892 | 22802 | 20573 | 20183 | 24891 | 27058 | 27841 | 24959 | 22467 | 26298 | 27634 | 29402
5228 | 5228 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 20 | 15641 | 21289 | 22507 | 22877 | 20634 | 17890 | 22286 | 23624 | 24590 | 22607 | 20426 | 20154 | 24721 | 27131 | 27564 | 25092 | 22563 | 26298 | 27822 | 29310
5229 | 5229 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 21 | 15721 | 21014 | 22375 | 22754 | 20488 | 18068 | 22224 | 23594 | 24744 | 22774 | 20811 | 20688 | 25085 | 27723 | 28060 | 25695 | 23266 | 26921 | 28506 | 29878
5230 | 5230 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 22 | 14982 | 19776 | 21093 | 21594 | 19697 | 17379 | 21142 | 22520 | 23646 | 22145 | 20192 | 20173 | 24236 | 26806 | 27196 | 25278 | 22785 | 26187 | 27792 | 29023
5231 | 5231 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 23 | 14094 | 18259 | 19556 | 20097 | 18620 | 16449 | 19658 | 21003 | 22148 | 21132 | 19183 | 19256 | 22834 | 25361 | 25785 | 24332 | 21824 | 24845 | 26398 | 27480
5232 | 5232 | 218 | 8 | 6 | Summer | 8 | 5 | Summer | 24 | 13343 | 16962 | 18180 | 18757 | 17596 | 15586 | 18397 | 19642 | 20758 | 20092 | 18185 | 18342 | 21618 | 23974 | 24411 | 23325 | 20825 | 23650 | 25056 | 26115
5233 | 5233 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 1 | 14343 | 16190 | 17578 | 17461 | 15918 | 16580 | 17714 | 18758 | 20093 | 18006 | 17004 | 19670 | 21024 | 23237 | 22886 | 20741 | 19575 | 23115 | 24221 | 25187
5234 | 5234 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 2 | 13856 | 15570 | 16867 | 16749 | 15308 | 15993 | 17114 | 18049 | 19247 | 17314 | 16496 | 18942 | 20313 | 22281 | 21938 | 19944 | 18972 | 22322 | 23303 | 24181
5235 | 5235 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 3 | 13571 | 15198 | 16424 | 16306 | 14883 | 15662 | 16729 | 17572 | 18674 | 16821 | 16077 | 18468 | 19761 | 21562 | 21270 | 19335 | 18431 | 21701 | 22599 | 23377
5236 | 5236 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 4 | 13498 | 15065 | 16243 | 15986 | 14604 | 15504 | 16497 | 17278 | 18272 | 16350 | 15742 | 17999 | 19201 | 20834 | 20426 | 18607 | 17873 | 20956 | 21781 | 22458
5237 | 5237 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 5 | 13807 | 15325 | 16416 | 15902 | 14410 | 15724 | 16634 | 17341 | 18193 | 15979 | 15440 | 17887 | 18926 | 20376 | 19712 | 17931 | 17327 | 20467 | 21267 | 21758
5238 | 5238 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 6 | 14511 | 15958 | 17040 | 15889 | 14129 | 16333 | 17281 | 17758 | 18523 | 15499 | 15027 | 18120 | 19196 | 20317 | 19037 | 17150 | 16689 | 20514 | 21129 | 21503
5239 | 5239 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 7 | 15628 | 17115 | 18228 | 16217 | 14254 | 17364 | 18379 | 18755 | 19425 | 15423 | 14908 | 18768 | 20020 | 20973 | 18839 | 16866 | 16397 | 21174 | 21677 | 21961
5240 | 5240 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 8 | 16599 | 18326 | 19515 | 17102 | 15030 | 18262 | 19467 | 19988 | 20694 | 16149 | 15525 | 19527 | 20941 | 22139 | 19593 | 17482 | 16944 | 22030 | 22717 | 23025
5241 | 5241 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 9 | 17379 | 19350 | 20548 | 18195 | 15982 | 19029 | 20276 | 21009 | 21747 | 17126 | 16283 | 20275 | 21693 | 23128 | 20640 | 18429 | 17662 | 22748 | 23726 | 23971
5242 | 5242 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 10 | 17922 | 20068 | 21306 | 18982 | 16569 | 19679 | 20957 | 21796 | 22566 | 17816 | 16877 | 21040 | 22479 | 24044 | 21624 | 19200 | 18326 | 23602 | 24619 | 25024
5243 | 5243 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 11 | 18386 | 20663 | 21935 | 19465 | 16985 | 20194 | 21574 | 22498 | 23277 | 18299 | 17380 | 21662 | 23212 | 24841 | 22302 | 19756 | 18920 | 24380 | 25542 | 26073
5244 | 5244 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 12 | 18782 | 21185 | 22458 | 19934 | 17334 | 20657 | 22233 | 23068 | 23820 | 18694 | 17732 | 22193 | 23965 | 25436 | 22848 | 20191 | 19308 | 25179 | 26321 | 26919
5245 | 5245 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 13 | 19190 | 21641 | 22808 | 20233 | 17498 | 21083 | 22696 | 23561 | 24187 | 18866 | 17890 | 22651 | 24461 | 25809 | 23183 | 20368 | 19471 | 25684 | 27028 | 27636
5246 | 5246 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 14 | 19431 | 21913 | 23038 | 20279 | 17566 | 21337 | 23017 | 23808 | 24364 | 18956 | 17912 | 22900 | 24785 | 25971 | 23212 | 20447 | 19443 | 26026 | 27416 | 27941
5247 | 5247 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 15 | 19603 | 22088 | 23182 | 20401 | 17685 | 21517 | 23200 | 23949 | 24468 | 19073 | 17919 | 23061 | 24967 | 26055 | 23313 | 20545 | 19422 | 26217 | 27699 | 28114
5248 | 5248 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 16 | 20046 | 22433 | 23402 | 20620 | 18102 | 22107 | 23576 | 24199 | 24633 | 19452 | 18310 | 23741 | 25295 | 26139 | 23445 | 20879 | 19804 | 26498 | 27933 | 28379
5249 | 5249 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 17 | 20385 | 22710 | 23690 | 20829 | 18633 | 22472 | 23871 | 24498 | 24955 | 19947 | 19004 | 24143 | 25674 | 26509 | 23771 | 21487 | 20547 | 26883 | 28390 | 28736
5250 | 5250 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 18 | 20514 | 22808 | 23647 | 21062 | 19036 | 22535 | 23957 | 24869 | 25269 | 20502 | 19825 | 24377 | 25884 | 27028 | 24427 | 22162 | 21570 | 27180 | 29167 | 29169
5251 | 5251 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 19 | 20336 | 22522 | 23338 | 20896 | 18683 | 22472 | 23779 | 24659 | 25185 | 20344 | 19801 | 24607 | 26042 | 27223 | 24732 | 22259 | 21743 | 27525 | 29230 | 29164
5252 | 5252 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 20 | 19745 | 21933 | 22687 | 20497 | 18348 | 21986 | 23350 | 24318 | 24722 | 20121 | 19717 | 24390 | 26030 | 27163 | 24826 | 22346 | 21917 | 27709 | 29151 | 28963
5253 | 5253 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 21 | 19505 | 21758 | 22523 | 20329 | 18424 | 21887 | 23274 | 24402 | 24869 | 20443 | 20194 | 24698 | 26432 | 27745 | 25385 | 23026 | 22714 | 28389 | 29709 | 29625
5254 | 5254 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 22 | 18332 | 20488 | 21351 | 19530 | 17638 | 20785 | 22176 | 23257 | 23881 | 19792 | 19658 | 23807 | 25575 | 26963 | 24954 | 22547 | 22313 | 27677 | 28864 | 28848
5255 | 5255 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 23 | 16895 | 18949 | 19858 | 18462 | 16612 | 19293 | 20649 | 21746 | 22406 | 18784 | 18749 | 22385 | 24134 | 25524 | 24001 | 21580 | 21424 | 26275 | 27324 | 27452
5256 | 5256 | 219 | 8 | 7 | Summer | 8 | 6 | Summer | 24 | 15709 | 17613 | 18517 | 17444 | 15637 | 18037 | 19278 | 20344 | 21083 | 17783 | 17857 | 21163 | 22777 | 24239 | 22989 | 20578 | 20491 | 24927 | 25963 | 26079
5257 | 5257 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 1 | 15011 | 16963 | 17169 | 15735 | 14459 | 17250 | 18283 | 19602 | 19519 | 17050 | 17582 | 20454 | 21816 | 22406 | 20390 | 19767 | 20442 | 23989 | 24983 | 24329
5258 | 5258 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 2 | 14513 | 16300 | 16510 | 15158 | 14076 | 16694 | 17623 | 18804 | 18754 | 16609 | 17081 | 19783 | 21017 | 21505 | 19632 | 19223 | 19842 | 23109 | 24006 | 23354
5259 | 5259 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 3 | 14159 | 15852 | 16046 | 14727 | 13723 | 16293 | 17138 | 18231 | 18197 | 16329 | 16700 | 19238 | 20379 | 20817 | 19008 | 18826 | 19339 | 22376 | 23176 | 22591
5260 | 5260 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 4 | 14054 | 15668 | 15736 | 14455 | 13614 | 16093 | 16883 | 17880 | 17684 | 16113 | 16404 | 18728 | 19760 | 20011 | 18302 | 18362 | 18788 | 21565 | 22266 | 21614
5261 | 5261 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 5 | 14329 | 15868 | 15683 | 14293 | 13590 | 16289 | 17014 | 17881 | 17357 | 16229 | 16349 | 18530 | 19511 | 19359 | 17669 | 18249 | 18445 | 21093 | 21591 | 20782
5262 | 5262 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 6 | 15007 | 16507 | 15704 | 14037 | 13456 | 16994 | 17506 | 18294 | 17104 | 16687 | 16685 | 18866 | 19602 | 18744 | 16931 | 18461 | 18485 | 20980 | 21354 | 19998
5263 | 5263 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 7 | 16220 | 17713 | 16045 | 14169 | 13496 | 18106 | 18532 | 19257 | 17260 | 17613 | 17329 | 19724 | 20265 | 18570 | 16647 | 19132 | 18919 | 21510 | 21780 | 19722
5264 | 5264 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 8 | 17286 | 18900 | 16881 | 14881 | 14058 | 19125 | 19702 | 20488 | 18064 | 18564 | 17838 | 20605 | 21282 | 19252 | 17205 | 19954 | 19298 | 22477 | 22778 | 20397
5265 | 5265 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 9 | 18032 | 19875 | 17934 | 15780 | 14788 | 19874 | 20668 | 21496 | 19079 | 19240 | 18194 | 21311 | 22222 | 20248 | 18102 | 20599 | 19537 | 23424 | 23658 | 21383
5266 | 5266 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 10 | 18732 | 20730 | 18807 | 16457 | 15360 | 20626 | 21522 | 22396 | 20061 | 19779 | 18690 | 22178 | 23141 | 21320 | 18962 | 21215 | 20120 | 24396 | 24802 | 22524
5267 | 5267 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 11 | 19347 | 21480 | 19390 | 16949 | 15873 | 21329 | 22320 | 23184 | 20730 | 20336 | 19151 | 22990 | 24090 | 22090 | 19607 | 21838 | 20670 | 25415 | 25948 | 23360
5268 | 5268 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 12 | 19859 | 22043 | 19869 | 17313 | 16194 | 21982 | 22892 | 23735 | 21246 | 20692 | 19418 | 23745 | 24822 | 22643 | 20055 | 22232 | 20979 | 26201 | 26806 | 23936
5269 | 5269 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 13 | 20276 | 22428 | 20170 | 17472 | 16342 | 22443 | 23375 | 24093 | 21555 | 20968 | 19723 | 24236 | 25475 | 22982 | 20236 | 22530 | 21282 | 26902 | 27524 | 24286
5270 | 5270 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 14 | 20526 | 22654 | 20194 | 17536 | 16370 | 22742 | 23604 | 24269 | 21583 | 21044 | 19859 | 24554 | 25869 | 22994 | 20295 | 22601 | 21407 | 27268 | 27807 | 24295
5271 | 5271 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 15 | 20787 | 22858 | 20360 | 17706 | 16431 | 22964 | 23790 | 24418 | 21731 | 21126 | 20028 | 24788 | 26204 | 23136 | 20442 | 22675 | 21562 | 27589 | 28019 | 24438
5272 | 5272 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 16 | 21270 | 23213 | 20685 | 18206 | 16977 | 23455 | 24167 | 24686 | 22019 | 21485 | 20766 | 25216 | 26608 | 23384 | 20890 | 22987 | 22314 | 27934 | 28390 | 24669
5273 | 5273 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 17 | 21698 | 23545 | 20937 | 18780 | 17718 | 23809 | 24513 | 25050 | 22362 | 21921 | 21302 | 25644 | 27103 | 23766 | 21536 | 23416 | 22887 | 28444 | 28799 | 25057
5274 | 5274 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 18 | 21648 | 23380 | 20994 | 19035 | 18167 | 23774 | 24721 | 25182 | 22612 | 22239 | 21434 | 25712 | 27649 | 24298 | 22097 | 23915 | 23119 | 29109 | 29125 | 25669
5275 | 5275 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 19 | 21188 | 22880 | 20663 | 18537 | 17894 | 23437 | 24353 | 24920 | 22463 | 22349 | 21549 | 25687 | 27445 | 24428 | 22038 | 24326 | 23452 | 29043 | 28983 | 25914
5276 | 5276 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 20 | 20583 | 22142 | 20216 | 18149 | 17529 | 22968 | 23949 | 24373 | 22173 | 22252 | 21540 | 25582 | 27147 | 24455 | 22067 | 24508 | 23820 | 28952 | 28769 | 26062
5277 | 5277 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 21 | 20298 | 21920 | 20025 | 18209 | 17671 | 22838 | 23971 | 24447 | 22259 | 22157 | 21824 | 25901 | 27412 | 24951 | 22717 | 24754 | 24474 | 29493 | 29422 | 26776
5278 | 5278 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 22 | 19093 | 20751 | 19228 | 17434 | 16999 | 21734 | 22802 | 23435 | 21644 | 21330 | 21029 | 25032 | 26459 | 24506 | 22235 | 24084 | 23877 | 28654 | 28660 | 26423
5279 | 5279 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 23 | 17584 | 19258 | 18149 | 16406 | 16052 | 20170 | 21267 | 21925 | 20612 | 20025 | 19873 | 23545 | 24889 | 23527 | 21248 | 22789 | 22800 | 27095 | 27256 | 25479
5280 | 5280 | 220 | 8 | 8 | Summer | 8 | 7 | Summer | 24 | 16334 | 17928 | 17145 | 15442 | 15231 | 18811 | 19870 | 20601 | 19582 | 18852 | 18888 | 22180 | 23525 | 22528 | 20239 | 21629 | 21821 | 25756 | 25898 | 24477
5281 | 5281 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 1 | 15546 | 16646 | 15489 | 14800 | 14743 | 17830 | 19122 | 19053 | 17508 | 17061 | 17973 | 21227 | 22684 | 19980 | 19418 | 20083 | 21013 | 24752 | 24161 | 21677
5282 | 5282 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 2 | 14945 | 15978 | 14904 | 14407 | 14344 | 17155 | 18314 | 18278 | 16840 | 16551 | 17472 | 20427 | 21755 | 19207 | 18870 | 19468 | 20396 | 23767 | 23177 | 20849
5283 | 5283 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 3 | 14583 | 15536 | 14501 | 14233 | 14105 | 16710 | 17783 | 17763 | 16365 | 16213 | 17105 | 19814 | 21058 | 18616 | 18504 | 18999 | 19906 | 22965 | 22436 | 20200
5284 | 5284 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 4 | 14472 | 15265 | 14259 | 14231 | 14088 | 16501 | 17500 | 17314 | 15954 | 15983 | 16810 | 19280 | 20401 | 17962 | 18084 | 18477 | 19342 | 22081 | 21486 | 19401
5285 | 5285 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 5 | 14739 | 15187 | 14093 | 14558 | 14324 | 16659 | 17549 | 17034 | 15628 | 15977 | 16811 | 19080 | 20010 | 17355 | 17990 | 18150 | 19062 | 21415 | 20644 | 18645
5286 | 5286 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 6 | 15394 | 15217 | 13861 | 15274 | 14995 | 17191 | 18031 | 16873 | 15207 | 16382 | 17221 | 19226 | 20010 | 16661 | 18238 | 18233 | 19213 | 21196 | 19870 | 17814
5287 | 5287 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 7 | 16564 | 15600 | 14034 | 16364 | 15990 | 18253 | 19059 | 17109 | 15178 | 17101 | 17994 | 19945 | 20717 | 16415 | 18927 | 18696 | 19762 | 21642 | 19604 | 17496
5288 | 5288 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 8 | 17781 | 16531 | 14860 | 17392 | 16701 | 19515 | 20389 | 18025 | 15945 | 17747 | 18668 | 21086 | 21908 | 17075 | 19845 | 19173 | 20328 | 22728 | 20351 | 18138
5289 | 5289 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 9 | 18840 | 17698 | 15909 | 18193 | 17215 | 20594 | 21517 | 19189 | 16991 | 18255 | 19205 | 22163 | 22966 | 18094 | 20619 | 19546 | 20758 | 23715 | 21465 | 19168
5290 | 5290 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 10 | 19582 | 18520 | 16520 | 18563 | 17527 | 21384 | 22334 | 20090 | 17696 | 18677 | 19686 | 23054 | 23887 | 18879 | 21169 | 20053 | 21242 | 24783 | 22533 | 20018
5291 | 5291 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 11 | 20190 | 19018 | 16951 | 18975 | 17807 | 22096 | 23054 | 20690 | 18199 | 19067 | 20144 | 23908 | 24720 | 19456 | 21727 | 20532 | 21782 | 25875 | 23303 | 20644
5292 | 5292 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 12 | 20696 | 19479 | 17282 | 19261 | 17997 | 22632 | 23569 | 21171 | 18576 | 19300 | 20604 | 24532 | 25308 | 19872 | 22089 | 20808 | 22297 | 26702 | 23852 | 21085
5293 | 5293 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 13 | 21182 | 19827 | 17478 | 19553 | 18321 | 23141 | 23959 | 21530 | 18782 | 19644 | 21006 | 25099 | 25720 | 20093 | 22425 | 21164 | 22719 | 27453 | 24240 | 21311
5294 | 5294 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 14 | 21529 | 19944 | 17630 | 19716 | 18567 | 23462 | 24228 | 21647 | 18944 | 19877 | 21239 | 25389 | 25964 | 20245 | 22591 | 21377 | 22965 | 27829 | 24340 | 21463
5295 | 5295 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 15 | 21772 | 20113 | 17822 | 19831 | 18759 | 23677 | 24401 | 21818 | 19119 | 20064 | 21427 | 25585 | 26104 | 20416 | 22689 | 21555 | 23167 | 28054 | 24502 | 21630
5296 | 5296 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 16 | 22134 | 20344 | 18232 | 20142 | 19301 | 23971 | 24598 | 22024 | 19501 | 20711 | 21666 | 25775 | 26216 | 20781 | 22913 | 22225 | 23316 | 28342 | 24640 | 21990
5297 | 5297 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 17 | 22402 | 20547 | 18738 | 20499 | 19786 | 24260 | 24901 | 22293 | 19984 | 21178 | 21980 | 26065 | 26579 | 21365 | 23282 | 22725 | 23637 | 28690 | 24968 | 22612
5298 | 5298 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 18 | 22289 | 20485 | 18848 | 20526 | 19688 | 24370 | 24897 | 22413 | 20337 | 21199 | 22046 | 26467 | 26887 | 21837 | 23684 | 22891 | 23914 | 28927 | 25497 | 23128
5299 | 5299 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 19 | 21866 | 20121 | 18325 | 20559 | 19565 | 23982 | 24595 | 22211 | 19999 | 21252 | 22173 | 26403 | 26895 | 21749 | 24073 | 23192 | 24314 | 28783 | 25746 | 23119
5300 | 5300 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 20 | 21228 | 19620 | 17899 | 20272 | 19309 | 23533 | 23998 | 21863 | 19693 | 21142 | 22373 | 26318 | 26758 | 21727 | 24220 | 23527 | 24811 | 28570 | 25884 | 23175
5301 | 5301 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 21 | 21042 | 19415 | 17934 | 19922 | 19230 | 23511 | 23998 | 21878 | 19967 | 21340 | 22744 | 26753 | 27264 | 22323 | 24419 | 24143 | 25595 | 29193 | 26584 | 23947
5302 | 5302 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 22 | 19767 | 18591 | 17136 | 18946 | 18207 | 22300 | 22931 | 21194 | 19286 | 20492 | 21951 | 25766 | 26436 | 21799 | 23714 | 23495 | 25006 | 28405 | 26219 | 23494
5303 | 5303 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 23 | 18227 | 17535 | 16121 | 17625 | 16988 | 20766 | 21427 | 20145 | 18270 | 19333 | 20677 | 24269 | 24980 | 20815 | 22421 | 22406 | 23795 | 27005 | 25287 | 22538
5304 | 5304 | 221 | 8 | 9 | Summer | 8 | 8 | Summer | 24 | 16915 | 16533 | 15143 | 16489 | 15974 | 19370 | 20086 | 19094 | 17265 | 18334 | 19546 | 22876 | 23694 | 19799 | 21238 | 21421 | 22700 | 25639 | 24276 | 21529
5305 | 5305 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 1 | 16185 | 14859 | 14472 | 14414 | 14906 | 18550 | 18534 | 17041 | 16472 | 17329 | 18727 | 21968 | 21829 | 18931 | 19576 | 20534 | 21903 | 23884 | 21432 | 20632
5306 | 5306 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 2 | 15558 | 14308 | 14132 | 14051 | 14544 | 17798 | 17807 | 16412 | 16053 | 16881 | 18163 | 21088 | 20951 | 18418 | 19008 | 19955 | 21227 | 22925 | 20637 | 20055
5307 | 5307 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 3 | 15152 | 13916 | 13974 | 13815 | 14308 | 17286 | 17312 | 15950 | 15823 | 16541 | 17727 | 20413 | 20307 | 18074 | 18552 | 19473 | 20656 | 22192 | 19992 | 19648
5308 | 5308 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 4 | 14983 | 13664 | 13967 | 13801 | 14270 | 17025 | 16895 | 15563 | 15648 | 16286 | 17335 | 19799 | 19548 | 17671 | 18062 | 18921 | 19966 | 21245 | 19188 | 19107
5309 | 5309 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 5 | 15201 | 13517 | 14313 | 14084 | 14642 | 17131 | 16687 | 15307 | 15813 | 16366 | 17290 | 19500 | 18955 | 17626 | 17789 | 18693 | 19584 | 20440 | 18454 | 18921
5310 | 5310 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 6 | 15853 | 13300 | 15045 | 14793 | 15388 | 17643 | 16586 | 14959 | 16326 | 16841 | 17584 | 19600 | 18401 | 17904 | 17910 | 18899 | 19647 | 19679 | 17624 | 19074
5311 | 5311 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 7 | 17071 | 13481 | 16151 | 15805 | 16348 | 18684 | 16862 | 14967 | 17273 | 17660 | 18219 | 20346 | 18257 | 18607 | 18392 | 19449 | 20121 | 19403 | 17290 | 19728
5312 | 5312 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 8 | 18480 | 14494 | 17342 | 16679 | 17263 | 20165 | 17936 | 15910 | 18487 | 18518 | 19152 | 21714 | 19206 | 19696 | 19031 | 20187 | 20971 | 20295 | 18075 | 20808
5313 | 5313 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 9 | 19808 | 15765 | 18411 | 17431 | 18067 | 21510 | 19343 | 17214 | 19518 | 19309 | 20118 | 23021 | 20564 | 20704 | 19648 | 20854 | 21855 | 21640 | 19337 | 21818
5314 | 5314 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 10 | 20603 | 16350 | 18788 | 17732 | 18441 | 22318 | 20225 | 17913 | 19995 | 19783 | 20786 | 23933 | 21558 | 21254 | 20144 | 21336 | 22551 | 22694 | 20183 | 22430
5315 | 5315 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 11 | 21289 | 16761 | 19183 | 18002 | 18772 | 23033 | 20799 | 18402 | 20460 | 20220 | 21392 | 24748 | 22243 | 21790 | 20615 | 21864 | 23243 | 23462 | 20797 | 23015
5316 | 5316 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 12 | 21773 | 17037 | 19410 | 18129 | 19087 | 23491 | 21214 | 18713 | 20726 | 20616 | 21851 | 25270 | 22725 | 22092 | 20833 | 22312 | 23748 | 23949 | 21181 | 23344
5317 | 5317 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 13 | 21855 | 16862 | 19330 | 18092 | 19101 | 23510 | 21200 | 18556 | 20675 | 20648 | 22078 | 25321 | 22744 | 22057 | 20822 | 22369 | 24021 | 23966 | 21038 | 23325
5318 | 5318 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 14 | 22128 | 16946 | 19429 | 18275 | 19277 | 23722 | 21257 | 18656 | 20786 | 20828 | 22213 | 25511 | 22798 | 22165 | 20978 | 22552 | 24118 | 24004 | 21129 | 23436
5319 | 5319 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 15 | 22322 | 17086 | 19503 | 18426 | 19433 | 23856 | 21382 | 18794 | 20857 | 20974 | 22405 | 25617 | 22927 | 22223 | 21109 | 22714 | 24313 | 24118 | 21249 | 23495
5320 | 5320 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 16 | 22769 | 17637 | 19963 | 19110 | 19921 | 24217 | 21747 | 19343 | 21286 | 21382 | 22660 | 25904 | 23253 | 22602 | 21942 | 23033 | 24480 | 24410 | 21757 | 23864
5321 | 5321 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 17 | 23076 | 18191 | 20367 | 19637 | 20236 | 24564 | 22057 | 19865 | 21709 | 21736 | 22955 | 26305 | 23619 | 23015 | 22487 | 23395 | 24860 | 24783 | 22423 | 24288
5322 | 5322 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 18 | 22750 | 18202 | 20278 | 19477 | 20177 | 24489 | 22086 | 20102 | 21862 | 21724 | 23325 | 26508 | 23997 | 23364 | 22590 | 23604 | 25351 | 25257 | 22892 | 24695
5323 | 5323 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 19 | 22201 | 17672 | 20266 | 19319 | 20027 | 24140 | 21837 | 19712 | 21913 | 21767 | 23322 | 26443 | 24063 | 23703 | 22836 | 23965 | 25597 | 25491 | 22878 | 25119
5324 | 5324 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 20 | 21425 | 17222 | 19954 | 19034 | 19922 | 23520 | 21461 | 19356 | 21754 | 21879 | 23479 | 26241 | 24029 | 23813 | 23149 | 24427 | 26089 | 25639 | 22945 | 25279
5325 | 5325 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 21 | 21149 | 17259 | 19592 | 18896 | 19884 | 23466 | 21413 | 19553 | 21595 | 22161 | 23887 | 26636 | 24427 | 23972 | 23694 | 25146 | 26917 | 26318 | 23695 | 25602
5326 | 5326 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 22 | 19950 | 16470 | 18623 | 17873 | 18852 | 22379 | 20704 | 18859 | 20727 | 21343 | 23028 | 25781 | 23933 | 23262 | 23035 | 24556 | 26228 | 25960 | 23264 | 24959
5327 | 5327 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 23 | 18495 | 15488 | 17323 | 16677 | 17505 | 20889 | 19665 | 17847 | 19440 | 20082 | 21687 | 24337 | 22958 | 21981 | 21964 | 23367 | 24976 | 25063 | 22326 | 23710
5328 | 5328 | 222 | 8 | 10 | Summer | 8 | 9 | Summer | 24 | 17175 | 14547 | 16170 | 15672 | 16376 | 19548 | 18603 | 16824 | 18258 | 18936 | 20479 | 23035 | 21942 | 20798 | 20969 | 22273 | 23756 | 24046 | 21318 | 22530
5329 | 5329 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 1 | 15982 | 14047 | 14216 | 14745 | 15681 | 18151 | 16755 | 16172 | 16470 | 18214 | 18912 | 21319 | 19546 | 19208 | 20211 | 21596 | 22018 | 21329 | 20557 | 21060
5330 | 5330 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 2 | 15348 | 13699 | 13860 | 14371 | 15207 | 17425 | 16123 | 15748 | 15993 | 17654 | 18197 | 20447 | 18795 | 18638 | 19627 | 20914 | 21184 | 20522 | 19968 | 20426
5331 | 5331 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 3 | 14914 | 13541 | 13640 | 14142 | 14916 | 16945 | 15678 | 15532 | 15682 | 17249 | 17754 | 19822 | 18229 | 18201 | 19164 | 20354 | 20615 | 19884 | 19567 | 19923
5332 | 5332 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 4 | 14643 | 13544 | 13643 | 14132 | 14814 | 16573 | 15334 | 15405 | 15499 | 16923 | 17276 | 19130 | 17605 | 17754 | 18650 | 19692 | 19835 | 19100 | 19038 | 19322
5333 | 5333 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 5 | 14569 | 13880 | 13925 | 14521 | 15065 | 16401 | 15112 | 15610 | 15562 | 16942 | 17127 | 18594 | 17049 | 17516 | 18452 | 19333 | 19409 | 18372 | 18848 | 18909
5334 | 5334 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 6 | 14584 | 14629 | 14633 | 15292 | 15683 | 16340 | 14816 | 16184 | 16021 | 17321 | 17268 | 18114 | 16394 | 17678 | 18683 | 19424 | 19339 | 17552 | 19001 | 18895
5335 | 5335 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 7 | 14974 | 15780 | 15699 | 16313 | 16640 | 16666 | 14889 | 17228 | 16795 | 18048 | 17841 | 18070 | 16184 | 18201 | 19286 | 19955 | 19677 | 17238 | 19656 | 19327
5336 | 5336 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 8 | 15811 | 16698 | 16352 | 16985 | 17431 | 17478 | 15585 | 18214 | 17369 | 18760 | 18560 | 18800 | 16766 | 18610 | 19792 | 20561 | 20271 | 17778 | 20481 | 19681
5337 | 5337 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 9 | 16753 | 17302 | 16673 | 17330 | 17928 | 18419 | 16435 | 18812 | 17669 | 19285 | 19161 | 19719 | 17572 | 18778 | 20010 | 20982 | 20771 | 18576 | 21038 | 19825
5338 | 5338 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 10 | 17653 | 17783 | 17068 | 17780 | 18577 | 19363 | 17207 | 19365 | 18152 | 20027 | 19765 | 20785 | 18431 | 19354 | 20574 | 21750 | 21380 | 19503 | 21726 | 20458
5339 | 5339 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 11 | 18140 | 18160 | 17339 | 18109 | 19078 | 19927 | 17684 | 19827 | 18524 | 20616 | 20308 | 21463 | 18993 | 19814 | 21094 | 22440 | 22005 | 20113 | 22303 | 20975
5340 | 5340 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 12 | 18612 | 18452 | 17539 | 18488 | 19533 | 20412 | 18059 | 20158 | 18757 | 21135 | 20697 | 21997 | 19415 | 20097 | 21609 | 23013 | 22419 | 20564 | 22702 | 21284
5341 | 5341 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 13 | 18941 | 18702 | 17847 | 18839 | 20049 | 20744 | 18246 | 20442 | 19081 | 21708 | 21008 | 22355 | 19618 | 20434 | 22012 | 23618 | 22743 | 20767 | 23027 | 21626
5342 | 5342 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 14 | 18986 | 18802 | 18027 | 19005 | 20204 | 20798 | 18342 | 20543 | 19249 | 21850 | 21138 | 22404 | 19703 | 20592 | 22193 | 23711 | 22848 | 20854 | 23134 | 21773
5343 | 5343 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 15 | 19180 | 18915 | 18245 | 19224 | 20487 | 20990 | 18551 | 20675 | 19461 | 22116 | 21255 | 22585 | 19901 | 20796 | 22425 | 23970 | 22955 | 21042 | 23261 | 21971
5344 | 5344 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 16 | 19438 | 19240 | 18733 | 19578 | 20707 | 21238 | 18970 | 20970 | 20127 | 22251 | 21393 | 22790 | 20289 | 21506 | 22624 | 24010 | 23011 | 21416 | 23496 | 22669
5345 | 5345 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 17 | 19677 | 19644 | 19262 | 19900 | 20997 | 21551 | 19489 | 21385 | 20624 | 22545 | 21780 | 23157 | 20904 | 22061 | 23005 | 24392 | 23339 | 22073 | 23930 | 23232
5346 | 5346 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 18 | 19744 | 19711 | 19285 | 20033 | 21310 | 21746 | 19880 | 21680 | 20761 | 23064 | 22191 | 23682 | 21501 | 22336 | 23381 | 25064 | 23914 | 22737 | 24522 | 23576
5347 | 5347 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 19 | 19424 | 19756 | 19171 | 19931 | 21085 | 21545 | 19532 | 21764 | 20826 | 23058 | 22010 | 23772 | 21442 | 22616 | 23766 | 25360 | 24072 | 22794 | 25017 | 23977
5348 | 5348 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 20 | 18903 | 19425 | 18838 | 19777 | 20940 | 21144 | 19140 | 21546 | 20649 | 23108 | 21933 | 23659 | 21371 | 22860 | 24172 | 25806 | 24333 | 22858 | 25181 | 24363
5349 | 5349 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 21 | 18665 | 19044 | 18667 | 19704 | 20962 | 21031 | 19283 | 21328 | 20755 | 23421 | 22368 | 23974 | 21901 | 23342 | 24835 | 26588 | 25178 | 23593 | 25481 | 25057
5350 | 5350 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 22 | 17853 | 18065 | 17626 | 18666 | 19876 | 20294 | 18559 | 20444 | 19890 | 22510 | 21603 | 23444 | 21367 | 22648 | 24216 | 25897 | 24624 | 23155 | 24848 | 24465
5351 | 5351 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 23 | 16820 | 16767 | 16417 | 17320 | 18475 | 19224 | 17519 | 19137 | 18735 | 21152 | 20384 | 22437 | 20384 | 21549 | 23000 | 24627 | 23472 | 22194 | 23576 | 23423
5352 | 5352 | 223 | 8 | 11 | Summer | 8 | 10 | Summer | 24 | 15849 | 15671 | 15429 | 16208 | 17278 | 18188 | 16508 | 17953 | 17741 | 19932 | 19236 | 21418 | 19368 | 20565 | 21899 | 23415 | 22361 | 21192 | 22405 | 22442
5353 | 5353 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 1 | 14188 | 13571 | 14345 | 15328 | 15767 | 16262 | 15705 | 15949 | 16674 | 18218 | 18448 | 18951 | 18486 | 19607 | 21047 | 21528 | 21340 | 20257 | 20798 | 21557
5354 | 5354 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 2 | 13637 | 13218 | 14001 | 14875 | 15163 | 15648 | 15300 | 15498 | 16238 | 17531 | 17821 | 18231 | 17969 | 19048 | 20385 | 20719 | 20614 | 19679 | 20172 | 20934
5355 | 5355 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 3 | 13227 | 12998 | 13746 | 14557 | 14817 | 15180 | 15066 | 15173 | 15893 | 17080 | 17333 | 17647 | 17610 | 18567 | 19804 | 20126 | 20007 | 19250 | 19643 | 20380
5356 | 5356 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 4 | 13006 | 13029 | 13777 | 14500 | 14660 | 14893 | 15002 | 15058 | 15723 | 16693 | 16844 | 17094 | 17273 | 18122 | 19218 | 19402 | 19238 | 18761 | 19073 | 19774
5357 | 5357 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 5 | 12848 | 13338 | 14190 | 14788 | 14861 | 14718 | 15261 | 15186 | 15866 | 16631 | 16392 | 16598 | 17267 | 17985 | 18911 | 19012 | 18514 | 18597 | 18663 | 19450
5358 | 5358 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 6 | 12637 | 14068 | 14980 | 15460 | 15372 | 14470 | 15905 | 15721 | 16414 | 16873 | 15978 | 16024 | 17595 | 18298 | 19062 | 19001 | 17883 | 18778 | 18684 | 19578
5359 | 5359 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 7 | 12857 | 15183 | 16027 | 16480 | 16221 | 14584 | 17012 | 16590 | 17326 | 17534 | 15974 | 15896 | 18369 | 18951 | 19641 | 19389 | 17694 | 19466 | 19134 | 20113
5360 | 5360 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 8 | 13734 | 15972 | 16802 | 17371 | 17137 | 15374 | 18108 | 17314 | 18050 | 18393 | 16840 | 16597 | 19319 | 19582 | 20365 | 20089 | 18443 | 20392 | 19600 | 20667
5361 | 5361 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 9 | 14700 | 16484 | 17336 | 18042 | 17955 | 16392 | 18890 | 17824 | 18575 | 19190 | 17792 | 17587 | 20058 | 19987 | 20966 | 20764 | 19178 | 21125 | 19927 | 21055
5362 | 5362 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 10 | 15219 | 16729 | 17638 | 18553 | 18318 | 17007 | 19286 | 18175 | 18971 | 19639 | 18564 | 18305 | 20541 | 20396 | 21591 | 21242 | 19947 | 21668 | 20425 | 21528
5363 | 5363 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 11 | 15634 | 16978 | 17967 | 19040 | 18770 | 17468 | 19736 | 18529 | 19402 | 20166 | 19218 | 18856 | 21077 | 20912 | 22271 | 21860 | 20677 | 22241 | 20930 | 22106
5364 | 5364 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 12 | 16039 | 17218 | 18395 | 19538 | 19162 | 17880 | 20103 | 18806 | 19911 | 20586 | 19697 | 19321 | 21507 | 21458 | 22878 | 22302 | 21181 | 22678 | 21280 | 22692
5365 | 5365 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 13 | 16180 | 17485 | 18729 | 20037 | 19420 | 18050 | 20369 | 19108 | 20267 | 20886 | 19926 | 19508 | 21800 | 21846 | 23465 | 22610 | 21411 | 22986 | 21605 | 23098
5366 | 5366 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 14 | 16335 | 17720 | 18961 | 20272 | 19645 | 18214 | 20535 | 19355 | 20526 | 21094 | 20112 | 19674 | 21992 | 22099 | 23634 | 22793 | 21574 | 23160 | 21821 | 23358
5367 | 5367 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 15 | 16517 | 17932 | 19161 | 20544 | 19767 | 18407 | 20652 | 19554 | 20707 | 21201 | 20264 | 19858 | 22094 | 22312 | 23880 | 22887 | 21717 | 23268 | 22005 | 23573
5368 | 5368 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 16 | 16910 | 18358 | 19509 | 20754 | 19954 | 18814 | 20936 | 20146 | 20982 | 21340 | 20492 | 20239 | 22325 | 22515 | 23916 | 22940 | 21890 | 23484 | 22677 | 23724
5369 | 5369 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 17 | 17440 | 18838 | 19782 | 21012 | 20268 | 19282 | 21302 | 20615 | 21301 | 21673 | 20988 | 20829 | 22704 | 22839 | 24239 | 23247 | 22426 | 23869 | 23193 | 24056
5370 | 5370 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 18 | 17483 | 18709 | 19765 | 21129 | 20310 | 19515 | 21414 | 20594 | 21306 | 21903 | 21332 | 21225 | 23081 | 23054 | 24759 | 23665 | 22920 | 24317 | 23397 | 24367
5371 | 5371 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 19 | 16942 | 18485 | 19562 | 20799 | 19844 | 19074 | 21387 | 20521 | 21280 | 21572 | 21285 | 21030 | 23378 | 23315 | 24944 | 23705 | 23077 | 24737 | 23716 | 24777
5372 | 5372 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 20 | 16482 | 18149 | 19408 | 20640 | 19433 | 18701 | 21177 | 20298 | 21330 | 21423 | 21237 | 20925 | 23444 | 23690 | 25372 | 23953 | 23412 | 24939 | 24113 | 25301
5373 | 5373 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 21 | 16481 | 17960 | 19288 | 20607 | 19465 | 18788 | 20895 | 20320 | 21497 | 21746 | 21681 | 21366 | 23517 | 24270 | 26081 | 24733 | 24251 | 25218 | 24791 | 26101
5374 | 5374 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 22 | 15702 | 16921 | 18238 | 19492 | 18481 | 18048 | 19995 | 19419 | 20640 | 20940 | 21185 | 20795 | 22795 | 23622 | 25367 | 24157 | 23977 | 24579 | 24205 | 25568
5375 | 5375 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 23 | 14703 | 15715 | 16879 | 18096 | 17171 | 16995 | 18662 | 18218 | 19344 | 19703 | 20311 | 19785 | 21471 | 22371 | 24082 | 22987 | 23178 | 23279 | 23149 | 24371
5376 | 5376 | 224 | 8 | 12 | Summer | 8 | 11 | Summer | 24 | 13819 | 14727 | 15752 | 16898 | 16010 | 15979 | 17461 | 17201 | 18207 | 18530 | 19465 | 18761 | 20292 | 21259 | 22850 | 21871 | 22381 | 22113 | 22158 | 23278
5377 | 5377 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 1 | 13380 | 13852 | 15138 | 15614 | 15619 | 15411 | 15639 | 16322 | 17513 | 18005 | 17879 | 18094 | 18699 | 20615 | 21186 | 21094 | 20383 | 20688 | 21459 | 22680
5378 | 5378 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 2 | 13060 | 13514 | 14704 | 15020 | 15110 | 15017 | 15201 | 15903 | 16984 | 17395 | 17226 | 17595 | 18152 | 19968 | 20389 | 20376 | 19634 | 20066 | 20839 | 21964
5379 | 5379 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 3 | 12879 | 13274 | 14397 | 14678 | 14751 | 14791 | 14890 | 15572 | 16580 | 16933 | 16744 | 17250 | 17710 | 19409 | 19808 | 19779 | 19059 | 19539 | 20286 | 21321
5380 | 5380 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 4 | 12898 | 13296 | 14350 | 14536 | 14528 | 14748 | 14808 | 15445 | 16328 | 16488 | 16293 | 16950 | 17313 | 18857 | 19100 | 19018 | 18387 | 18967 | 19679 | 20606
5381 | 5381 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 5 | 13231 | 13738 | 14679 | 14789 | 14400 | 15059 | 15006 | 15671 | 16427 | 16116 | 15904 | 17015 | 17134 | 18623 | 18781 | 18334 | 17759 | 18604 | 19384 | 20185
5382 | 5382 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 6 | 14004 | 14538 | 15384 | 15343 | 14377 | 15734 | 15593 | 16287 | 16905 | 15770 | 15463 | 17409 | 17370 | 18823 | 18818 | 17738 | 17149 | 18639 | 19505 | 20216
5383 | 5383 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 7 | 15221 | 15631 | 16479 | 16260 | 14745 | 16892 | 16550 | 17284 | 17742 | 15866 | 15337 | 18267 | 18005 | 19466 | 19263 | 17604 | 16842 | 19127 | 20076 | 20769
5384 | 5384 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 8 | 16340 | 16534 | 17491 | 17300 | 15776 | 18088 | 17413 | 18162 | 18679 | 16894 | 16057 | 19359 | 18658 | 20314 | 20095 | 18485 | 17489 | 19707 | 20757 | 21595
5385 | 5385 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 9 | 17205 | 17162 | 18287 | 18211 | 16864 | 18950 | 18032 | 18790 | 19482 | 17963 | 16870 | 20200 | 19133 | 21015 | 20872 | 19340 | 18182 | 20132 | 21241 | 22312
5386 | 5386 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 10 | 17663 | 17562 | 18889 | 18666 | 17648 | 19425 | 18464 | 19278 | 20182 | 18830 | 17568 | 20776 | 19684 | 21718 | 21433 | 20212 | 18882 | 20719 | 21805 | 23082
5387 | 5387 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 11 | 18069 | 17941 | 19403 | 19131 | 18240 | 19894 | 18836 | 19725 | 20790 | 19491 | 18140 | 21331 | 20164 | 22420 | 22076 | 20958 | 19514 | 21252 | 22411 | 23841
5388 | 5388 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 12 | 18348 | 18309 | 19858 | 19465 | 18632 | 20218 | 19069 | 20173 | 21288 | 19926 | 18547 | 21701 | 20440 | 22982 | 22479 | 21406 | 19912 | 21562 | 22956 | 24456
5389 | 5389 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 13 | 18548 | 18608 | 20332 | 19704 | 18822 | 20457 | 19351 | 20509 | 21815 | 20132 | 18754 | 21970 | 20736 | 23540 | 22761 | 21612 | 20134 | 21860 | 23334 | 25052
5390 | 5390 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 14 | 18590 | 18735 | 20472 | 19810 | 18913 | 20527 | 19504 | 20657 | 21917 | 20228 | 18775 | 22048 | 20850 | 23614 | 22847 | 21665 | 20111 | 21975 | 23489 | 25106
5391 | 5391 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 15 | 18584 | 18822 | 20644 | 19839 | 18990 | 20542 | 19598 | 20742 | 22075 | 20287 | 18860 | 22063 | 20946 | 23764 | 22844 | 21725 | 20206 | 22058 | 23599 | 25239
5392 | 5392 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 16 | 18904 | 19168 | 20852 | 20046 | 19287 | 20830 | 20160 | 21036 | 22230 | 20525 | 19134 | 22306 | 21641 | 23806 | 22902 | 21892 | 20455 | 22722 | 23746 | 25225
5393 | 5393 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 17 | 19173 | 19335 | 20983 | 20241 | 19669 | 21089 | 20524 | 21243 | 22368 | 20913 | 19618 | 22563 | 22044 | 24024 | 23102 | 22312 | 20973 | 23133 | 23976 | 25480
5394 | 5394 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 18 | 19022 | 19233 | 20978 | 20190 | 19684 | 21122 | 20431 | 21174 | 22652 | 21167 | 20069 | 22840 | 22111 | 24470 | 23450 | 22745 | 21626 | 23279 | 24224 | 26004
5395 | 5395 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 19 | 19009 | 19056 | 20647 | 19734 | 19418 | 21117 | 20348 | 21127 | 22536 | 21078 | 20111 | 23121 | 22291 | 24645 | 23484 | 22906 | 21883 | 23621 | 24658 | 26289
5396 | 5396 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 20 | 18692 | 18856 | 20448 | 19297 | 19119 | 20898 | 20082 | 21118 | 22528 | 20923 | 20213 | 23150 | 22477 | 25018 | 23685 | 23209 | 22205 | 24013 | 25178 | 26794
5397 | 5397 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 21 | 18292 | 18726 | 20403 | 19306 | 19192 | 20597 | 20059 | 21229 | 22753 | 21295 | 20611 | 23180 | 22888 | 25680 | 24428 | 24035 | 22926 | 24691 | 25983 | 27672
5398 | 5398 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 22 | 17311 | 17656 | 19266 | 18284 | 18457 | 19669 | 19110 | 20315 | 21799 | 20756 | 20008 | 22404 | 22166 | 24928 | 23818 | 23730 | 22482 | 24093 | 25441 | 27029
5399 | 5399 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 23 | 16028 | 16333 | 17878 | 17018 | 17521 | 18346 | 17914 | 19014 | 20436 | 19889 | 19049 | 21092 | 21045 | 23621 | 22674 | 22944 | 21568 | 23045 | 24256 | 25757
5400 | 5400 | 225 | 8 | 13 | Summer | 8 | 12 | Summer | 24 | 14970 | 15244 | 16675 | 15866 | 16615 | 17167 | 16900 | 17863 | 19213 | 19019 | 18183 | 19897 | 20054 | 22425 | 21539 | 22138 | 20734 | 22057 | 23176 | 24541
5401 | 5401 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 1 | 13057 | 14605 | 15402 | 15479 | 15444 | 15265 | 15961 | 17114 | 17738 | 17466 | 17492 | 18244 | 19246 | 20743 | 20748 | 20148 | 19955 | 21325 | 22525 | 22721
5402 | 5402 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 2 | 12712 | 14158 | 14815 | 14961 | 14866 | 14828 | 15541 | 16589 | 17062 | 16818 | 16994 | 17699 | 18690 | 19950 | 20031 | 19392 | 19377 | 20696 | 21804 | 21859
5403 | 5403 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 3 | 12540 | 13897 | 14523 | 14641 | 14513 | 14569 | 15270 | 16234 | 16667 | 16395 | 16648 | 17308 | 18263 | 19426 | 19481 | 18855 | 18930 | 20189 | 21202 | 21260
5404 | 5404 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 4 | 12558 | 13864 | 14395 | 14433 | 14275 | 14514 | 15178 | 16032 | 16329 | 15981 | 16404 | 16962 | 17849 | 18771 | 18751 | 18202 | 18477 | 19589 | 20491 | 20433
5405 | 5405 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 5 | 12860 | 14177 | 14641 | 14321 | 14161 | 14725 | 15426 | 16188 | 16334 | 15613 | 16504 | 16833 | 17760 | 18460 | 18077 | 17587 | 18306 | 19283 | 20051 | 19943
5406 | 5406 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 6 | 13567 | 14881 | 15210 | 14301 | 14001 | 15336 | 16079 | 16721 | 16637 | 15213 | 16975 | 17103 | 18115 | 18529 | 17503 | 16973 | 18534 | 19417 | 20071 | 19835
5407 | 5407 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 7 | 14703 | 16001 | 16147 | 14666 | 14057 | 16302 | 17090 | 17601 | 17367 | 15119 | 17789 | 17756 | 18825 | 18989 | 17376 | 16644 | 19199 | 19958 | 20598 | 20195
5408 | 5408 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 8 | 15466 | 16823 | 17039 | 15550 | 14684 | 17010 | 17822 | 18405 | 18222 | 15712 | 18619 | 18294 | 19447 | 19673 | 18109 | 17149 | 19963 | 20485 | 21250 | 20839
5409 | 5409 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 9 | 15861 | 17368 | 17768 | 16429 | 15344 | 17420 | 18251 | 19012 | 18900 | 16340 | 19222 | 18575 | 19752 | 20243 | 18766 | 17634 | 20515 | 20762 | 21754 | 21420
5410 | 5410 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 10 | 16082 | 17856 | 18118 | 17083 | 15849 | 17727 | 18623 | 19573 | 19319 | 16928 | 19794 | 18989 | 20151 | 20686 | 19526 | 18203 | 21148 | 21221 | 22404 | 21918
5411 | 5411 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 11 | 16311 | 18323 | 18548 | 17632 | 16303 | 18045 | 19012 | 20138 | 19825 | 17459 | 20310 | 19420 | 20645 | 21287 | 20233 | 18794 | 21718 | 21781 | 23135 | 22568
5412 | 5412 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 12 | 16476 | 18746 | 18857 | 18008 | 16644 | 18250 | 19431 | 20613 | 20164 | 17840 | 20670 | 19677 | 21115 | 21667 | 20658 | 19174 | 22096 | 22300 | 23718 | 22979
5413 | 5413 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 13 | 16695 | 19201 | 19079 | 18192 | 16823 | 18523 | 19753 | 21132 | 20429 | 18040 | 20989 | 19965 | 21463 | 21942 | 20858 | 19382 | 22415 | 22666 | 24306 | 23274
5414 | 5414 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 14 | 16873 | 19419 | 19250 | 18361 | 16915 | 18734 | 19955 | 21321 | 20598 | 18119 | 21206 | 20159 | 21667 | 22085 | 20974 | 19437 | 22609 | 22875 | 24419 | 23416
5415 | 5415 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 15 | 17072 | 19658 | 19355 | 18512 | 17095 | 18907 | 20122 | 21551 | 20690 | 18281 | 21422 | 20329 | 21866 | 22167 | 21111 | 19604 | 22816 | 23062 | 24625 | 23478
5416 | 5416 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 16 | 17477 | 19884 | 19571 | 18808 | 17417 | 19467 | 20425 | 21714 | 20840 | 18571 | 21706 | 20995 | 22071 | 22239 | 21296 | 19847 | 23052 | 23211 | 24623 | 23516
5417 | 5417 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 17 | 17985 | 20139 | 19878 | 19300 | 17960 | 19960 | 20758 | 21962 | 21181 | 19185 | 22151 | 21520 | 22414 | 22562 | 21844 | 20493 | 23566 | 23570 | 25001 | 23859
5418 | 5418 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 18 | 18033 | 20293 | 19977 | 19500 | 18481 | 20088 | 20897 | 22400 | 21551 | 19813 | 22644 | 21788 | 22780 | 23119 | 22487 | 21360 | 24161 | 24037 | 25741 | 24469
5419 | 5419 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 19 | 17897 | 20076 | 19580 | 19300 | 18404 | 20071 | 20903 | 22328 | 21273 | 19885 | 22507 | 21996 | 23104 | 23199 | 22698 | 21680 | 24238 | 24554 | 26116 | 24674
5420 | 5420 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 20 | 17531 | 19835 | 19094 | 18963 | 18270 | 19765 | 20835 | 22252 | 21052 | 19893 | 22530 | 22119 | 23417 | 23336 | 22941 | 21975 | 24547 | 25052 | 26617 | 24940
5421 | 5421 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 21 | 17362 | 19763 | 19076 | 19008 | 18360 | 19693 | 20891 | 22396 | 21320 | 20217 | 22701 | 22455 | 23954 | 24012 | 23713 | 22670 | 25048 | 25843 | 27475 | 25827
5422 | 5422 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 22 | 16328 | 18639 | 18045 | 18259 | 17594 | 18720 | 19960 | 21395 | 20475 | 19583 | 21712 | 21701 | 23270 | 23374 | 23383 | 22209 | 24215 | 25297 | 26834 | 25301
5423 | 5423 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 23 | 15146 | 17245 | 16768 | 17322 | 16555 | 17507 | 18625 | 19997 | 19224 | 18615 | 20349 | 20549 | 22015 | 22205 | 22580 | 21305 | 22913 | 24099 | 25562 | 24190
5424 | 5424 | 226 | 8 | 14 | Summer | 8 | 13 | Summer | 24 | 14192 | 16080 | 15612 | 16429 | 15691 | 16500 | 17470 | 18774 | 18065 | 17746 | 19156 | 19546 | 20902 | 21072 | 21786 | 20472 | 21715 | 23011 | 24356 | 23068
5425 | 5425 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 1 | 13283 | 14838 | 15210 | 15267 | 15055 | 15495 | 16638 | 17263 | 17492 | 17003 | 18552 | 18663 | 20138 | 20260 | 19797 | 19623 | 21358 | 22289 | 22530 | 22142
5426 | 5426 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 2 | 12944 | 14282 | 14713 | 14694 | 14642 | 15092 | 16134 | 16606 | 16893 | 16528 | 17974 | 18133 | 19501 | 19563 | 19052 | 19059 | 20688 | 21579 | 21677 | 21381
5427 | 5427 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 3 | 12744 | 13966 | 14402 | 14355 | 14374 | 14835 | 15799 | 16238 | 16481 | 16199 | 17556 | 17741 | 18991 | 19036 | 18531 | 18610 | 20147 | 20984 | 21081 | 20785
5428 | 5428 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 4 | 12749 | 13857 | 14202 | 14120 | 14342 | 14774 | 15634 | 15944 | 16080 | 15995 | 17221 | 17372 | 18481 | 18350 | 17896 | 18173 | 19551 | 20281 | 20257 | 19924
5429 | 5429 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 5 | 13172 | 14114 | 14116 | 14028 | 14686 | 15085 | 15865 | 16033 | 15758 | 16175 | 17239 | 17334 | 18294 | 17719 | 17310 | 18018 | 19292 | 19853 | 19775 | 19100
5430 | 5430 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 6 | 13945 | 14754 | 14184 | 13956 | 15404 | 15876 | 16561 | 16520 | 15459 | 16832 | 17692 | 17760 | 18539 | 17196 | 16738 | 18275 | 19366 | 19897 | 19680 | 18414
5431 | 5431 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 7 | 14992 | 15720 | 14601 | 14053 | 16456 | 16951 | 17526 | 17352 | 15573 | 17743 | 18343 | 18516 | 19182 | 17096 | 16425 | 18954 | 19662 | 20421 | 20033 | 18212
5432 | 5432 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 8 | 15684 | 16571 | 15462 | 14631 | 17299 | 17638 | 18299 | 18180 | 16409 | 18559 | 19045 | 19105 | 19827 | 17799 | 16897 | 19663 | 20158 | 21036 | 20634 | 18886
5433 | 5433 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 9 | 16112 | 17273 | 16339 | 15274 | 17934 | 18019 | 18852 | 18813 | 17310 | 19100 | 19465 | 19447 | 20323 | 18483 | 17408 | 20240 | 20569 | 21548 | 21223 | 19546
5434 | 5434 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 10 | 16508 | 17709 | 17066 | 15848 | 18511 | 18426 | 19448 | 19268 | 18152 | 19691 | 20137 | 19942 | 21016 | 19341 | 18087 | 20970 | 21384 | 22303 | 21828 | 20468
5435 | 5435 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 11 | 16823 | 18065 | 17580 | 16262 | 18923 | 18764 | 19966 | 19736 | 18750 | 20172 | 20663 | 20398 | 21659 | 20007 | 18631 | 21518 | 22007 | 22998 | 22445 | 21182
5436 | 5436 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 12 | 17144 | 18349 | 17949 | 16606 | 19262 | 19160 | 20419 | 20064 | 19169 | 20511 | 21066 | 20869 | 22202 | 20435 | 19021 | 21909 | 22481 | 23580 | 22856 | 21623
5437 | 5437 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 13 | 17527 | 18689 | 18234 | 16889 | 19671 | 19578 | 21028 | 20435 | 19469 | 20935 | 21455 | 21323 | 22854 | 20740 | 19331 | 22340 | 22870 | 24260 | 23255 | 21932
5438 | 5438 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 14 | 17710 | 18858 | 18396 | 16978 | 19916 | 19771 | 21209 | 20605 | 19636 | 21156 | 21648 | 21527 | 23002 | 20854 | 19382 | 22534 | 23062 | 24366 | 23389 | 22024
5439 | 5439 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 15 | 17855 | 18958 | 18545 | 17154 | 20118 | 19939 | 21445 | 20700 | 19749 | 21379 | 21800 | 21708 | 23210 | 20981 | 19543 | 22719 | 23163 | 24556 | 23438 | 22143
5440 | 5440 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 16 | 18145 | 19136 | 18789 | 17418 | 20393 | 20195 | 21569 | 20811 | 19937 | 21617 | 22403 | 21875 | 23215 | 21115 | 19723 | 22910 | 23767 | 24503 | 23417 | 22249
5441 | 5441 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 17 | 18458 | 19422 | 19272 | 17964 | 20874 | 20530 | 21800 | 21149 | 20444 | 22048 | 22804 | 22224 | 23557 | 21659 | 20372 | 23432 | 24134 | 24882 | 23761 | 22805
5442 | 5442 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 18 | 18523 | 19424 | 19357 | 18397 | 21097 | 20607 | 22137 | 21404 | 20834 | 22446 | 22971 | 22508 | 24138 | 22239 | 21184 | 23960 | 24408 | 25571 | 24327 | 23448
5443 | 5443 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 19 | 18402 | 18984 | 19096 | 18273 | 20691 | 20555 | 21997 | 21044 | 20753 | 22219 | 22802 | 22762 | 24330 | 22396 | 21459 | 23996 | 24572 | 25918 | 24503 | 23717
5444 | 5444 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 20 | 18156 | 18486 | 18732 | 18098 | 20499 | 20462 | 21886 | 20743 | 20514 | 22176 | 22941 | 23000 | 24638 | 22591 | 21721 | 24282 | 25046 | 26432 | 24781 | 24055
5445 | 5445 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 21 | 18006 | 18447 | 18748 | 18153 | 20353 | 20470 | 21969 | 20919 | 20808 | 22266 | 23173 | 23441 | 25208 | 23295 | 22374 | 24724 | 25658 | 27272 | 25658 | 24982
5446 | 5446 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 22 | 16941 | 17410 | 17985 | 17374 | 19215 | 19499 | 20935 | 20026 | 20230 | 21243 | 22239 | 22703 | 24426 | 22942 | 21901 | 23864 | 24921 | 26623 | 25133 | 24737
5447 | 5447 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 23 | 15624 | 16149 | 17055 | 16353 | 17818 | 18163 | 19530 | 18756 | 19345 | 19875 | 20897 | 21432 | 23095 | 22131 | 20972 | 22555 | 23645 | 25342 | 23994 | 23980
5448 | 5448 | 227 | 8 | 15 | Summer | 8 | 14 | Summer | 24 | 14573 | 15039 | 16166 | 15499 | 16658 | 17015 | 18304 | 17586 | 18486 | 18694 | 19760 | 20316 | 21887 | 21316 | 20133 | 21362 | 22531 | 24137 | 22878 | 23187
5449 | 5449 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 1 | 13913 | 14603 | 14975 | 14775 | 15769 | 16118 | 16741 | 16952 | 16911 | 17964 | 18900 | 19484 | 20137 | 19333 | 19213 | 20912 | 21784 | 22256 | 21902 | 20979
5450 | 5450 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 2 | 13503 | 14140 | 14449 | 14400 | 15298 | 15655 | 16132 | 16400 | 16308 | 17438 | 18269 | 18896 | 19396 | 18631 | 18686 | 20285 | 21070 | 21442 | 21179 | 20228
5451 | 5451 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 3 | 13254 | 13848 | 14120 | 14153 | 14983 | 15343 | 15782 | 16022 | 15906 | 17046 | 17858 | 18425 | 18887 | 18126 | 18263 | 19770 | 20541 | 20852 | 20589 | 19667
5452 | 5452 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 4 | 13240 | 13670 | 13907 | 14149 | 14922 | 15224 | 15553 | 15686 | 15543 | 16777 | 17507 | 17983 | 18298 | 17540 | 17868 | 19223 | 19923 | 20062 | 19761 | 18950
5453 | 5453 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 5 | 13575 | 13609 | 13838 | 14522 | 15248 | 15503 | 15708 | 15445 | 15258 | 16867 | 17424 | 17840 | 18053 | 17004 | 17757 | 18986 | 19502 | 19597 | 18965 | 18264
5454 | 5454 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 6 | 14322 | 13651 | 13757 | 15320 | 15969 | 16204 | 16230 | 15316 | 15014 | 17364 | 17889 | 18154 | 18184 | 16450 | 18023 | 19084 | 19536 | 19509 | 18266 | 17573
5455 | 5455 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 7 | 15465 | 14079 | 13878 | 16427 | 16869 | 17178 | 17111 | 15549 | 14997 | 18072 | 18629 | 18867 | 18677 | 16158 | 18716 | 19409 | 19979 | 19864 | 18056 | 17206
5456 | 5456 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 8 | 16282 | 15007 | 14530 | 17329 | 17769 | 18006 | 18000 | 16478 | 15623 | 18873 | 19392 | 19606 | 19386 | 16703 | 19496 | 19993 | 20606 | 20520 | 18783 | 17732
5457 | 5457 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 9 | 16745 | 15879 | 15172 | 17890 | 18323 | 18535 | 18627 | 17298 | 16177 | 19290 | 19850 | 20097 | 19955 | 17192 | 20055 | 20400 | 21045 | 21075 | 19416 | 18192
5458 | 5458 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 10 | 17182 | 16484 | 15626 | 18300 | 18783 | 19004 | 18943 | 17949 | 16667 | 19827 | 20316 | 20655 | 20359 | 17742 | 20655 | 21092 | 21648 | 21543 | 20208 | 18789
5459 | 5459 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 11 | 17674 | 17070 | 16104 | 18759 | 19271 | 19563 | 19468 | 18592 | 17219 | 20405 | 20803 | 21329 | 20995 | 18344 | 21260 | 21754 | 22218 | 22225 | 20982 | 19434
5460 | 5460 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 12 | 18080 | 17413 | 16434 | 19063 | 19629 | 19996 | 19778 | 18966 | 17574 | 20789 | 21240 | 21840 | 21369 | 18717 | 21634 | 22199 | 22745 | 22619 | 21411 | 19820
5461 | 5461 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 13 | 18568 | 17645 | 16654 | 19409 | 19954 | 20525 | 20076 | 19199 | 17821 | 21111 | 21590 | 22425 | 21697 | 18965 | 22001 | 22528 | 23114 | 22948 | 21657 | 20073
5462 | 5462 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 14 | 18806 | 17807 | 16757 | 19648 | 20178 | 20718 | 20252 | 19362 | 17917 | 21315 | 21764 | 22578 | 21860 | 19033 | 22210 | 22709 | 23286 | 23092 | 21764 | 20126
5463 | 5463 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 15 | 19096 | 18019 | 16998 | 19937 | 20399 | 21019 | 20408 | 19568 | 18148 | 21533 | 21973 | 22863 | 21983 | 19259 | 22459 | 22882 | 23444 | 23201 | 21947 | 20347
5464 | 5464 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 16 | 19389 | 18390 | 17398 | 20352 | 21038 | 21279 | 20663 | 19896 | 18507 | 22264 | 22239 | 23020 | 22147 | 19571 | 22787 | 23621 | 23638 | 23318 | 22188 | 20654
5465 | 5465 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 17 | 19720 | 18930 | 18015 | 20903 | 21514 | 21585 | 21066 | 20473 | 19195 | 22737 | 22672 | 23442 | 22543 | 20297 | 23387 | 24063 | 24089 | 23738 | 22813 | 21384
5466 | 5466 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 18 | 19695 | 18890 | 18276 | 20991 | 21487 | 21798 | 21169 | 20702 | 19634 | 22767 | 22640 | 23873 | 22913 | 20993 | 23801 | 24235 | 24184 | 24197 | 23351 | 22131
5467 | 5467 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 19 | 19349 | 18502 | 18033 | 20480 | 21056 | 21551 | 20682 | 20471 | 19525 | 22451 | 22545 | 23926 | 22821 | 21148 | 23731 | 24288 | 24308 | 24283 | 23530 | 22386
5468 | 5468 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 20 | 19055 | 18062 | 17786 | 20227 | 20800 | 21371 | 20311 | 20124 | 19434 | 22455 | 22695 | 24120 | 22881 | 21319 | 23933 | 24692 | 24890 | 24527 | 23823 | 22665
5469 | 5469 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 21 | 18966 | 18052 | 17813 | 20054 | 20654 | 21411 | 20413 | 20343 | 19689 | 22589 | 22977 | 24600 | 23468 | 21915 | 24317 | 25256 | 25589 | 25372 | 24730 | 23442
5470 | 5470 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 22 | 17851 | 17298 | 17036 | 18908 | 19506 | 20363 | 19491 | 19734 | 19047 | 21636 | 22151 | 23786 | 22808 | 21425 | 23458 | 24505 | 24987 | 24847 | 24496 | 23039
5471 | 5471 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 23 | 16469 | 16383 | 16012 | 17519 | 18089 | 18953 | 18215 | 18823 | 18073 | 20275 | 20856 | 22450 | 21619 | 20484 | 22130 | 23236 | 23794 | 23694 | 23737 | 22147
5472 | 5472 | 228 | 8 | 16 | Summer | 8 | 15 | Summer | 24 | 15342 | 15506 | 15167 | 16377 | 16940 | 17739 | 17035 | 17955 | 17205 | 19137 | 19721 | 21228 | 20488 | 19650 | 20948 | 22133 | 22680 | 22612 | 22959 | 21313
5473 | 5473 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 1 | 14037 | 14322 | 14441 | 15401 | 15911 | 16162 | 16415 | 16412 | 16337 | 18235 | 19265 | 19420 | 19591 | 18693 | 20392 | 21296 | 22277 | 21596 | 20696 | 20322
5474 | 5474 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 2 | 13514 | 13794 | 14064 | 14925 | 15368 | 15552 | 15860 | 15806 | 15888 | 17607 | 18659 | 18684 | 18924 | 18164 | 19758 | 20576 | 21547 | 20857 | 19930 | 19740
5475 | 5475 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 3 | 13189 | 13475 | 13825 | 14617 | 15064 | 15214 | 15495 | 15420 | 15580 | 17218 | 18232 | 18200 | 18401 | 17762 | 19249 | 20054 | 20982 | 20268 | 19369 | 19276
5476 | 5476 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 4 | 13116 | 13273 | 13827 | 14573 | 14985 | 15020 | 15204 | 15095 | 15432 | 16919 | 17875 | 17667 | 17780 | 17395 | 18730 | 19452 | 20351 | 19442 | 18657 | 18783
5477 | 5477 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 5 | 13390 | 13203 | 14200 | 14923 | 15229 | 15207 | 15011 | 14857 | 15665 | 16910 | 17841 | 17506 | 17226 | 17314 | 18527 | 19065 | 19953 | 18662 | 17973 | 18556
5478 | 5478 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 6 | 14044 | 13162 | 15038 | 15689 | 16038 | 15785 | 14966 | 14694 | 16368 | 17470 | 18228 | 17740 | 16772 | 17642 | 18694 | 19157 | 19838 | 18008 | 17316 | 18759
5479 | 5479 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 7 | 15048 | 13312 | 16197 | 16651 | 17098 | 16711 | 15272 | 14760 | 17342 | 18282 | 18923 | 18308 | 16745 | 18379 | 19076 | 19662 | 20204 | 17825 | 16969 | 19438
5480 | 5480 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 8 | 16016 | 14038 | 17181 | 17634 | 18003 | 17676 | 16282 | 15481 | 18300 | 19155 | 19822 | 19115 | 17595 | 19225 | 19741 | 20372 | 21042 | 18614 | 17560 | 20301
5481 | 5481 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 9 | 16838 | 14883 | 17958 | 18370 | 18694 | 18471 | 17296 | 16238 | 19013 | 19810 | 20598 | 19861 | 18449 | 19967 | 20332 | 20992 | 21949 | 19424 | 18208 | 21023
5482 | 5482 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 10 | 17505 | 15694 | 18740 | 19188 | 19460 | 19137 | 18294 | 17089 | 19843 | 20627 | 21361 | 20615 | 19522 | 20924 | 21370 | 21949 | 22866 | 20565 | 19152 | 22028
5483 | 5483 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 11 | 17965 | 16231 | 19238 | 19711 | 19906 | 19699 | 18972 | 17672 | 20425 | 21152 | 22059 | 21278 | 20297 | 21564 | 22082 | 22558 | 23662 | 21385 | 19845 | 22711
5484 | 5484 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 12 | 18211 | 16562 | 19540 | 20054 | 20267 | 20001 | 19338 | 18012 | 20736 | 21577 | 22543 | 21638 | 20697 | 21932 | 22521 | 23066 | 24215 | 21810 | 20229 | 23099
5485 | 5485 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 13 | 18415 | 16686 | 19817 | 20299 | 20528 | 20223 | 19501 | 18176 | 21017 | 21861 | 22948 | 21885 | 20868 | 22228 | 22782 | 23350 | 24630 | 21984 | 20412 | 23399
5486 | 5486 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 14 | 18529 | 16727 | 19994 | 20454 | 20641 | 20338 | 19608 | 18205 | 21181 | 21982 | 23132 | 21985 | 20934 | 22377 | 22903 | 23453 | 24764 | 22029 | 20402 | 23535
5487 | 5487 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 15 | 18728 | 16994 | 20324 | 20712 | 20904 | 20533 | 19850 | 18479 | 21510 | 22231 | 23301 | 22153 | 21168 | 22670 | 23113 | 23655 | 24876 | 22247 | 20654 | 23823
5488 | 5488 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 16 | 18968 | 17316 | 20642 | 21235 | 21147 | 20704 | 20096 | 18750 | 21796 | 22415 | 23451 | 22240 | 21359 | 22900 | 23769 | 23758 | 24936 | 22390 | 20861 | 24040
5489 | 5489 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 17 | 19090 | 17678 | 20959 | 21480 | 21362 | 20878 | 20437 | 19203 | 22069 | 22617 | 23606 | 22408 | 21753 | 23276 | 23986 | 23989 | 25125 | 22800 | 21363 | 24422
5490 | 5490 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 18 | 18813 | 17773 | 20847 | 21319 | 21031 | 20824 | 20484 | 19462 | 22196 | 22423 | 23554 | 22600 | 22068 | 23550 | 23997 | 23943 | 25306 | 23196 | 21982 | 24742
5491 | 5491 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 19 | 18180 | 17416 | 20214 | 20774 | 20595 | 20219 | 20125 | 19222 | 21745 | 22151 | 23562 | 22355 | 21990 | 23337 | 23919 | 23948 | 25591 | 23276 | 22128 | 24620
5492 | 5492 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 20 | 17612 | 17122 | 19900 | 20458 | 20467 | 19802 | 19724 | 19045 | 21565 | 22192 | 23960 | 22324 | 22064 | 23479 | 24266 | 24460 | 26281 | 23543 | 22387 | 24852
5493 | 5493 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 21 | 17528 | 17128 | 19714 | 20264 | 20328 | 19858 | 19880 | 19240 | 21582 | 22383 | 24241 | 22816 | 22677 | 23829 | 24767 | 25107 | 26962 | 24430 | 23159 | 25372
5494 | 5494 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 22 | 16488 | 16326 | 18542 | 19098 | 19243 | 18900 | 19212 | 18547 | 20542 | 21490 | 23358 | 22092 | 22274 | 22927 | 23979 | 24480 | 26299 | 24177 | 22737 | 24549
5495 | 5495 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 23 | 15250 | 15341 | 17169 | 17688 | 17867 | 17618 | 18300 | 17561 | 19178 | 20210 | 22106 | 20873 | 21451 | 21615 | 22708 | 23290 | 25139 | 23428 | 21857 | 23266
5496 | 5496 | 229 | 8 | 17 | Summer | 8 | 16 | Summer | 24 | 14191 | 14493 | 16013 | 16549 | 16695 | 16442 | 17412 | 16679 | 17995 | 19062 | 20853 | 19745 | 20619 | 20424 | 21595 | 22178 | 23923 | 22629 | 21031 | 22066
5497 | 5497 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 1 | 14005 | 14039 | 15277 | 15796 | 16465 | 16078 | 16175 | 16092 | 17425 | 18816 | 19954 | 19134 | 18923 | 20071 | 21020 | 22031 | 23020 | 20650 | 20293 | 21850
5498 | 5498 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 2 | 13530 | 13678 | 14813 | 15255 | 15950 | 15534 | 15575 | 15649 | 16892 | 18218 | 19188 | 18484 | 18211 | 19446 | 20306 | 21301 | 22145 | 19883 | 19709 | 21176
5499 | 5499 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 3 | 13238 | 13455 | 14509 | 14954 | 15648 | 15174 | 15196 | 15350 | 16512 | 17805 | 18634 | 17990 | 17716 | 18946 | 19784 | 20730 | 21470 | 19319 | 19242 | 20616
5500 | 5500 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 4 | 13064 | 13463 | 14473 | 14889 | 15564 | 14920 | 14903 | 15236 | 16295 | 17507 | 18134 | 17421 | 17165 | 18469 | 19222 | 20122 | 20668 | 18618 | 18752 | 19988
5501 | 5501 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 5 | 13019 | 13866 | 14851 | 15173 | 15892 | 14789 | 14725 | 15533 | 16460 | 17564 | 18064 | 16938 | 16687 | 18332 | 18893 | 19777 | 20193 | 17969 | 18550 | 19671
5502 | 5502 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 6 | 13074 | 14682 | 15600 | 15993 | 16593 | 14764 | 14594 | 16286 | 17039 | 18026 | 18404 | 16556 | 16195 | 18517 | 19013 | 19689 | 20050 | 17310 | 18742 | 19700
5503 | 5503 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 7 | 13519 | 15834 | 16585 | 17061 | 17509 | 15084 | 14687 | 17298 | 17816 | 18777 | 19096 | 16579 | 15950 | 18922 | 19542 | 20072 | 20483 | 16951 | 19403 | 19989
5504 | 5504 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 8 | 14540 | 16840 | 17607 | 17987 | 18516 | 16098 | 15427 | 18290 | 18731 | 19716 | 20125 | 17469 | 16599 | 19619 | 20285 | 20918 | 21421 | 17554 | 20272 | 20638
5505 | 5505 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 9 | 15399 | 17420 | 18193 | 18497 | 19136 | 16933 | 16021 | 18850 | 19156 | 20320 | 20912 | 18148 | 17091 | 20037 | 20732 | 21628 | 22299 | 18017 | 20809 | 21022
5506 | 5506 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 10 | 16184 | 18031 | 18842 | 19081 | 19679 | 17736 | 16689 | 19498 | 19867 | 20891 | 21757 | 19028 | 17822 | 20889 | 21513 | 22359 | 23304 | 18790 | 21636 | 21926
5507 | 5507 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 11 | 16672 | 18389 | 19224 | 19369 | 20119 | 18264 | 17118 | 19922 | 20329 | 21431 | 22396 | 19649 | 18312 | 21449 | 21970 | 23003 | 24013 | 19337 | 22175 | 22536
5508 | 5508 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 12 | 16998 | 18683 | 19559 | 19722 | 20555 | 18616 | 17444 | 20227 | 20696 | 21895 | 22866 | 20040 | 18676 | 21871 | 22463 | 23542 | 24553 | 19708 | 22550 | 22980
5509 | 5509 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 13 | 17142 | 18956 | 19799 | 19986 | 20895 | 18773 | 17599 | 20506 | 20931 | 22296 | 23202 | 20213 | 18831 | 22130 | 22750 | 23954 | 24883 | 19887 | 22847 | 23243
5510 | 5510 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 14 | 17203 | 19083 | 19920 | 20069 | 21064 | 18846 | 17593 | 20643 | 21042 | 22450 | 23349 | 20257 | 18804 | 22223 | 22823 | 24063 | 24989 | 19845 | 22952 | 23322
5511 | 5511 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 15 | 17360 | 19298 | 20082 | 20230 | 21160 | 18989 | 17770 | 20875 | 21200 | 22531 | 23475 | 20393 | 18975 | 22342 | 22933 | 24074 | 25067 | 20006 | 23143 | 23425
5512 | 5512 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 16 | 17643 | 19627 | 20552 | 20467 | 21398 | 19250 | 18048 | 21157 | 21818 | 22703 | 23607 | 20589 | 19196 | 23015 | 23053 | 24136 | 25111 | 20213 | 23362 | 24080
5513 | 5513 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 17 | 18095 | 20074 | 20932 | 20818 | 21593 | 19730 | 18632 | 21553 | 22202 | 22981 | 23890 | 21113 | 19835 | 23362 | 23409 | 24468 | 25510 | 20841 | 23882 | 24425
5514 | 5514 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 18 | 18163 | 20178 | 21014 | 20745 | 21624 | 20013 | 19103 | 21887 | 22342 | 23140 | 24230 | 21642 | 20626 | 23615 | 23603 | 24902 | 25975 | 21715 | 24454 | 24742
5515 | 5515 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 19 | 17864 | 19717 | 20647 | 20473 | 21602 | 19824 | 19031 | 21583 | 22078 | 23271 | 23971 | 21696 | 20844 | 23689 | 23764 | 25350 | 26007 | 22057 | 24526 | 24942
5516 | 5516 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 20 | 17434 | 19402 | 20350 | 20352 | 21747 | 19454 | 18870 | 21397 | 22036 | 23629 | 23979 | 21751 | 20989 | 24032 | 24272 | 26052 | 26364 | 22361 | 24803 | 25423
5517 | 5517 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 21 | 17405 | 19228 | 20140 | 20198 | 21650 | 19560 | 19027 | 21383 | 22105 | 23827 | 24224 | 22293 | 21536 | 24476 | 24872 | 26710 | 27018 | 23124 | 25325 | 26092
5518 | 5518 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 22 | 16639 | 18066 | 18955 | 19102 | 20544 | 18870 | 18320 | 20314 | 21090 | 22913 | 23315 | 21850 | 21012 | 23671 | 24223 | 26035 | 26315 | 22709 | 24508 | 25387
5519 | 5519 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 23 | 15747 | 16703 | 17536 | 17729 | 19191 | 17939 | 17310 | 18934 | 19728 | 21637 | 21978 | 20998 | 20081 | 22380 | 23009 | 24861 | 25086 | 21809 | 23230 | 24143
5520 | 5520 | 230 | 8 | 18 | Summer | 8 | 17 | Summer | 24 | 14884 | 15573 | 16400 | 16571 | 17962 | 17058 | 16429 | 17741 | 18602 | 20388 | 20640 | 20172 | 19243 | 21266 | 21892 | 23660 | 23751 | 20984 | 22047 | 23063
5521 | 5521 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 1 | 13909 | 14799 | 15586 | 16260 | 16987 | 15856 | 15812 | 17056 | 17816 | 19432 | 19619 | 18484 | 18477 | 20585 | 21657 | 22679 | 22574 | 20175 | 21767 | 22441
5522 | 5522 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 2 | 13394 | 14346 | 15069 | 15755 | 16345 | 15269 | 15381 | 16538 | 17209 | 18690 | 18875 | 17791 | 17956 | 19890 | 20947 | 21818 | 21720 | 19610 | 21094 | 21696
5523 | 5523 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 3 | 13077 | 14055 | 14764 | 15452 | 15920 | 14893 | 15087 | 16168 | 16834 | 18154 | 18294 | 17303 | 17557 | 19387 | 20388 | 21143 | 21022 | 19138 | 20533 | 21130
5524 | 5524 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 4 | 12864 | 14025 | 14717 | 15389 | 15707 | 14631 | 15008 | 15994 | 16586 | 17719 | 17734 | 16795 | 17219 | 18871 | 19817 | 20377 | 20176 | 18663 | 19898 | 20441
5525 | 5525 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 5 | 12798 | 14391 | 15000 | 15728 | 15916 | 14472 | 15334 | 16199 | 16644 | 17712 | 17393 | 16355 | 17184 | 18578 | 19500 | 19924 | 19515 | 18463 | 19574 | 19957
5526 | 5526 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 6 | 12740 | 15134 | 15814 | 16452 | 16547 | 14361 | 16128 | 16824 | 17252 | 18136 | 17065 | 15924 | 17539 | 18748 | 19453 | 19814 | 18785 | 18664 | 19606 | 19938
5527 | 5527 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 7 | 12900 | 16184 | 16905 | 17413 | 17571 | 14488 | 17196 | 17680 | 18137 | 18919 | 17151 | 15750 | 18312 | 19324 | 19881 | 20279 | 18530 | 19340 | 19911 | 20383
5528 | 5528 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 8 | 13533 | 17102 | 17720 | 18303 | 18618 | 15112 | 18085 | 18528 | 18929 | 19869 | 18046 | 16308 | 19087 | 19959 | 20625 | 21086 | 19272 | 20079 | 20449 | 20960
5529 | 5529 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 9 | 14388 | 17900 | 18430 | 19120 | 19630 | 15894 | 18843 | 19185 | 19600 | 20852 | 19119 | 17009 | 19834 | 20609 | 21530 | 22159 | 20416 | 20800 | 21021 | 21569
5530 | 5530 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 10 | 14979 | 18504 | 18976 | 19615 | 20352 | 16514 | 19445 | 19856 | 20182 | 21627 | 19998 | 17686 | 20567 | 21340 | 22215 | 23112 | 21458 | 21582 | 21890 | 22349
5531 | 5531 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 11 | 15427 | 18917 | 19313 | 20107 | 20941 | 16978 | 19905 | 20366 | 20603 | 22313 | 20708 | 18232 | 21103 | 21843 | 22898 | 23877 | 22254 | 22165 | 22543 | 22901
5532 | 5532 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 12 | 15633 | 19137 | 19576 | 20433 | 21255 | 17203 | 20107 | 20626 | 20892 | 22672 | 21123 | 18488 | 21344 | 22229 | 23334 | 24325 | 22715 | 22439 | 22887 | 23316
5533 | 5533 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 13 | 15729 | 19381 | 19829 | 20778 | 21541 | 17342 | 20372 | 20862 | 21151 | 23000 | 21320 | 18648 | 21620 | 22501 | 23729 | 24650 | 22916 | 22719 | 23132 | 23593
5534 | 5534 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 14 | 15837 | 19580 | 20012 | 21055 | 21797 | 17440 | 20616 | 21082 | 21327 | 23257 | 21471 | 18728 | 21835 | 22677 | 23946 | 24864 | 23018 | 22923 | 23310 | 23768
5535 | 5535 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 15 | 16064 | 19780 | 20220 | 21197 | 21994 | 17660 | 20890 | 21284 | 21530 | 23437 | 21562 | 18945 | 22087 | 22830 | 24001 | 24986 | 23086 | 23156 | 23461 | 23909
5536 | 5536 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 16 | 16467 | 20270 | 20548 | 21513 | 22274 | 18007 | 21245 | 21933 | 21787 | 23653 | 21809 | 19251 | 22389 | 23034 | 24138 | 25112 | 23268 | 23435 | 24171 | 24087
5537 | 5537 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 17 | 16977 | 20686 | 20916 | 21720 | 22591 | 18616 | 21664 | 22319 | 22137 | 23951 | 22197 | 19899 | 22905 | 23411 | 24489 | 25522 | 23632 | 23979 | 24546 | 24471
5538 | 5538 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 18 | 17230 | 20705 | 20756 | 21624 | 22622 | 18990 | 21876 | 22358 | 22095 | 24172 | 22600 | 20572 | 23336 | 23498 | 24828 | 25888 | 24204 | 24470 | 24781 | 24628
5539 | 5539 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 19 | 16949 | 20198 | 20349 | 21456 | 21959 | 18787 | 21428 | 21932 | 21865 | 23726 | 22248 | 20605 | 23178 | 23502 | 25129 | 25772 | 24189 | 24429 | 24864 | 24767
5540 | 5540 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 20 | 16665 | 19831 | 20192 | 21559 | 21641 | 18604 | 21207 | 21812 | 21865 | 23630 | 22412 | 20678 | 23299 | 23955 | 25780 | 26083 | 24689 | 24707 | 25327 | 25375
5541 | 5541 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 21 | 16669 | 19611 | 20011 | 21431 | 21505 | 18726 | 21147 | 21821 | 21984 | 23784 | 22677 | 21159 | 23607 | 24492 | 26390 | 26697 | 25335 | 25222 | 25999 | 26146
5542 | 5542 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 22 | 15862 | 18417 | 18875 | 20308 | 20346 | 17986 | 20047 | 20762 | 21045 | 22816 | 22057 | 20594 | 22678 | 23792 | 25679 | 25968 | 24909 | 24392 | 25287 | 25577
5543 | 5543 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 23 | 14886 | 17031 | 17507 | 18966 | 18950 | 16979 | 18655 | 19387 | 19748 | 21460 | 21149 | 19652 | 21357 | 22561 | 24496 | 24716 | 24080 | 23108 | 24048 | 24406
5544 | 5544 | 231 | 8 | 19 | Summer | 8 | 18 | Summer | 24 | 14045 | 15916 | 16350 | 17743 | 17606 | 16101 | 17459 | 18232 | 18599 | 20118 | 20089 | 18800 | 20155 | 21448 | 23276 | 23393 | 23038 | 21915 | 22940 | 23306
5545 | 5545 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 1 | 13288 | 14836 | 15798 | 16537 | 16474 | 15231 | 16462 | 17178 | 18054 | 18873 | 18523 | 17800 | 19445 | 20960 | 22052 | 21996 | 21002 | 21365 | 22057 | 22874
5546 | 5546 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 2 | 12944 | 14340 | 15313 | 15900 | 15829 | 14811 | 15955 | 16582 | 17478 | 18148 | 17777 | 17290 | 18835 | 20266 | 21205 | 21154 | 20175 | 20696 | 21316 | 22126
5547 | 5547 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 3 | 12719 | 14032 | 15017 | 15471 | 15368 | 14523 | 15595 | 16212 | 17082 | 17592 | 17279 | 16895 | 18343 | 19727 | 20541 | 20458 | 19576 | 20134 | 20748 | 21507
5548 | 5548 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 4 | 12731 | 13979 | 14971 | 15284 | 15090 | 14469 | 15460 | 16016 | 16843 | 17082 | 16808 | 16603 | 17909 | 19197 | 19814 | 19647 | 18892 | 19526 | 20078 | 20822
5549 | 5549 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 5 | 13117 | 14266 | 15313 | 15500 | 15061 | 14804 | 15688 | 16103 | 16951 | 16768 | 16381 | 16618 | 17807 | 18928 | 19403 | 19021 | 18210 | 19221 | 19604 | 20375
5550 | 5550 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 6 | 13941 | 15034 | 16031 | 16118 | 15049 | 15559 | 16290 | 16683 | 17493 | 16414 | 15985 | 17052 | 18069 | 18952 | 19357 | 18338 | 17547 | 19289 | 19613 | 20226
5551 | 5551 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 7 | 15131 | 16155 | 17026 | 17165 | 15384 | 16625 | 17179 | 17593 | 18338 | 16536 | 15935 | 17893 | 18551 | 19431 | 19868 | 18122 | 17324 | 19621 | 20082 | 20614
5552 | 5552 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 8 | 16330 | 17276 | 18230 | 18523 | 16656 | 17804 | 18358 | 18719 | 19491 | 17778 | 16970 | 18995 | 19466 | 20497 | 21001 | 19179 | 18279 | 20466 | 20966 | 21641
5553 | 5553 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 9 | 17095 | 18057 | 19151 | 19611 | 17855 | 18651 | 19138 | 19521 | 20311 | 18999 | 18203 | 19779 | 20120 | 21411 | 22097 | 20350 | 19449 | 21056 | 21593 | 22572
5554 | 5554 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 10 | 17808 | 18759 | 19821 | 20508 | 18803 | 19433 | 19995 | 20303 | 20967 | 20087 | 19279 | 20646 | 21072 | 22223 | 23178 | 21525 | 20591 | 22056 | 22502 | 23424
5555 | 5555 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 11 | 18349 | 19236 | 20432 | 21210 | 19542 | 20008 | 20618 | 20845 | 21677 | 20908 | 20140 | 21305 | 21803 | 23017 | 24062 | 22434 | 21525 | 22834 | 23179 | 24273
5556 | 5556 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 12 | 18597 | 19511 | 20802 | 21580 | 19963 | 20257 | 20927 | 21198 | 22091 | 21373 | 20712 | 21591 | 22170 | 23485 | 24530 | 22951 | 22140 | 23212 | 23629 | 24774
5557 | 5557 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 13 | 18749 | 19630 | 21012 | 21738 | 20026 | 20389 | 21031 | 21332 | 22366 | 21442 | 20982 | 21738 | 22304 | 23757 | 24727 | 23026 | 22437 | 23331 | 23787 | 25067
5558 | 5558 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 14 | 18787 | 19646 | 21110 | 21825 | 20019 | 20451 | 21070 | 21338 | 22452 | 21415 | 21084 | 21782 | 22319 | 23795 | 24769 | 22955 | 22512 | 23328 | 23778 | 25086
5559 | 5559 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 15 | 18835 | 19640 | 21051 | 21810 | 19921 | 20518 | 21062 | 21323 | 22382 | 21300 | 21218 | 21831 | 22289 | 23665 | 24703 | 22826 | 22628 | 23287 | 23727 | 24943
5560 | 5560 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 16 | 19039 | 19777 | 21172 | 21903 | 20019 | 20677 | 21479 | 21400 | 22430 | 21351 | 21484 | 21946 | 22815 | 23620 | 24639 | 22803 | 22849 | 23794 | 23704 | 24845
5561 | 5561 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 17 | 19463 | 20061 | 21320 | 22183 | 20338 | 21047 | 21820 | 21708 | 22673 | 21684 | 22078 | 22417 | 23126 | 23915 | 24993 | 23116 | 23462 | 24112 | 24032 | 25163
5562 | 5562 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 18 | 19469 | 19898 | 21155 | 22180 | 20524 | 21247 | 21854 | 21654 | 22726 | 22057 | 22585 | 22803 | 23297 | 24238 | 25346 | 23681 | 24119 | 24352 | 24191 | 25554
5563 | 5563 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 19 | 18969 | 19594 | 21071 | 21591 | 20085 | 20902 | 21509 | 21474 | 22776 | 21749 | 22354 | 22698 | 23299 | 24608 | 25302 | 23738 | 24047 | 24538 | 24432 | 26032
5564 | 5564 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 20 | 18610 | 19413 | 21136 | 21246 | 19889 | 20672 | 21350 | 21421 | 23036 | 21813 | 22372 | 22763 | 23554 | 25202 | 25564 | 24208 | 24395 | 24997 | 25033 | 26761
5565 | 5565 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 21 | 18415 | 19196 | 20966 | 21061 | 19773 | 20559 | 21284 | 21449 | 23142 | 21986 | 22544 | 22992 | 23929 | 25734 | 26110 | 24810 | 24895 | 25635 | 25775 | 27506
5566 | 5566 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 22 | 17241 | 18032 | 19820 | 19890 | 18934 | 19425 | 20187 | 20459 | 22171 | 21315 | 21727 | 22025 | 23097 | 24981 | 25345 | 24365 | 24240 | 24905 | 25193 | 26874
5567 | 5567 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 23 | 15913 | 16694 | 18488 | 18506 | 17966 | 18048 | 18799 | 19152 | 20902 | 20409 | 20671 | 20699 | 21794 | 23798 | 24096 | 23526 | 23243 | 23656 | 24052 | 25730
5568 | 5568 | 232 | 8 | 20 | Summer | 8 | 19 | Summer | 24 | 14814 | 15558 | 17250 | 17175 | 16913 | 16860 | 17635 | 17991 | 19633 | 19333 | 19559 | 19501 | 20667 | 22576 | 22760 | 22473 | 22113 | 22555 | 22958 | 24525
5569 | 5569 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 1 | 14117 | 15324 | 16360 | 16368 | 16128 | 16143 | 16888 | 17705 | 18735 | 18158 | 18523 | 19043 | 20028 | 21646 | 21689 | 20807 | 21104 | 21981 | 22810 | 23594
5570 | 5570 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 2 | 13679 | 14874 | 15759 | 15742 | 15491 | 15658 | 16310 | 17158 | 18021 | 17439 | 17929 | 18460 | 19338 | 20839 | 20866 | 20000 | 20399 | 21250 | 22073 | 22697
5571 | 5571 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 3 | 13394 | 14594 | 15364 | 15307 | 15091 | 15328 | 15977 | 16797 | 17506 | 16979 | 17487 | 18007 | 18855 | 20211 | 20216 | 19428 | 19839 | 20712 | 21465 | 22011
5572 | 5572 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 4 | 13360 | 14545 | 15195 | 15043 | 14837 | 15224 | 15819 | 16605 | 17129 | 16549 | 17172 | 17617 | 18378 | 19524 | 19432 | 18760 | 19302 | 20053 | 20780 | 21159
5573 | 5573 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 5 | 13737 | 14919 | 15444 | 15027 | 14701 | 15504 | 15969 | 16757 | 17181 | 16183 | 17241 | 17584 | 18161 | 19175 | 18853 | 18100 | 19139 | 19607 | 20353 | 20624
5574 | 5574 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 6 | 14462 | 15665 | 16098 | 14985 | 14622 | 16152 | 16606 | 17280 | 17586 | 15847 | 17735 | 17901 | 18404 | 19183 | 18213 | 17466 | 19355 | 19636 | 20210 | 20449
5575 | 5575 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 7 | 15493 | 16631 | 17131 | 15267 | 14793 | 17021 | 17502 | 18097 | 18358 | 15799 | 18541 | 18390 | 19012 | 19673 | 17971 | 17203 | 19950 | 20060 | 20539 | 20847
5576 | 5576 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 8 | 16486 | 17578 | 18260 | 16305 | 15607 | 17965 | 18407 | 19037 | 19390 | 16630 | 19495 | 19116 | 19762 | 20586 | 18798 | 17927 | 20872 | 20717 | 21320 | 21718
5577 | 5577 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 9 | 17047 | 18159 | 19078 | 17254 | 16523 | 18443 | 18919 | 19659 | 20206 | 17579 | 20134 | 19486 | 20147 | 21371 | 19677 | 18783 | 21552 | 21043 | 21933 | 22527
5578 | 5578 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 10 | 17506 | 18544 | 19675 | 17940 | 17222 | 18992 | 19407 | 20085 | 20890 | 18356 | 20769 | 20132 | 20722 | 22148 | 20550 | 19634 | 22247 | 21663 | 22485 | 23358
5579 | 5579 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 11 | 17858 | 18973 | 20216 | 18497 | 17829 | 19433 | 19764 | 20618 | 21503 | 19049 | 21273 | 20677 | 21165 | 22859 | 21299 | 20396 | 22804 | 22170 | 23175 | 24119
5580 | 5580 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 12 | 18189 | 19427 | 20690 | 19022 | 18446 | 19842 | 20220 | 21125 | 21993 | 19723 | 21679 | 21132 | 21665 | 23428 | 21916 | 21104 | 23235 | 22722 | 23780 | 24721
5581 | 5581 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 13 | 18528 | 19879 | 21077 | 19291 | 18921 | 20172 | 20577 | 21603 | 22408 | 20222 | 22060 | 21473 | 22026 | 23852 | 22214 | 21603 | 23620 | 23090 | 24294 | 25164
5582 | 5582 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 14 | 18667 | 20097 | 21299 | 19416 | 19170 | 20342 | 20714 | 21826 | 22620 | 20466 | 22263 | 21626 | 22152 | 24032 | 22281 | 21811 | 23795 | 23212 | 24448 | 25337
5583 | 5583 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 15 | 18790 | 20161 | 21400 | 19426 | 19433 | 20451 | 20819 | 21859 | 22702 | 20717 | 22369 | 21721 | 22237 | 24084 | 22268 | 22043 | 23887 | 23279 | 24418 | 25377
5584 | 5584 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 16 | 19252 | 20486 | 21682 | 19714 | 19923 | 21041 | 21075 | 22116 | 22913 | 21171 | 22699 | 22415 | 22422 | 24217 | 22441 | 22450 | 24160 | 23431 | 24515 | 25469
5585 | 5585 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 17 | 19733 | 20727 | 22054 | 20139 | 20605 | 21502 | 21496 | 22461 | 23259 | 21864 | 23138 | 22831 | 22844 | 24677 | 22861 | 23175 | 24621 | 23873 | 24936 | 25948
5586 | 5586 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 18 | 19860 | 20636 | 22094 | 20399 | 20941 | 21650 | 21548 | 22563 | 23563 | 22448 | 23456 | 23094 | 23033 | 25130 | 23523 | 23944 | 25116 | 24145 | 25437 | 26461
5587 | 5587 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 19 | 19467 | 20532 | 21493 | 19974 | 20530 | 21294 | 21355 | 22605 | 23207 | 22175 | 23206 | 23080 | 23123 | 25062 | 23564 | 23881 | 25096 | 24399 | 25934 | 26510
5588 | 5588 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 20 | 19092 | 20622 | 21135 | 19781 | 20399 | 21129 | 21271 | 22844 | 23045 | 22132 | 23157 | 23296 | 23513 | 25294 | 24012 | 24237 | 25236 | 25012 | 26694 | 26877
5589 | 5589 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 21 | 18873 | 20431 | 20934 | 19645 | 20277 | 21024 | 21254 | 22874 | 23126 | 22241 | 23133 | 23603 | 23988 | 25784 | 24572 | 24714 | 25520 | 25750 | 27430 | 27577
5590 | 5590 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 22 | 17676 | 19266 | 19721 | 18773 | 19294 | 19885 | 20206 | 21833 | 22108 | 21372 | 22015 | 22692 | 23244 | 24968 | 24082 | 24015 | 24572 | 25138 | 26775 | 26876
5591 | 5591 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 23 | 16310 | 17939 | 18345 | 17814 | 18185 | 18485 | 18880 | 20551 | 20763 | 20308 | 20562 | 21366 | 22011 | 23696 | 23232 | 23004 | 23147 | 23995 | 25638 | 25655
5592 | 5592 | 233 | 8 | 21 | Summer | 8 | 20 | Summer | 24 | 15213 | 16746 | 17003 | 16775 | 17082 | 17325 | 17708 | 19272 | 19402 | 19188 | 19308 | 20230 | 20883 | 22371 | 22170 | 21886 | 21919 | 22897 | 24437 | 24343
5593 | 5593 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 1 | 14324 | 15751 | 16057 | 15905 | 15939 | 16419 | 17250 | 18220 | 18350 | 18011 | 19027 | 19417 | 20513 | 21176 | 20436 | 20715 | 21839 | 22582 | 23386 | 23080
5594 | 5594 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 2 | 13841 | 15144 | 15435 | 15260 | 15429 | 15836 | 16699 | 17509 | 17648 | 17417 | 18414 | 18746 | 19838 | 20353 | 19621 | 20005 | 21131 | 21833 | 22491 | 22200
5595 | 5595 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 3 | 13555 | 14756 | 15015 | 14888 | 15086 | 15518 | 16361 | 17033 | 17137 | 16995 | 17975 | 18312 | 19343 | 19723 | 19068 | 19469 | 20573 | 21229 | 21800 | 21487
5596 | 5596 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 4 | 13506 | 14636 | 14788 | 14665 | 15015 | 15418 | 16234 | 16730 | 16696 | 16749 | 17603 | 17909 | 18875 | 19004 | 18447 | 18978 | 19935 | 20586 | 20992 | 20599
5597 | 5597 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 5 | 13791 | 14887 | 14777 | 14524 | 15360 | 15605 | 16428 | 16823 | 16441 | 16861 | 17627 | 17733 | 18662 | 18465 | 17822 | 18820 | 19626 | 20166 | 20457 | 19870
5598 | 5598 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 6 | 14571 | 15586 | 14769 | 14483 | 16157 | 16300 | 17026 | 17325 | 16172 | 17427 | 18129 | 18056 | 18768 | 17884 | 17230 | 19073 | 19831 | 20050 | 20304 | 19116
5599 | 5599 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 7 | 15655 | 16673 | 15107 | 14691 | 17173 | 17255 | 17917 | 18181 | 16309 | 18312 | 18831 | 18719 | 19245 | 17699 | 17010 | 19696 | 20296 | 20399 | 20727 | 18829
5600 | 5600 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 8 | 16466 | 17699 | 16082 | 15425 | 18077 | 18080 | 18792 | 19164 | 17263 | 19215 | 19575 | 19415 | 20014 | 18458 | 17663 | 20526 | 20890 | 21096 | 21485 | 19584
5601 | 5601 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 9 | 16918 | 18470 | 17044 | 16319 | 18695 | 18569 | 19395 | 19970 | 18164 | 19854 | 20111 | 19791 | 20618 | 19319 | 18506 | 21178 | 21363 | 21684 | 22261 | 20437
5602 | 5602 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 10 | 17425 | 19156 | 17832 | 17119 | 19298 | 19147 | 19918 | 20745 | 19035 | 20566 | 20926 | 20459 | 21216 | 20287 | 19451 | 21956 | 22265 | 22336 | 23192 | 21472
5603 | 5603 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 11 | 17711 | 19649 | 18362 | 17695 | 19696 | 19463 | 20412 | 21331 | 19654 | 21042 | 21551 | 20875 | 21825 | 20986 | 20174 | 22506 | 22973 | 23000 | 23925 | 22241
5604 | 5604 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 12 | 18033 | 20085 | 18859 | 18306 | 20023 | 19884 | 20890 | 21812 | 20195 | 21418 | 21960 | 21362 | 22365 | 21582 | 20858 | 22925 | 23424 | 23576 | 24501 | 22848
5605 | 5605 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 13 | 18318 | 20420 | 19065 | 18727 | 20321 | 20180 | 21299 | 22172 | 20420 | 21741 | 22392 | 21672 | 22796 | 21820 | 21299 | 23259 | 23863 | 24027 | 24885 | 23105
5606 | 5606 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 14 | 18475 | 20656 | 19192 | 18981 | 20528 | 20319 | 21527 | 22393 | 20539 | 21949 | 22674 | 21807 | 22980 | 21894 | 21514 | 23455 | 24125 | 24182 | 25059 | 23156
5607 | 5607 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 15 | 18688 | 20863 | 19314 | 19351 | 20745 | 20530 | 21670 | 22584 | 20631 | 22161 | 22913 | 22001 | 23062 | 21990 | 21860 | 23648 | 24329 | 24259 | 25205 | 23248
5608 | 5608 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 16 | 19071 | 21206 | 19653 | 19890 | 21187 | 20845 | 21996 | 22864 | 20925 | 22559 | 23677 | 22256 | 23272 | 22224 | 22318 | 23981 | 25087 | 24410 | 25350 | 23455
5609 | 5609 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 17 | 19510 | 21612 | 20111 | 20610 | 21583 | 21312 | 22372 | 23256 | 21406 | 23028 | 24037 | 22729 | 23710 | 22684 | 23076 | 24489 | 25519 | 24870 | 25868 | 23929
5610 | 5610 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 18 | 19422 | 21564 | 20248 | 20873 | 21703 | 21300 | 22372 | 23447 | 21812 | 23251 | 23948 | 22840 | 24068 | 23282 | 23780 | 24925 | 25484 | 25312 | 26325 | 24586
5611 | 5611 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 19 | 19063 | 20893 | 19746 | 20391 | 21216 | 21032 | 22334 | 22978 | 21418 | 22892 | 23679 | 22814 | 24359 | 23233 | 23642 | 24827 | 25491 | 25758 | 26324 | 24647
5612 | 5612 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 20 | 18869 | 20492 | 19504 | 20213 | 20965 | 20904 | 22509 | 22736 | 21420 | 22758 | 23835 | 23136 | 24911 | 23615 | 23938 | 24953 | 25971 | 26507 | 26678 | 25161
5613 | 5613 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 21 | 18640 | 20270 | 19321 | 20044 | 20645 | 20816 | 22464 | 22712 | 21519 | 22642 | 23890 | 23496 | 25360 | 24092 | 24363 | 25168 | 26403 | 27213 | 27356 | 25849
5614 | 5614 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 22 | 17455 | 19062 | 18435 | 19041 | 19377 | 19734 | 21384 | 21634 | 20805 | 21492 | 22882 | 22685 | 24562 | 23577 | 23650 | 24173 | 25593 | 26550 | 26657 | 25431
5615 | 5615 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 23 | 16116 | 17667 | 17467 | 17931 | 17869 | 18380 | 20070 | 20252 | 19877 | 20031 | 21455 | 21423 | 23360 | 22703 | 22629 | 22755 | 24262 | 25398 | 25436 | 24607
5616 | 5616 | 234 | 8 | 22 | Summer | 8 | 21 | Summer | 24 | 15004 | 16361 | 16410 | 16827 | 16640 | 17201 | 18775 | 18864 | 18804 | 18767 | 20292 | 20276 | 22128 | 21634 | 21487 | 21522 | 23138 | 24191 | 24110 | 23554
5617 | 5617 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 1 | 14742 | 15546 | 15683 | 15771 | 16259 | 16838 | 17791 | 17919 | 17680 | 18523 | 19452 | 19996 | 21140 | 20053 | 20385 | 21526 | 22394 | 23219 | 22960 | 21695
5618 | 5618 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 2 | 14306 | 14962 | 15083 | 15288 | 15760 | 16325 | 17124 | 17253 | 16976 | 17954 | 18816 | 19358 | 20339 | 19277 | 19726 | 20847 | 21646 | 22355 | 22101 | 20881
5619 | 5619 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 3 | 14043 | 14572 | 14718 | 14951 | 15432 | 16007 | 16663 | 16761 | 16546 | 17533 | 18382 | 18886 | 19734 | 18739 | 19202 | 20301 | 21094 | 21666 | 21392 | 20286
5620 | 5620 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 4 | 14021 | 14367 | 14508 | 14905 | 15328 | 15910 | 16408 | 16381 | 16182 | 17214 | 17956 | 18480 | 19128 | 18153 | 18742 | 19700 | 20387 | 20864 | 20516 | 19570
5621 | 5621 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 5 | 14407 | 14356 | 14394 | 15292 | 15643 | 16159 | 16575 | 16212 | 15869 | 17316 | 17945 | 18355 | 18844 | 17584 | 18632 | 19446 | 20092 | 20365 | 19814 | 18849
5622 | 5622 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 6 | 15149 | 14348 | 14345 | 16084 | 16395 | 16764 | 17117 | 15988 | 15567 | 17855 | 18316 | 18506 | 18900 | 17002 | 18887 | 19648 | 20180 | 20199 | 19039 | 18129
5623 | 5623 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 7 | 16183 | 14707 | 14609 | 17161 | 17471 | 17703 | 18055 | 16232 | 15620 | 18648 | 18991 | 19085 | 19495 | 16836 | 19546 | 20173 | 20569 | 20641 | 18777 | 17891
5624 | 5624 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 8 | 17163 | 15823 | 15491 | 18181 | 18519 | 18711 | 19182 | 17332 | 16513 | 19562 | 19748 | 19993 | 20466 | 17629 | 20514 | 20899 | 21140 | 21547 | 19640 | 18665
5625 | 5625 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 9 | 17912 | 16985 | 16658 | 19039 | 19351 | 19555 | 20229 | 18506 | 17689 | 20358 | 20253 | 20847 | 21473 | 18720 | 21411 | 21607 | 21572 | 22550 | 20722 | 19741
5626 | 5626 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 10 | 18552 | 17908 | 17596 | 19781 | 20200 | 20212 | 21111 | 19521 | 18713 | 21309 | 20932 | 21593 | 22473 | 19795 | 22324 | 22649 | 22332 | 23609 | 21897 | 20866
5627 | 5627 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 11 | 19035 | 18529 | 18267 | 20264 | 20818 | 20781 | 21802 | 20222 | 19464 | 22020 | 21398 | 22271 | 23257 | 20600 | 22960 | 23441 | 22875 | 24442 | 22755 | 21724
5628 | 5628 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 12 | 19463 | 18989 | 18851 | 20566 | 21175 | 21230 | 22253 | 20734 | 20109 | 22399 | 21819 | 22784 | 23806 | 21256 | 23356 | 23869 | 23384 | 24989 | 23348 | 22413
5629 | 5629 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 13 | 19827 | 19152 | 19222 | 20817 | 21544 | 21580 | 22557 | 20910 | 20506 | 22781 | 22059 | 23169 | 24135 | 21654 | 23648 | 24263 | 23638 | 25324 | 23555 | 22817
5630 | 5630 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 14 | 20226 | 19449 | 19649 | 21194 | 22014 | 21981 | 22951 | 21204 | 20934 | 23239 | 22243 | 23530 | 24500 | 22051 | 24019 | 24700 | 23804 | 25674 | 23788 | 23199
5631 | 5631 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 15 | 20399 | 19578 | 20017 | 21419 | 22264 | 22120 | 23137 | 21305 | 21293 | 23477 | 22401 | 23636 | 24652 | 22399 | 24210 | 24909 | 23942 | 25810 | 23875 | 23538
5632 | 5632 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 16 | 20659 | 19771 | 20431 | 21738 | 22824 | 22326 | 23312 | 21485 | 21682 | 24107 | 22476 | 23736 | 24738 | 22739 | 24428 | 25541 | 23953 | 25838 | 23955 | 23860
5633 | 5633 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 17 | 20697 | 20000 | 20909 | 21890 | 23016 | 22464 | 23454 | 21711 | 22178 | 24222 | 22566 | 23919 | 25000 | 23257 | 24694 | 25746 | 24024 | 26112 | 24178 | 24387
5634 | 5634 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 18 | 20273 | 19839 | 20852 | 21718 | 22593 | 22193 | 23343 | 21792 | 22420 | 23850 | 22344 | 23975 | 25110 | 23690 | 24869 | 25444 | 23906 | 26311 | 24582 | 24882
5635 | 5635 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 19 | 19976 | 19191 | 20208 | 21075 | 21900 | 22001 | 22697 | 21212 | 21916 | 23382 | 22198 | 24074 | 24810 | 23386 | 24605 | 25286 | 24099 | 26174 | 24508 | 24665
5636 | 5636 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 20 | 20001 | 18880 | 19962 | 20759 | 21731 | 22105 | 22385 | 21108 | 21753 | 23417 | 22754 | 24511 | 24950 | 23600 | 24659 | 25689 | 25008 | 26499 | 24983 | 24981
5637 | 5637 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 21 | 19787 | 18702 | 19790 | 20428 | 21436 | 22047 | 22316 | 21151 | 21796 | 23416 | 22883 | 24898 | 25350 | 23996 | 24856 | 26094 | 25541 | 27174 | 25683 | 25555
5638 | 5638 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 22 | 18621 | 17846 | 18789 | 19166 | 20206 | 20957 | 21215 | 20409 | 20911 | 22363 | 22056 | 24058 | 24490 | 23272 | 23862 | 25265 | 24938 | 26477 | 25282 | 24904
5639 | 5639 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 23 | 17277 | 16886 | 17691 | 17669 | 18717 | 19638 | 19818 | 19458 | 19835 | 20943 | 20846 | 22822 | 23210 | 22245 | 22436 | 23921 | 23796 | 25247 | 24469 | 23923
5640 | 5640 | 235 | 8 | 23 | Summer | 8 | 22 | Summer | 24 | 16132 | 15888 | 16596 | 16463 | 17538 | 18366 | 18444 | 18377 | 18713 | 19788 | 19803 | 21599 | 21868 | 21135 | 21213 | 22802 | 22787 | 23949 | 23439 | 22814
5641 | 5641 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 1 | 15151 | 15171 | 15537 | 16006 | 16595 | 17343 | 17502 | 17291 | 17556 | 18906 | 18613 | 20548 | 20758 | 20002 | 21123 | 22002 | 21652 | 22765 | 21556 | 21700
5642 | 5642 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 2 | 14590 | 14597 | 15068 | 15522 | 16036 | 16687 | 16846 | 16604 | 17001 | 18285 | 18019 | 19771 | 19975 | 19335 | 20454 | 21278 | 20969 | 21906 | 20729 | 20976
5643 | 5643 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 3 | 14222 | 14244 | 14762 | 15213 | 15722 | 16257 | 16388 | 16203 | 16611 | 17892 | 17601 | 19202 | 19361 | 18846 | 19934 | 20753 | 20420 | 21219 | 20153 | 20431
5644 | 5644 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 4 | 14104 | 14030 | 14714 | 15118 | 15557 | 16026 | 16044 | 15867 | 16392 | 17512 | 17209 | 18643 | 18673 | 18406 | 19359 | 20070 | 19729 | 20350 | 19434 | 19848
5645 | 5645 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 5 | 14377 | 13922 | 15085 | 15442 | 15865 | 16210 | 15908 | 15587 | 16560 | 17542 | 17163 | 18411 | 18197 | 18309 | 19122 | 19790 | 19366 | 19648 | 18699 | 19604
5646 | 5646 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 6 | 15073 | 13886 | 15895 | 16230 | 16572 | 16794 | 15751 | 15357 | 17153 | 17982 | 17432 | 18553 | 17650 | 18599 | 19367 | 19917 | 19276 | 18890 | 17985 | 19769
5647 | 5647 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 7 | 16216 | 14172 | 17020 | 17355 | 17503 | 17775 | 16066 | 15480 | 18125 | 18735 | 17908 | 19236 | 17549 | 19310 | 19943 | 20344 | 19485 | 18649 | 17760 | 20416
5648 | 5648 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 8 | 17498 | 15196 | 18194 | 18563 | 18495 | 19045 | 17319 | 16542 | 19311 | 19668 | 18670 | 20370 | 18613 | 20423 | 20829 | 21076 | 20131 | 19649 | 18679 | 21537
5649 | 5649 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 9 | 18627 | 16512 | 19247 | 19567 | 19248 | 20252 | 18668 | 17915 | 20360 | 20366 | 19282 | 21543 | 19877 | 21487 | 21709 | 21686 | 20677 | 20896 | 19912 | 22597
5650 | 5650 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 10 | 19438 | 17451 | 19986 | 20388 | 19812 | 21120 | 19661 | 18919 | 21197 | 21028 | 19808 | 22526 | 20970 | 22396 | 22729 | 22433 | 21294 | 22050 | 21035 | 23561
5651 | 5651 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 11 | 20053 | 18174 | 20512 | 21048 | 20211 | 21837 | 20399 | 19708 | 21777 | 21536 | 20279 | 23345 | 21792 | 23070 | 23575 | 23017 | 21828 | 22953 | 21942 | 24282
5652 | 5652 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 12 | 20229 | 18546 | 20614 | 21181 | 20326 | 22086 | 20706 | 20127 | 21893 | 21752 | 20354 | 23669 | 22120 | 23263 | 23798 | 23294 | 21914 | 23349 | 22422 | 24504
5653 | 5653 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 13 | 20400 | 18739 | 20720 | 21400 | 20424 | 22238 | 20735 | 20369 | 22034 | 21848 | 20516 | 23844 | 22189 | 23406 | 24050 | 23395 | 22108 | 23407 | 22682 | 24659
5654 | 5654 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 14 | 20747 | 19100 | 21032 | 21802 | 20558 | 22570 | 20965 | 20732 | 22350 | 21973 | 20646 | 24152 | 22385 | 23717 | 24430 | 23491 | 22203 | 23580 | 23004 | 24971
5655 | 5655 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 15 | 20885 | 19384 | 21203 | 21991 | 20671 | 22694 | 21001 | 21022 | 22499 | 22073 | 20702 | 24246 | 22416 | 23849 | 24574 | 23564 | 22221 | 23601 | 23279 | 25098
5656 | 5656 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 16 | 21111 | 19805 | 21512 | 22505 | 20817 | 22871 | 21177 | 21402 | 22770 | 22146 | 20841 | 24328 | 22532 | 24060 | 25209 | 23566 | 22288 | 23669 | 23591 | 25287
5657 | 5657 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 17 | 21272 | 20273 | 21659 | 22690 | 20918 | 23016 | 21405 | 21888 | 23006 | 22236 | 21167 | 24579 | 22765 | 24328 | 25415 | 23631 | 22637 | 23898 | 24118 | 25569
5658 | 5658 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 18 | 21019 | 20249 | 21489 | 22340 | 20679 | 22957 | 21517 | 22147 | 23025 | 22055 | 21382 | 24722 | 23158 | 24570 | 25171 | 23588 | 23007 | 24375 | 24686 | 25859
5659 | 5659 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 19 | 20247 | 19651 | 20874 | 21673 | 20385 | 22343 | 20956 | 21646 | 22530 | 21901 | 21427 | 24415 | 22965 | 24329 | 25031 | 23810 | 23274 | 24355 | 24521 | 25703
5660 | 5660 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 20 | 19823 | 19411 | 20557 | 21496 | 20584 | 22034 | 20840 | 21456 | 22318 | 22388 | 21866 | 24500 | 23268 | 24362 | 25425 | 24700 | 24099 | 24859 | 24866 | 25810
5661 | 5661 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 21 | 19591 | 19219 | 20215 | 21172 | 20303 | 21918 | 20822 | 21457 | 22172 | 22429 | 22033 | 24816 | 23684 | 24513 | 25769 | 25197 | 24689 | 25541 | 25428 | 26117
5662 | 5662 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 22 | 18387 | 18220 | 18941 | 19933 | 19211 | 20780 | 20032 | 20546 | 21017 | 21551 | 21239 | 23930 | 23152 | 23496 | 24896 | 24572 | 24136 | 25127 | 24775 | 25165
5663 | 5663 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 23 | 17009 | 17138 | 17448 | 18455 | 17906 | 19375 | 19071 | 19456 | 19552 | 20325 | 20093 | 22626 | 22263 | 22054 | 23550 | 23412 | 23069 | 24301 | 23784 | 23757
5664 | 5664 | 236 | 8 | 24 | Summer | 8 | 23 | Summer | 24 | 15779 | 16077 | 16230 | 17292 | 16838 | 18009 | 17981 | 18325 | 18301 | 19270 | 19076 | 21283 | 21221 | 20837 | 22429 | 22413 | 22106 | 23265 | 22674 | 22549
5665 | 5665 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 1 | 14882 | 15016 | 15742 | 16342 | 15628 | 17053 | 16951 | 17165 | 17939 | 18063 | 18395 | 20156 | 19630 | 20672 | 21609 | 21277 | 21482 | 21394 | 21535 | 22496
5666 | 5666 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 2 | 14317 | 14552 | 15280 | 15791 | 15155 | 16416 | 16276 | 16624 | 17391 | 17487 | 17792 | 19396 | 18868 | 20020 | 20896 | 20596 | 20757 | 20570 | 20817 | 21786
5667 | 5667 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 3 | 13949 | 14257 | 14977 | 15486 | 14861 | 15962 | 15881 | 16250 | 16999 | 17092 | 17360 | 18798 | 18356 | 19509 | 20376 | 20063 | 20193 | 19991 | 20267 | 21214
5668 | 5668 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 4 | 13735 | 14210 | 14890 | 15343 | 14743 | 15650 | 15573 | 16073 | 16717 | 16750 | 16958 | 18170 | 17782 | 18965 | 19721 | 19391 | 19491 | 19277 | 19691 | 20515
5669 | 5669 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 5 | 13710 | 14610 | 15244 | 15682 | 15047 | 15581 | 15357 | 16296 | 16878 | 16799 | 16943 | 17768 | 17255 | 18793 | 19500 | 19070 | 19146 | 18564 | 19473 | 20165
5670 | 5670 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 6 | 13722 | 15452 | 16051 | 16432 | 15745 | 15483 | 15196 | 16968 | 17498 | 17167 | 17327 | 17314 | 16738 | 19099 | 19684 | 19028 | 19148 | 17879 | 19657 | 20303
5671 | 5671 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 7 | 14039 | 16534 | 17156 | 17343 | 16540 | 15773 | 15310 | 17953 | 18319 | 17651 | 17854 | 17231 | 16573 | 19657 | 20092 | 19226 | 19374 | 17599 | 20245 | 20740
5672 | 5672 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 8 | 15070 | 17483 | 18167 | 18113 | 17166 | 16784 | 16149 | 18933 | 19176 | 18227 | 18503 | 18088 | 17299 | 20334 | 20618 | 19665 | 19953 | 18286 | 21130 | 21358
5673 | 5673 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 9 | 16003 | 18171 | 18856 | 18531 | 17413 | 17776 | 17192 | 19665 | 19804 | 18506 | 18990 | 19016 | 18220 | 20875 | 20897 | 19865 | 20454 | 19185 | 21849 | 21898
5674 | 5674 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 10 | 16736 | 18742 | 19508 | 18911 | 17705 | 18568 | 18012 | 20316 | 20559 | 18864 | 19527 | 19919 | 19115 | 21716 | 21459 | 20311 | 21076 | 20129 | 22636 | 22801
5675 | 5675 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 11 | 17330 | 19173 | 20079 | 19231 | 17987 | 19203 | 18695 | 20820 | 21229 | 19219 | 20017 | 20663 | 19890 | 22459 | 21946 | 20761 | 21659 | 20940 | 23260 | 23593
5676 | 5676 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 12 | 17824 | 19484 | 20426 | 19583 | 18268 | 19719 | 19325 | 21175 | 21648 | 19503 | 20352 | 21232 | 20592 | 22892 | 22435 | 21091 | 22074 | 21629 | 23687 | 24047
5677 | 5677 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 13 | 18029 | 19781 | 20836 | 19857 | 18572 | 19942 | 19760 | 21491 | 22071 | 19859 | 20643 | 21479 | 21028 | 23340 | 22733 | 21457 | 22362 | 22084 | 24036 | 24505
5678 | 5678 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 14 | 18219 | 20050 | 21200 | 19960 | 18674 | 20142 | 20089 | 21773 | 22421 | 19956 | 20824 | 21648 | 21325 | 23685 | 22802 | 21520 | 22513 | 22370 | 24315 | 24843
5679 | 5679 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 15 | 18304 | 20237 | 21391 | 20079 | 18769 | 20178 | 20382 | 21926 | 22599 | 20024 | 20863 | 21680 | 21617 | 23841 | 22882 | 21548 | 22510 | 22651 | 24445 | 24986
5680 | 5680 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 16 | 18514 | 20562 | 21876 | 20255 | 18996 | 20404 | 20801 | 22235 | 23253 | 20209 | 21031 | 21846 | 21976 | 24518 | 22920 | 21643 | 22576 | 23001 | 24666 | 25643
5681 | 5681 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 17 | 18907 | 20896 | 22224 | 20509 | 19446 | 20799 | 21449 | 22618 | 23516 | 20697 | 21424 | 22228 | 22649 | 24888 | 23146 | 22157 | 22957 | 23689 | 25109 | 26017
5682 | 5682 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 18 | 18993 | 20889 | 22081 | 20481 | 19591 | 21100 | 21879 | 22797 | 23403 | 21097 | 21701 | 22787 | 23338 | 24845 | 23304 | 22741 | 23426 | 24467 | 25615 | 26025
5683 | 5683 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 19 | 18470 | 20340 | 21475 | 20253 | 19444 | 20594 | 21430 | 22348 | 23011 | 21144 | 21629 | 22632 | 23126 | 24739 | 23566 | 23059 | 23658 | 24380 | 25535 | 26048
5684 | 5684 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 20 | 18169 | 19985 | 21254 | 20405 | 19629 | 20452 | 21198 | 22078 | 22996 | 21468 | 22056 | 22862 | 23311 | 25068 | 24396 | 23840 | 24386 | 24716 | 25634 | 26511
5685 | 5685 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 21 | 17966 | 19645 | 20909 | 20095 | 19396 | 20385 | 21148 | 21884 | 22919 | 21546 | 22244 | 23197 | 23651 | 25359 | 24843 | 24391 | 24995 | 25270 | 25942 | 27004
5686 | 5686 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 22 | 17108 | 18373 | 19648 | 18988 | 18345 | 19568 | 20212 | 20695 | 21820 | 20717 | 21419 | 22618 | 22894 | 24460 | 24189 | 23818 | 24390 | 24616 | 24999 | 26210
5687 | 5687 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 23 | 16158 | 16902 | 18166 | 17681 | 17093 | 18590 | 19104 | 19211 | 20381 | 19546 | 20265 | 21720 | 21846 | 23086 | 23015 | 22745 | 23309 | 23614 | 23588 | 24908
5688 | 5688 | 237 | 8 | 25 | Summer | 8 | 24 | Summer | 24 | 15224 | 15709 | 16995 | 16611 | 16024 | 17507 | 17964 | 17936 | 19219 | 18504 | 19187 | 20650 | 20716 | 21961 | 22016 | 21775 | 22318 | 22497 | 22375 | 23795
5689 | 5689 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 1 | 14590 | 15268 | 16103 | 15447 | 15357 | 16615 | 16851 | 17592 | 18350 | 17852 | 18094 | 19214 | 19608 | 21159 | 20910 | 21174 | 21155 | 21397 | 22385 | 23044
5690 | 5690 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 2 | 14028 | 14804 | 15556 | 14965 | 14854 | 15937 | 16308 | 17039 | 17737 | 17253 | 17478 | 18451 | 18948 | 20450 | 20228 | 20439 | 20425 | 20670 | 21663 | 22283
5691 | 5691 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 3 | 13670 | 14501 | 15248 | 14673 | 14560 | 15547 | 15941 | 16661 | 17362 | 16842 | 17031 | 17950 | 18480 | 19940 | 19703 | 19881 | 19862 | 20118 | 21090 | 21710
5692 | 5692 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 4 | 13469 | 14435 | 15140 | 14595 | 14471 | 15284 | 15819 | 16442 | 17054 | 16521 | 16554 | 17443 | 18091 | 19346 | 19077 | 19218 | 19097 | 19573 | 20421 | 20951
5693 | 5693 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 5 | 13356 | 14787 | 15483 | 14916 | 14787 | 15093 | 16074 | 16647 | 17141 | 16569 | 16242 | 16958 | 18028 | 19164 | 18787 | 18895 | 18425 | 19360 | 20067 | 20581
5694 | 5694 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 6 | 13311 | 15583 | 16223 | 15643 | 15516 | 14952 | 16788 | 17315 | 17647 | 17026 | 15947 | 16492 | 18359 | 19387 | 18778 | 18919 | 17845 | 19543 | 20198 | 20614
5695 | 5695 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 7 | 13581 | 16763 | 17193 | 16531 | 16353 | 15139 | 17871 | 18253 | 18451 | 17675 | 15751 | 16431 | 19080 | 19894 | 19062 | 19219 | 17432 | 20185 | 20688 | 20972
5696 | 5696 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 8 | 14351 | 17793 | 17949 | 17147 | 17082 | 15949 | 18841 | 19139 | 19163 | 18341 | 16375 | 17157 | 19973 | 20421 | 19498 | 19787 | 17957 | 21046 | 21286 | 21431
5697 | 5697 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 9 | 15323 | 18509 | 18391 | 17412 | 17621 | 16996 | 19587 | 19813 | 19559 | 18864 | 17145 | 18103 | 20733 | 20723 | 19719 | 20305 | 18747 | 21774 | 21841 | 21697
5698 | 5698 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 10 | 16101 | 19149 | 18770 | 17698 | 18079 | 17804 | 20227 | 20570 | 20036 | 19388 | 17802 | 18992 | 21470 | 21274 | 20163 | 20924 | 19469 | 22564 | 22751 | 22308
5699 | 5699 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 11 | 16678 | 19623 | 19025 | 17889 | 18415 | 18405 | 20649 | 21143 | 20388 | 19793 | 18244 | 19673 | 21988 | 21690 | 20536 | 21423 | 19943 | 23114 | 23464 | 22766
5700 | 5700 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 12 | 17247 | 20004 | 19396 | 18144 | 18697 | 19039 | 21004 | 21536 | 20798 | 20120 | 18618 | 20350 | 22389 | 22177 | 20872 | 21798 | 20347 | 23541 | 23930 | 23287
5701 | 5701 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 13 | 17637 | 20405 | 19682 | 18475 | 18969 | 19490 | 21335 | 21983 | 21099 | 20435 | 18709 | 20819 | 22736 | 22493 | 21255 | 22122 | 20437 | 23910 | 24404 | 23613
5702 | 5702 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 14 | 17934 | 20742 | 19758 | 18565 | 19135 | 19796 | 21591 | 22324 | 21170 | 20599 | 18807 | 21105 | 22990 | 22537 | 21299 | 22256 | 20517 | 24160 | 24706 | 23657
5703 | 5703 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 15 | 18304 | 21043 | 19961 | 18747 | 19296 | 20177 | 21830 | 22588 | 21348 | 20730 | 18866 | 21476 | 23210 | 22707 | 21416 | 22330 | 20563 | 24375 | 24939 | 23810
5704 | 5704 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 16 | 18848 | 21555 | 20238 | 19075 | 19630 | 20682 | 22226 | 23282 | 21560 | 20997 | 19049 | 21939 | 23541 | 22846 | 21605 | 22503 | 20681 | 24673 | 25674 | 23924
5705 | 5705 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 17 | 19426 | 21831 | 20430 | 19473 | 19893 | 21274 | 22546 | 23498 | 21750 | 21323 | 19473 | 22567 | 23910 | 23010 | 22056 | 22851 | 21170 | 25058 | 25992 | 24101
5706 | 5706 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 18 | 19520 | 21599 | 20305 | 19506 | 19935 | 21593 | 22588 | 23295 | 21694 | 21474 | 19968 | 23138 | 24273 | 23060 | 22531 | 23241 | 21823 | 25476 | 25916 | 24212
5707 | 5707 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 19 | 18993 | 20964 | 20057 | 19328 | 19593 | 21135 | 22115 | 22860 | 21563 | 21337 | 19902 | 22878 | 24072 | 23284 | 22825 | 23441 | 21975 | 25404 | 25941 | 24570
5708 | 5708 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 20 | 18713 | 20695 | 20166 | 19460 | 19707 | 20873 | 21813 | 22753 | 21947 | 21649 | 20391 | 22978 | 24033 | 24048 | 23551 | 24110 | 22809 | 25498 | 26378 | 25488
5709 | 5709 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 21 | 18513 | 20334 | 19821 | 19186 | 19496 | 20783 | 21574 | 22611 | 21904 | 21739 | 20626 | 23247 | 24139 | 24417 | 24037 | 24670 | 23439 | 25790 | 26868 | 26095
5710 | 5710 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 22 | 17540 | 19094 | 18700 | 18127 | 18440 | 19839 | 20371 | 21491 | 20993 | 20881 | 20109 | 22473 | 23116 | 23737 | 23450 | 24060 | 23110 | 24854 | 26088 | 25554
5711 | 5711 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 23 | 16444 | 17619 | 17386 | 16865 | 17165 | 18713 | 18867 | 20021 | 19736 | 19699 | 19294 | 21407 | 21661 | 22561 | 22367 | 22971 | 22400 | 23435 | 24793 | 24428
5712 | 5712 | 238 | 8 | 26 | Summer | 8 | 25 | Summer | 24 | 15430 | 16463 | 16317 | 15800 | 16080 | 17585 | 17585 | 18835 | 18667 | 18607 | 18437 | 20272 | 20414 | 21536 | 21374 | 21955 | 21537 | 22215 | 23683 | 23430
5713 | 5713 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 1 | 14367 | 15484 | 15131 | 15090 | 15009 | 16410 | 17140 | 17864 | 17449 | 17471 | 16669 | 19096 | 20205 | 20367 | 20718 | 20733 | 19188 | 22147 | 22843 | 22292
5714 | 5714 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 2 | 13920 | 14978 | 14682 | 14604 | 14529 | 15892 | 16612 | 17280 | 16896 | 16891 | 16138 | 18461 | 19567 | 19713 | 20005 | 20031 | 18585 | 21442 | 22092 | 21579
5715 | 5715 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 3 | 13635 | 14680 | 14408 | 14317 | 14211 | 15543 | 16256 | 16919 | 16522 | 16476 | 15733 | 17998 | 19074 | 19198 | 19473 | 19476 | 18085 | 20879 | 21511 | 21007
5716 | 5716 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 4 | 13598 | 14598 | 14347 | 14240 | 14003 | 15447 | 16077 | 16654 | 16247 | 16063 | 15352 | 17647 | 18578 | 18627 | 18852 | 18747 | 17478 | 20216 | 20758 | 20272
5717 | 5717 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 5 | 13995 | 14949 | 14703 | 14614 | 13983 | 15752 | 16348 | 16832 | 16366 | 15832 | 15016 | 17665 | 18458 | 18401 | 18586 | 18135 | 16931 | 19895 | 20412 | 19866
5718 | 5718 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 6 | 14842 | 15723 | 15483 | 15402 | 14014 | 16516 | 17093 | 17425 | 16820 | 15636 | 14584 | 18081 | 18824 | 18465 | 18672 | 17616 | 16333 | 20063 | 20475 | 19748
5719 | 5719 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 7 | 15955 | 16673 | 16394 | 16255 | 14120 | 17595 | 18065 | 18273 | 17402 | 15481 | 14255 | 18848 | 19456 | 18764 | 18964 | 17212 | 15779 | 20539 | 20815 | 19923
5720 | 5720 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 8 | 16846 | 17429 | 16998 | 16971 | 14844 | 18525 | 18950 | 18979 | 17940 | 16101 | 14789 | 19730 | 20117 | 19193 | 19529 | 17711 | 16182 | 21122 | 21249 | 20295
5721 | 5721 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 9 | 17437 | 17808 | 17218 | 17417 | 15547 | 19184 | 19568 | 19306 | 18160 | 16815 | 15440 | 20409 | 20611 | 19344 | 19975 | 18420 | 16804 | 21597 | 21444 | 20446
5722 | 5722 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 10 | 17994 | 18182 | 17493 | 17859 | 16060 | 19795 | 20295 | 19756 | 18496 | 17451 | 16069 | 21121 | 21442 | 19767 | 20585 | 19113 | 17462 | 22488 | 22041 | 20914
5723 | 5723 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 11 | 18376 | 18445 | 17690 | 18176 | 16407 | 20215 | 20870 | 20096 | 18789 | 17896 | 16568 | 21630 | 22124 | 20140 | 21079 | 19574 | 17960 | 23209 | 22509 | 21338
5724 | 5724 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 12 | 18677 | 18773 | 17929 | 18456 | 16687 | 20553 | 21243 | 20509 | 19058 | 18251 | 16965 | 22026 | 22548 | 20461 | 21451 | 19970 | 18364 | 23661 | 23015 | 21681
5725 | 5725 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 13 | 18970 | 19028 | 18243 | 18719 | 16748 | 20866 | 21670 | 20802 | 19410 | 18329 | 17187 | 22365 | 22993 | 20828 | 21748 | 20043 | 18580 | 24117 | 23325 | 22075
5726 | 5726 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 14 | 19179 | 19105 | 18309 | 18862 | 16839 | 21097 | 21987 | 20852 | 19468 | 18407 | 17360 | 22596 | 23292 | 20852 | 21861 | 20098 | 18733 | 24402 | 23344 | 22088
5727 | 5727 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 15 | 19438 | 19241 | 18465 | 19002 | 16905 | 21311 | 22226 | 21011 | 19603 | 18445 | 17594 | 22797 | 23515 | 20950 | 21923 | 20123 | 18966 | 24607 | 23470 | 22158
5728 | 5728 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 16 | 19823 | 19487 | 18768 | 19314 | 17153 | 21683 | 22855 | 21200 | 19852 | 18617 | 17992 | 23112 | 24241 | 21120 | 22060 | 20220 | 19330 | 25304 | 23554 | 22290
5729 | 5729 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 17 | 20217 | 19758 | 19239 | 19671 | 17719 | 22089 | 23166 | 21478 | 20376 | 19120 | 18769 | 23567 | 24650 | 21665 | 22501 | 20807 | 20098 | 25714 | 23819 | 22838
5730 | 5730 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 18 | 20192 | 19718 | 19299 | 19768 | 18107 | 22215 | 23051 | 21490 | 20757 | 19682 | 19399 | 23976 | 24604 | 22224 | 22984 | 21543 | 20896 | 25735 | 24027 | 23453
5731 | 5731 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 19 | 19636 | 19436 | 19083 | 19392 | 17695 | 21728 | 22575 | 21306 | 20745 | 19545 | 19216 | 23725 | 24456 | 22462 | 23135 | 21664 | 20911 | 25748 | 24374 | 23832
5732 | 5732 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 20 | 19260 | 19532 | 19195 | 19478 | 17878 | 21422 | 22442 | 21636 | 20987 | 19960 | 19711 | 23638 | 24713 | 23151 | 23771 | 22480 | 21677 | 26200 | 25302 | 24648
5733 | 5733 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 21 | 18914 | 19176 | 18893 | 19227 | 17768 | 21157 | 22244 | 21517 | 20978 | 20092 | 19946 | 23681 | 24942 | 23567 | 24274 | 23056 | 22250 | 26673 | 25895 | 25301
5734 | 5734 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 22 | 17642 | 18041 | 17798 | 18141 | 17032 | 19923 | 21071 | 20540 | 20099 | 19507 | 19274 | 22605 | 24015 | 22931 | 23634 | 22694 | 21754 | 25872 | 25333 | 24797
5735 | 5735 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 23 | 16189 | 16748 | 16546 | 16890 | 16202 | 18426 | 19599 | 19275 | 18927 | 18683 | 18405 | 21151 | 22638 | 21844 | 22542 | 21974 | 20942 | 24563 | 24218 | 23767
5736 | 5736 | 239 | 8 | 27 | Summer | 8 | 26 | Summer | 24 | 15041 | 15709 | 15472 | 15816 | 15343 | 17156 | 18408 | 18199 | 17876 | 17831 | 17563 | 19906 | 21488 | 20848 | 21513 | 21127 | 20117 | 23453 | 23230 | 22795
5737 | 5737 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 1 | 14606 | 14594 | 14839 | 14810 | 14243 | 16748 | 17502 | 17012 | 17228 | 16232 | 16939 | 19707 | 20678 | 20249 | 20339 | 18909 | 19632 | 22691 | 22148 | 22229
5738 | 5738 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 2 | 14167 | 14143 | 14376 | 14333 | 13778 | 16232 | 16924 | 16472 | 16657 | 15715 | 16509 | 19083 | 19988 | 19554 | 19652 | 18308 | 19153 | 21939 | 21435 | 21468
5739 | 5739 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 3 | 13876 | 13862 | 14097 | 14020 | 13458 | 15880 | 16574 | 16110 | 16278 | 15322 | 16244 | 18604 | 19503 | 19029 | 19110 | 17812 | 18959 | 21371 | 20849 | 20865
5740 | 5740 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 4 | 13811 | 13804 | 14026 | 13824 | 13283 | 15720 | 16337 | 15883 | 16010 | 14976 | 16026 | 18152 | 18949 | 18438 | 18403 | 17220 | 18555 | 20618 | 20119 | 20113
5741 | 5741 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 5 | 14178 | 14179 | 14425 | 13830 | 13198 | 16037 | 16570 | 16070 | 16147 | 14701 | 16122 | 18094 | 18838 | 18225 | 17834 | 16701 | 18539 | 20287 | 19725 | 19721
5742 | 5742 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 6 | 14975 | 14982 | 15240 | 13884 | 13028 | 16817 | 17211 | 16599 | 16688 | 14323 | 16634 | 18514 | 19122 | 18354 | 17349 | 16118 | 18889 | 20363 | 19609 | 19681
5743 | 5743 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 7 | 16152 | 15943 | 16151 | 14033 | 12924 | 17838 | 18114 | 17269 | 17386 | 14059 | 17327 | 19220 | 19657 | 18710 | 16989 | 15592 | 19428 | 20725 | 19801 | 19928
5744 | 5744 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 8 | 17182 | 16541 | 16880 | 14767 | 13551 | 18731 | 18840 | 17851 | 18070 | 14618 | 18116 | 19931 | 20202 | 19279 | 17503 | 16008 | 20079 | 21169 | 20162 | 20457
5745 | 5745 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 9 | 17912 | 16826 | 17427 | 15556 | 14352 | 19423 | 19254 | 18170 | 18591 | 15362 | 18734 | 20537 | 20530 | 19804 | 18290 | 16715 | 20593 | 21447 | 20381 | 20979
5746 | 5746 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 10 | 18463 | 17047 | 17817 | 16014 | 14822 | 20077 | 19643 | 18439 | 19046 | 15939 | 19293 | 21300 | 21013 | 20354 | 18925 | 17320 | 21010 | 21986 | 20789 | 21573
5747 | 5747 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 11 | 18933 | 17254 | 18145 | 16357 | 15227 | 20647 | 19979 | 18732 | 19434 | 16448 | 19802 | 21975 | 21417 | 20855 | 19390 | 17820 | 21425 | 22465 | 21235 | 22116
5748 | 5748 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 12 | 19298 | 17476 | 18410 | 16624 | 15573 | 21004 | 20373 | 18986 | 19741 | 16832 | 20206 | 22383 | 21891 | 21206 | 19763 | 18214 | 21820 | 22954 | 21564 | 22504
5749 | 5749 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 13 | 19695 | 17816 | 18702 | 16714 | 15807 | 21449 | 20690 | 19366 | 20060 | 17081 | 20564 | 22858 | 22213 | 21531 | 19869 | 18461 | 22120 | 23289 | 21982 | 22846
5750 | 5750 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 14 | 20027 | 17920 | 18858 | 16825 | 16019 | 21782 | 20756 | 19448 | 20226 | 17274 | 20808 | 23179 | 22264 | 21656 | 19943 | 18634 | 22369 | 23322 | 22007 | 22976
5751 | 5751 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 15 | 20273 | 18013 | 18959 | 16850 | 16230 | 21979 | 20877 | 19537 | 20292 | 17466 | 21043 | 23362 | 22369 | 21683 | 19929 | 18824 | 22641 | 23408 | 22041 | 22976
5752 | 5752 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 16 | 20734 | 18326 | 19270 | 17102 | 16684 | 22614 | 21075 | 19807 | 20537 | 17875 | 21383 | 24068 | 22481 | 21845 | 20038 | 19192 | 22896 | 23487 | 22180 | 23094
5753 | 5753 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 17 | 21106 | 18787 | 19624 | 17665 | 17427 | 22936 | 21360 | 20318 | 20960 | 18657 | 21973 | 24475 | 22730 | 22297 | 20638 | 19954 | 23450 | 23765 | 22734 | 23547
5754 | 5754 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 18 | 20949 | 18786 | 19618 | 17987 | 17837 | 22788 | 21333 | 20600 | 21162 | 19213 | 22341 | 24379 | 22836 | 22732 | 21328 | 20718 | 23885 | 23942 | 23316 | 24031
5755 | 5755 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 19 | 20275 | 18533 | 19206 | 17534 | 17492 | 22276 | 21102 | 20517 | 20931 | 18964 | 22186 | 24158 | 22992 | 22827 | 21403 | 20695 | 23823 | 24271 | 23678 | 24264
5756 | 5756 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 20 | 20004 | 18640 | 19265 | 17701 | 17712 | 22130 | 21391 | 20716 | 21187 | 19402 | 22493 | 24362 | 23704 | 23417 | 22178 | 21451 | 24463 | 25198 | 24510 | 24991
5757 | 5757 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 21 | 19639 | 18311 | 18983 | 17548 | 17661 | 21880 | 21210 | 20615 | 21186 | 19547 | 22426 | 24509 | 24003 | 23847 | 22700 | 21980 | 24742 | 25770 | 25136 | 25642
5758 | 5758 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 22 | 18391 | 17207 | 17895 | 16812 | 16823 | 20698 | 20206 | 19715 | 20302 | 18849 | 21417 | 23559 | 23285 | 23186 | 22322 | 21492 | 23910 | 25221 | 24638 | 25102
5759 | 5759 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 23 | 16950 | 15962 | 16639 | 15983 | 15907 | 19205 | 18913 | 18497 | 19108 | 17951 | 20108 | 22165 | 22099 | 22075 | 21592 | 20671 | 22670 | 24079 | 23595 | 24050
5760 | 5760 | 240 | 8 | 28 | Summer | 8 | 27 | Summer | 24 | 15820 | 14921 | 15554 | 15133 | 15048 | 18009 | 17820 | 17432 | 18009 | 17105 | 18966 | 21000 | 21068 | 21031 | 20732 | 19844 | 21719 | 23077 | 22627 | 23029
5761 | 5761 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 1 | 14935 | 14323 | 14571 | 14088 | 14462 | 17092 | 16613 | 16790 | 16945 | 16487 | 18548 | 20158 | 19920 | 19894 | 18590 | 19352 | 21426 | 21979 | 22076 | 21882
5762 | 5762 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 2 | 14426 | 13866 | 14108 | 13628 | 14113 | 16523 | 16085 | 16234 | 16372 | 16069 | 17971 | 19485 | 19272 | 19228 | 17997 | 18869 | 20750 | 21264 | 21316 | 21129
5763 | 5763 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 3 | 14115 | 13595 | 13813 | 13314 | 13933 | 16192 | 15747 | 15876 | 15974 | 15831 | 17606 | 19013 | 18764 | 18709 | 17518 | 18683 | 20265 | 20695 | 20728 | 20533
5764 | 5764 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 4 | 14046 | 13562 | 13649 | 13162 | 13941 | 16008 | 15581 | 15666 | 15621 | 15675 | 17297 | 18517 | 18248 | 18057 | 16974 | 18303 | 19696 | 19987 | 19993 | 19720
5765 | 5765 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 5 | 14384 | 13966 | 13669 | 13082 | 14287 | 16280 | 15813 | 15857 | 15453 | 15830 | 17323 | 18454 | 18077 | 17534 | 16478 | 18307 | 19423 | 19603 | 19603 | 19020
5766 | 5766 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 6 | 15122 | 14770 | 13716 | 12911 | 15084 | 16939 | 16380 | 16452 | 15292 | 16373 | 17854 | 18781 | 18173 | 17068 | 15902 | 18651 | 19671 | 19472 | 19539 | 18381
5767 | 5767 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 7 | 16104 | 15727 | 13921 | 12860 | 16081 | 17900 | 17136 | 17246 | 15229 | 17142 | 18456 | 19401 | 18560 | 16766 | 15427 | 19227 | 19986 | 19697 | 19808 | 17966
5768 | 5768 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 8 | 16896 | 16482 | 14706 | 13500 | 16936 | 18662 | 17763 | 17977 | 15898 | 17983 | 18976 | 19994 | 19034 | 17326 | 15873 | 19917 | 20361 | 20096 | 20368 | 18491
5769 | 5769 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 9 | 17304 | 16989 | 15487 | 14278 | 17503 | 19038 | 18070 | 18498 | 16633 | 18587 | 19324 | 20310 | 19220 | 18073 | 16564 | 20404 | 20644 | 20286 | 20861 | 19247
5770 | 5770 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 10 | 17649 | 17395 | 15966 | 14759 | 17983 | 19423 | 18342 | 18958 | 17227 | 19161 | 20007 | 20803 | 19594 | 18721 | 17175 | 20838 | 21362 | 20708 | 21471 | 19979
5771 | 5771 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 11 | 17912 | 17690 | 16288 | 15164 | 18396 | 19731 | 18609 | 19344 | 17658 | 19651 | 20551 | 21210 | 19974 | 19152 | 17658 | 21262 | 21908 | 21138 | 21999 | 20491
5772 | 5772 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 12 | 18219 | 17980 | 16581 | 15531 | 18790 | 20144 | 18889 | 19661 | 18022 | 20088 | 21010 | 21691 | 20308 | 19559 | 18080 | 21682 | 22390 | 21497 | 22409 | 20942
5773 | 5773 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 13 | 18492 | 18275 | 16671 | 15774 | 19142 | 20449 | 19265 | 19970 | 18127 | 20448 | 21389 | 22011 | 20708 | 19662 | 18337 | 21981 | 22781 | 21900 | 22754 | 21044
5774 | 5774 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 14 | 18613 | 18457 | 16806 | 16004 | 19430 | 20556 | 19370 | 20173 | 18246 | 20710 | 21697 | 22089 | 20778 | 19772 | 18537 | 22248 | 23059 | 21961 | 22909 | 21138
5775 | 5775 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 15 | 18754 | 18612 | 16881 | 16258 | 19734 | 20727 | 19504 | 20290 | 18287 | 20991 | 21974 | 22237 | 20876 | 19805 | 18771 | 22563 | 23316 | 22035 | 22954 | 21156
5776 | 5776 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 16 | 18991 | 18893 | 17109 | 16693 | 20119 | 20913 | 19763 | 20531 | 18451 | 21321 | 22644 | 22355 | 21050 | 19897 | 19117 | 22810 | 23996 | 22149 | 23050 | 21206
5777 | 5777 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 17 | 19243 | 19205 | 17629 | 17399 | 20667 | 21163 | 20228 | 20919 | 18942 | 21884 | 23146 | 22569 | 21568 | 20456 | 19831 | 23334 | 24537 | 22669 | 23463 | 21768
5778 | 5778 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 18 | 19158 | 19152 | 17877 | 17758 | 20758 | 21114 | 20452 | 21038 | 19427 | 22193 | 23069 | 22636 | 22054 | 21124 | 20582 | 23730 | 24672 | 23237 | 23934 | 22483
5779 | 5779 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 19 | 18824 | 18687 | 17354 | 17365 | 20372 | 20833 | 20298 | 20721 | 19186 | 21950 | 22954 | 22715 | 22213 | 21127 | 20506 | 23625 | 24745 | 23564 | 24140 | 22635
5780 | 5780 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 20 | 18879 | 18688 | 17462 | 17540 | 20472 | 21061 | 20433 | 20887 | 19512 | 22158 | 23529 | 23323 | 22828 | 21824 | 21201 | 24208 | 25617 | 24373 | 24836 | 23491
5781 | 5781 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 21 | 18509 | 18391 | 17284 | 17460 | 20119 | 20830 | 20274 | 20811 | 19551 | 22010 | 23575 | 23540 | 23153 | 22280 | 21686 | 24457 | 26073 | 24985 | 25482 | 24137
5782 | 5782 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 22 | 17374 | 17293 | 16532 | 16591 | 18915 | 19777 | 19310 | 19864 | 18942 | 20949 | 22553 | 22759 | 22483 | 21877 | 21163 | 23614 | 25280 | 24462 | 24929 | 23799
5783 | 5783 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 23 | 16085 | 16055 | 15709 | 15695 | 17558 | 18475 | 18087 | 18651 | 18113 | 19628 | 21192 | 21531 | 21358 | 21146 | 20338 | 22354 | 24023 | 23404 | 23878 | 23082
5784 | 5784 | 241 | 8 | 29 | Summer | 8 | 28 | Summer | 24 | 15073 | 14984 | 14855 | 14847 | 16386 | 17392 | 17015 | 17537 | 17263 | 18489 | 20078 | 20509 | 20354 | 20283 | 19506 | 21406 | 22972 | 22446 | 22867 | 22253
5785 | 5785 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 1 | 14010 | 14008 | 13837 | 14247 | 15709 | 16170 | 16324 | 16469 | 15756 | 17995 | 19418 | 19340 | 19721 | 18172 | 18990 | 21063 | 22399 | 21852 | 21690 | 19802
5786 | 5786 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 2 | 13564 | 13552 | 13393 | 13912 | 15227 | 15652 | 15786 | 15919 | 15253 | 17436 | 18797 | 18717 | 19042 | 17590 | 18515 | 20395 | 21687 | 21096 | 20945 | 19174
5787 | 5787 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 3 | 13306 | 13279 | 13097 | 13760 | 14976 | 15343 | 15454 | 15564 | 14892 | 17106 | 18338 | 18267 | 18557 | 17136 | 18352 | 19943 | 21112 | 20522 | 20365 | 18668
5788 | 5788 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 4 | 13273 | 13131 | 12959 | 13781 | 14919 | 15210 | 15293 | 15260 | 14610 | 16857 | 17943 | 17799 | 18035 | 16628 | 18001 | 19400 | 20436 | 19807 | 19562 | 18037
5789 | 5789 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 5 | 13655 | 13162 | 12895 | 14151 | 15291 | 15482 | 15540 | 15158 | 14385 | 16956 | 17938 | 17696 | 17883 | 16173 | 18041 | 19158 | 20184 | 19436 | 18871 | 17445
5790 | 5790 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 6 | 14452 | 13226 | 12753 | 14981 | 16158 | 16099 | 16209 | 15082 | 14040 | 17563 | 18463 | 17877 | 18052 | 15645 | 18426 | 19438 | 20439 | 19396 | 18247 | 16784
5791 | 5791 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 7 | 15465 | 13456 | 12729 | 16005 | 17066 | 16887 | 17060 | 15089 | 13853 | 18230 | 19171 | 18324 | 18478 | 15195 | 19022 | 19777 | 20949 | 19671 | 17830 | 16249
5792 | 5792 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 8 | 16103 | 14267 | 13396 | 16864 | 17788 | 17532 | 17807 | 15796 | 14460 | 18792 | 19927 | 18840 | 19115 | 15657 | 19732 | 20179 | 21532 | 20233 | 18343 | 16676
5793 | 5793 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 9 | 16427 | 15088 | 14278 | 17525 | 18316 | 17912 | 18410 | 16649 | 15271 | 19242 | 20446 | 19137 | 19702 | 16425 | 20301 | 20573 | 21978 | 20796 | 19181 | 17413
5794 | 5794 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 10 | 16547 | 15428 | 14639 | 17876 | 18765 | 18062 | 18732 | 17110 | 15730 | 19792 | 21036 | 19383 | 20132 | 16906 | 20608 | 21163 | 22614 | 21276 | 19782 | 17954
5795 | 5795 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 11 | 16757 | 15775 | 15068 | 18300 | 19226 | 18334 | 19135 | 17547 | 16247 | 20354 | 21642 | 19763 | 20645 | 17406 | 21052 | 21718 | 23258 | 21835 | 20313 | 18505
5796 | 5796 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 12 | 16989 | 16041 | 15416 | 18676 | 19614 | 18595 | 19437 | 17886 | 16638 | 20795 | 22191 | 20076 | 21004 | 17810 | 21456 | 22172 | 23842 | 22225 | 20742 | 18931
5797 | 5797 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 13 | 17327 | 16129 | 15652 | 19023 | 19994 | 18955 | 19750 | 17985 | 16891 | 21184 | 22618 | 20468 | 21339 | 18064 | 21756 | 22560 | 24230 | 22560 | 20842 | 19186
5798 | 5798 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 14 | 17476 | 16262 | 15899 | 19334 | 20330 | 19081 | 19956 | 18129 | 17120 | 21515 | 22944 | 20566 | 21510 | 18286 | 22040 | 22864 | 24523 | 22731 | 20954 | 19396
5799 | 5799 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 15 | 17585 | 16316 | 16127 | 19611 | 20597 | 19194 | 20047 | 18145 | 17331 | 21757 | 23209 | 20645 | 21556 | 18495 | 22329 | 23096 | 24804 | 22744 | 20952 | 19598
5800 | 5800 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 16 | 17902 | 16586 | 16606 | 20037 | 21226 | 19495 | 20343 | 18358 | 17763 | 22471 | 23520 | 20863 | 21746 | 18889 | 22621 | 23827 | 25071 | 22888 | 21041 | 19973
5801 | 5801 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 17 | 18310 | 17085 | 17292 | 20566 | 21643 | 19954 | 20710 | 18822 | 18481 | 22952 | 23889 | 21360 | 22138 | 19596 | 23142 | 24350 | 25532 | 23290 | 21587 | 20705
5802 | 5802 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 18 | 18262 | 17294 | 17584 | 20620 | 21532 | 20155 | 20782 | 19250 | 18998 | 22836 | 23861 | 21811 | 22524 | 20333 | 23525 | 24475 | 25487 | 23757 | 22299 | 21482
5803 | 5803 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 19 | 17951 | 16757 | 17158 | 20200 | 21136 | 19969 | 20419 | 18939 | 18666 | 22646 | 23763 | 21896 | 22523 | 20221 | 23375 | 24506 | 25544 | 23947 | 22439 | 21465
5804 | 5804 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 20 | 18020 | 16853 | 17306 | 20271 | 21395 | 20074 | 20560 | 19196 | 19026 | 23150 | 24397 | 22429 | 23037 | 20871 | 23933 | 25340 | 26553 | 24660 | 23293 | 22222
5805 | 5805 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 21 | 17679 | 16642 | 17195 | 19889 | 21087 | 19866 | 20409 | 19170 | 19106 | 23087 | 24413 | 22674 | 23392 | 21296 | 24130 | 25747 | 27032 | 25273 | 23928 | 22789
5806 | 5806 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 22 | 16545 | 15871 | 16307 | 18662 | 19829 | 18861 | 19406 | 18509 | 18349 | 22009 | 23426 | 21945 | 22677 | 20742 | 23248 | 24923 | 26305 | 24701 | 23591 | 22319
5807 | 5807 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 23 | 15317 | 15074 | 15417 | 17329 | 18397 | 17635 | 18183 | 17665 | 17461 | 20630 | 22071 | 20805 | 21562 | 19912 | 21985 | 23673 | 25054 | 23643 | 22886 | 21538
5808 | 5808 | 242 | 8 | 30 | Summer | 8 | 29 | Summer | 24 | 14296 | 14259 | 14564 | 16169 | 17244 | 16564 | 17065 | 16798 | 16616 | 19515 | 20859 | 19783 | 20525 | 19082 | 21032 | 22623 | 23904 | 22640 | 22059 | 20738
5809 | 5809 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 1 | 13662 | 13319 | 13995 | 15474 | 16506 | 15858 | 16022 | 15410 | 15986 | 18853 | 19723 | 19133 | 19393 | 18571 | 20655 | 22039 | 22997 | 21479 | 19668 | 20214
5810 | 5810 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 2 | 13229 | 12879 | 13685 | 15003 | 15970 | 15341 | 15496 | 14918 | 15587 | 18249 | 19026 | 18481 | 18735 | 18116 | 20009 | 21334 | 22210 | 20745 | 19045 | 19716
5811 | 5811 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 3 | 12959 | 12583 | 13522 | 14746 | 15604 | 15007 | 15142 | 14560 | 15357 | 17797 | 18533 | 18005 | 18227 | 17948 | 19552 | 20755 | 21753 | 20153 | 18525 | 19494
5812 | 5812 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 4 | 12951 | 12445 | 13561 | 14708 | 15487 | 14880 | 14881 | 14318 | 15258 | 17465 | 18099 | 17546 | 17632 | 17636 | 19040 | 20113 | 21058 | 19365 | 17897 | 19059
5813 | 5813 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 5 | 13385 | 12413 | 13954 | 15118 | 15794 | 15178 | 14842 | 14152 | 15481 | 17541 | 18011 | 17470 | 17184 | 17725 | 18861 | 19905 | 20680 | 18702 | 17324 | 19008
5814 | 5814 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 6 | 14207 | 12272 | 14806 | 16014 | 16636 | 15877 | 14823 | 13873 | 16090 | 18143 | 18379 | 17720 | 16784 | 18145 | 19167 | 20190 | 20789 | 18090 | 16662 | 19302
5815 | 5815 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 7 | 15188 | 12263 | 15870 | 16962 | 17678 | 16761 | 14892 | 13748 | 16905 | 18910 | 19013 | 18219 | 16525 | 18773 | 19539 | 20738 | 21143 | 17684 | 16129 | 19854
5816 | 5816 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 8 | 15959 | 12983 | 16759 | 17728 | 18624 | 17532 | 15643 | 14411 | 17783 | 19719 | 19863 | 18888 | 17127 | 19517 | 19992 | 21369 | 21826 | 18239 | 16588 | 20547
5817 | 5817 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 9 | 16555 | 13867 | 17479 | 18277 | 19262 | 18153 | 16531 | 15256 | 18514 | 20282 | 20597 | 19504 | 17991 | 20120 | 20421 | 21840 | 22601 | 19083 | 17351 | 21126
5818 | 5818 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 10 | 16882 | 14294 | 17885 | 18773 | 19801 | 18523 | 17026 | 15770 | 19005 | 20922 | 21247 | 19975 | 18560 | 20474 | 21064 | 22530 | 23288 | 19727 | 17954 | 21531
5819 | 5819 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 11 | 17134 | 14644 | 18249 | 19157 | 20242 | 18850 | 17381 | 16205 | 19448 | 21458 | 21885 | 20411 | 18950 | 20851 | 21557 | 23104 | 23935 | 20190 | 18433 | 21954
5820 | 5820 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 12 | 17366 | 14952 | 18577 | 19505 | 20682 | 19107 | 17665 | 16555 | 19825 | 21964 | 22303 | 20729 | 19296 | 21209 | 21976 | 23640 | 24359 | 20570 | 18819 | 22334
5821 | 5821 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 13 | 17701 | 15214 | 18959 | 19911 | 21138 | 19444 | 17794 | 16833 | 20221 | 22424 | 22776 | 21087 | 19438 | 21545 | 22392 | 24055 | 24828 | 20706 | 19103 | 22671
5822 | 5822 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 14 | 17852 | 15407 | 19215 | 20205 | 21437 | 19598 | 17889 | 17022 | 20469 | 22699 | 22996 | 21224 | 19518 | 21777 | 22644 | 24299 | 25073 | 20765 | 19261 | 22897
5823 | 5823 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 15 | 18025 | 15682 | 19536 | 20511 | 21763 | 19733 | 17949 | 17273 | 20756 | 23008 | 23248 | 21316 | 19565 | 22111 | 22923 | 24620 | 25178 | 20799 | 19501 | 23219
5824 | 5824 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 16 | 18373 | 16212 | 20006 | 21163 | 22188 | 20087 | 18215 | 17750 | 21170 | 23382 | 23575 | 21568 | 19749 | 22453 | 23698 | 24937 | 25293 | 20928 | 19905 | 23531
5825 | 5825 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 17 | 18667 | 16867 | 20517 | 21576 | 22592 | 20450 | 18675 | 18462 | 21708 | 23742 | 23920 | 21961 | 20295 | 22962 | 24219 | 25397 | 25573 | 21479 | 20634 | 24049
5826 | 5826 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 18 | 18565 | 17085 | 20471 | 21422 | 22428 | 20463 | 19023 | 18895 | 21959 | 23644 | 24145 | 22263 | 20904 | 23301 | 24285 | 25306 | 25985 | 22150 | 21379 | 24440
5827 | 5827 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 19 | 18049 | 16616 | 20015 | 20985 | 21975 | 20066 | 18645 | 18503 | 21649 | 23460 | 23937 | 22187 | 20823 | 23096 | 24259 | 25320 | 26054 | 22256 | 21338 | 24340
5828 | 5828 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 20 | 18022 | 16739 | 20044 | 21197 | 22239 | 20168 | 18847 | 18799 | 21780 | 23996 | 24465 | 22616 | 21446 | 23610 | 25039 | 26278 | 26924 | 23096 | 22085 | 24950
5829 | 5829 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 21 | 17684 | 16597 | 19633 | 20841 | 21849 | 19969 | 18768 | 18806 | 21542 | 23906 | 24511 | 22870 | 21820 | 23745 | 25393 | 26694 | 27390 | 23725 | 22647 | 25248
5830 | 5830 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 22 | 16579 | 15736 | 18384 | 19566 | 20598 | 18932 | 18081 | 18020 | 20433 | 22874 | 23458 | 22106 | 21369 | 22834 | 24548 | 25940 | 26562 | 23389 | 22186 | 24421
5831 | 5831 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 23 | 15359 | 14831 | 17058 | 18140 | 19148 | 17701 | 17234 | 17114 | 19110 | 21478 | 22051 | 20965 | 20625 | 21570 | 23293 | 24688 | 25218 | 22697 | 21396 | 23188
5832 | 5832 | 243 | 8 | 31 | Summer | 8 | 30 | Summer | 24 | 14331 | 14004 | 15900 | 17006 | 17895 | 16597 | 16362 | 16258 | 17976 | 20278 | 20851 | 19913 | 19770 | 20613 | 22242 | 23522 | 24199 | 21873 | 20596 | 22279
5833 | 5833 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 1 | 13286 | 14033 | 15178 | 16226 | 16669 | 15527 | 15041 | 16189 | 17384 | 19096 | 17968 | 18749 | 17737 | 20147 | 21573 | 22545 | 21285 | 19444 | 20437 | 21965
5834 | 5834 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 2 | 12861 | 13517 | 14731 | 15707 | 16067 | 15028 | 14569 | 15579 | 16852 | 18433 | 17388 | 18125 | 17174 | 19521 | 20898 | 21789 | 20609 | 18842 | 19714 | 21294
5835 | 5835 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 3 | 12592 | 13216 | 14501 | 15374 | 15718 | 14708 | 14245 | 15220 | 16547 | 17991 | 17019 | 17662 | 16741 | 19108 | 20365 | 21366 | 20262 | 18357 | 19195 | 20819
5836 | 5836 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 4 | 12445 | 13044 | 14470 | 15263 | 15568 | 14473 | 14026 | 14935 | 16338 | 17621 | 16648 | 17110 | 16256 | 18625 | 19748 | 20693 | 19608 | 17727 | 18521 | 20189
5837 | 5837 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 5 | 12484 | 13033 | 14898 | 15599 | 15805 | 14480 | 13906 | 14820 | 16510 | 17622 | 16589 | 16724 | 15850 | 18491 | 19580 | 20344 | 19193 | 17162 | 17942 | 19882
5838 | 5838 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 6 | 12559 | 13183 | 15852 | 16528 | 16555 | 14567 | 13750 | 14796 | 17202 | 18161 | 17080 | 16429 | 15385 | 18885 | 19940 | 20518 | 19314 | 16536 | 17431 | 20104
5839 | 5839 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 7 | 12774 | 13350 | 16814 | 17583 | 17428 | 14649 | 13656 | 14796 | 17910 | 18851 | 17707 | 16215 | 14948 | 19258 | 20476 | 20865 | 19689 | 15980 | 17079 | 20333
5840 | 5840 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 8 | 13556 | 13952 | 17551 | 18489 | 18312 | 15339 | 14274 | 15382 | 18476 | 19673 | 18246 | 16786 | 15403 | 19675 | 21062 | 21503 | 20105 | 16383 | 17504 | 20664
5841 | 5841 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 9 | 14286 | 14810 | 18054 | 19041 | 19005 | 16141 | 15057 | 16264 | 18889 | 20355 | 18751 | 17563 | 16122 | 20038 | 21474 | 22185 | 20506 | 17073 | 18264 | 20984
5842 | 5842 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 10 | 14707 | 15645 | 18585 | 19600 | 19590 | 16625 | 15571 | 17188 | 19538 | 20981 | 19234 | 18153 | 16708 | 20718 | 22200 | 22911 | 20901 | 17712 | 19304 | 21712
5843 | 5843 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 11 | 15033 | 16365 | 18969 | 20027 | 20143 | 16946 | 15965 | 17946 | 20052 | 21557 | 19607 | 18566 | 17168 | 21226 | 22800 | 23581 | 21253 | 18215 | 20166 | 22278
5844 | 5844 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 12 | 15265 | 16952 | 19336 | 20473 | 20527 | 17232 | 16322 | 18572 | 20464 | 21973 | 19927 | 18925 | 17554 | 21663 | 23360 | 24032 | 21585 | 18619 | 20835 | 22743
5845 | 5845 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 13 | 15345 | 17265 | 19698 | 20882 | 20899 | 17318 | 16555 | 18889 | 20837 | 22403 | 20230 | 19023 | 17793 | 22039 | 23736 | 24444 | 21879 | 18860 | 21139 | 23123
5846 | 5846 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 14 | 15426 | 17570 | 20006 | 21193 | 21148 | 17431 | 16761 | 19201 | 21135 | 22648 | 20422 | 19116 | 17981 | 22311 | 24006 | 24707 | 22060 | 19031 | 21419 | 23381
5847 | 5847 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 15 | 15475 | 17834 | 20273 | 21481 | 21371 | 17453 | 16977 | 19456 | 21364 | 22874 | 20593 | 19119 | 18178 | 22545 | 24279 | 24769 | 22202 | 19223 | 21646 | 23597
5848 | 5848 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 16 | 15747 | 18371 | 20813 | 21863 | 21726 | 17690 | 17414 | 19952 | 22061 | 23185 | 20784 | 19271 | 18558 | 23270 | 24549 | 24834 | 22269 | 19574 | 22058 | 24306
5849 | 5849 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 17 | 16286 | 19050 | 21273 | 22321 | 22097 | 18206 | 18178 | 20701 | 22584 | 23594 | 21219 | 19868 | 19308 | 23840 | 25055 | 25164 | 22694 | 20336 | 22864 | 24890
5850 | 5850 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 18 | 16480 | 19160 | 21178 | 22217 | 22172 | 18612 | 18654 | 21105 | 22460 | 23869 | 21600 | 20467 | 20032 | 23941 | 24998 | 25612 | 23241 | 21133 | 23559 | 25045
5851 | 5851 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 19 | 15960 | 18887 | 20736 | 21749 | 21787 | 18199 | 18221 | 20908 | 22246 | 23565 | 21576 | 20377 | 19912 | 23922 | 25023 | 25704 | 23465 | 21139 | 23681 | 25166
5852 | 5852 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 20 | 16074 | 19089 | 20945 | 22012 | 21976 | 18411 | 18516 | 21189 | 22694 | 24033 | 21951 | 20973 | 20543 | 24677 | 25962 | 26577 | 24264 | 21918 | 24475 | 26080
5853 | 5853 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 21 | 15840 | 18663 | 20563 | 21595 | 21654 | 18300 | 18492 | 20900 | 22553 | 23977 | 21978 | 21270 | 20911 | 24972 | 26323 | 27010 | 24741 | 22490 | 24767 | 26576
5854 | 5854 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 22 | 15078 | 17469 | 19285 | 20332 | 20382 | 17598 | 17685 | 19792 | 21449 | 22901 | 21118 | 20787 | 20341 | 24098 | 25543 | 26168 | 24139 | 22023 | 23960 | 25823
5855 | 5855 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 23 | 14284 | 16228 | 17843 | 18891 | 18897 | 16744 | 16768 | 18522 | 20032 | 21442 | 19956 | 20008 | 19488 | 22822 | 24257 | 24785 | 23070 | 21228 | 22848 | 24588
5856 | 5856 | 244 | 9 | 1 | Summer | 8 | 31 | Summer | 24 | 13524 | 15183 | 16692 | 17629 | 17655 | 15871 | 15895 | 17445 | 18925 | 20231 | 18934 | 19144 | 18646 | 21747 | 23085 | 23749 | 22261 | 20409 | 21820 | 23564
5857 | 5857 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 1 | 12696 | 14658 | 16006 | 16466 | 14888 | 14708 | 15908 | 17003 | 18267 | 17411 | 18045 | 17305 | 18595 | 21155 | 22188 | 20941 | 21199 | 20361 | 21874 | 23044
5858 | 5858 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 2 | 12255 | 14215 | 15492 | 15864 | 14418 | 14233 | 15290 | 16480 | 17677 | 16838 | 17440 | 16746 | 17905 | 20467 | 21419 | 20265 | 20496 | 19613 | 21181 | 22304
5859 | 5859 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 3 | 11981 | 13969 | 15161 | 15518 | 14167 | 13912 | 14940 | 16189 | 17268 | 16482 | 16982 | 16321 | 17452 | 19923 | 21002 | 19921 | 20074 | 19085 | 20678 | 21705
5860 | 5860 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 4 | 11847 | 13958 | 15081 | 15409 | 14107 | 13731 | 14698 | 16052 | 16995 | 16193 | 16530 | 15896 | 16937 | 19360 | 20370 | 19316 | 19368 | 18427 | 20075 | 20985
5861 | 5861 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 5 | 11813 | 14394 | 15432 | 15683 | 14378 | 13631 | 14617 | 16293 | 17153 | 16206 | 16152 | 15545 | 16535 | 19242 | 20059 | 18930 | 18650 | 17855 | 19766 | 20677
5862 | 5862 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 6 | 11683 | 15333 | 16340 | 16480 | 15227 | 13474 | 14617 | 17084 | 17882 | 16760 | 16016 | 15125 | 16176 | 19630 | 20240 | 19060 | 18130 | 17332 | 19970 | 20867
5863 | 5863 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 7 | 11675 | 16331 | 17424 | 17418 | 16235 | 13424 | 14686 | 17893 | 18723 | 17483 | 15990 | 14761 | 15973 | 20237 | 20653 | 19488 | 17795 | 17005 | 20240 | 21327
5864 | 5864 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 8 | 12379 | 17145 | 18371 | 18337 | 16894 | 14076 | 15331 | 18531 | 19540 | 18089 | 16507 | 15267 | 16496 | 20895 | 21342 | 19942 | 18218 | 17475 | 20603 | 21884
5865 | 5865 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 9 | 13117 | 17636 | 18880 | 18972 | 17345 | 14809 | 16170 | 18931 | 19993 | 18557 | 17132 | 15943 | 17228 | 21266 | 21974 | 20294 | 18771 | 18173 | 20878 | 22197
5866 | 5866 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 10 | 13588 | 18141 | 19451 | 19532 | 17774 | 15310 | 17096 | 19541 | 20647 | 19033 | 17773 | 16525 | 18225 | 21993 | 22693 | 20697 | 19316 | 19222 | 21608 | 22978
5867 | 5867 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 11 | 13929 | 18541 | 19873 | 20024 | 18072 | 15687 | 17831 | 19979 | 21121 | 19382 | 18296 | 16965 | 19016 | 22577 | 23345 | 21048 | 19796 | 20063 | 22165 | 23611
5868 | 5868 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 12 | 14281 | 18934 | 20370 | 20435 | 18365 | 16075 | 18488 | 20416 | 21665 | 19737 | 18698 | 17388 | 19702 | 23158 | 23830 | 21402 | 20183 | 20768 | 22661 | 24230
5869 | 5869 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 13 | 14503 | 19312 | 20778 | 20818 | 18653 | 16314 | 18809 | 20799 | 22082 | 20051 | 18950 | 17639 | 20017 | 23540 | 24245 | 21703 | 20420 | 21076 | 23052 | 24615
5870 | 5870 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 14 | 14728 | 19616 | 21113 | 21098 | 18889 | 16545 | 19145 | 21124 | 22396 | 20281 | 19079 | 17854 | 20336 | 23838 | 24536 | 21912 | 20531 | 21379 | 23332 | 24898
5871 | 5871 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 15 | 15013 | 19895 | 21442 | 21386 | 19130 | 16806 | 19444 | 21416 | 22719 | 20502 | 19296 | 18107 | 20612 | 24162 | 24646 | 22111 | 20733 | 21653 | 23593 | 25208
5872 | 5872 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 16 | 15493 | 20365 | 21820 | 21740 | 19401 | 17233 | 19927 | 22064 | 23056 | 20697 | 19589 | 18480 | 21040 | 24427 | 24703 | 22171 | 20928 | 22041 | 24283 | 25443
5873 | 5873 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 17 | 16163 | 20763 | 22239 | 22087 | 19773 | 17957 | 20628 | 22562 | 23448 | 21087 | 20087 | 19194 | 21797 | 24899 | 24997 | 22565 | 21435 | 22817 | 24826 | 25935
5874 | 5874 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 18 | 16406 | 20657 | 22103 | 22133 | 19837 | 18401 | 20980 | 22443 | 23390 | 21408 | 20514 | 19873 | 22407 | 24802 | 25420 | 23086 | 22086 | 23499 | 24972 | 25909
5875 | 5875 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 19 | 15926 | 20194 | 21587 | 21646 | 19530 | 17927 | 20726 | 22085 | 23097 | 21288 | 20480 | 19678 | 22361 | 24752 | 25447 | 23250 | 22334 | 23586 | 25065 | 26013
5876 | 5876 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 20 | 16049 | 20365 | 21803 | 21788 | 19608 | 18190 | 20961 | 22461 | 23568 | 21553 | 21000 | 20232 | 22979 | 25620 | 26261 | 23995 | 23144 | 24368 | 25960 | 27058
5877 | 5877 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 21 | 15887 | 19935 | 21354 | 21424 | 19239 | 18138 | 20628 | 22244 | 23393 | 21467 | 21147 | 20526 | 23053 | 25908 | 26633 | 24419 | 23732 | 24650 | 26440 | 27575
5878 | 5878 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 22 | 15031 | 18643 | 20073 | 20125 | 18128 | 17304 | 19492 | 21075 | 22318 | 20556 | 20558 | 19904 | 22140 | 25088 | 25755 | 23778 | 23386 | 23841 | 25669 | 26894
5879 | 5879 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 23 | 14113 | 17218 | 18615 | 18647 | 16872 | 16386 | 18210 | 19656 | 20889 | 19348 | 19684 | 19032 | 20949 | 23777 | 24356 | 22695 | 22625 | 22693 | 24423 | 25634
5880 | 5880 | 245 | 9 | 2 | Summer | 9 | 1 | Summer | 24 | 13323 | 16099 | 17354 | 17422 | 15787 | 15521 | 17128 | 18531 | 19675 | 18344 | 18909 | 18190 | 19912 | 22607 | 23327 | 21907 | 22074 | 21693 | 23403 | 24486
5881 | 5881 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 1 | 13439 | 15391 | 16190 | 14625 | 15063 | 15518 | 16592 | 17806 | 18515 | 17454 | 17603 | 18125 | 19712 | 21672 | 20492 | 20852 | 20342 | 21678 | 22851 | 23604
5882 | 5882 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 2 | 12933 | 14888 | 15606 | 14165 | 14573 | 14910 | 16080 | 17231 | 17864 | 16870 | 17006 | 17443 | 19092 | 20918 | 19831 | 20149 | 19678 | 20988 | 22114 | 22792
5883 | 5883 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 3 | 12642 | 14574 | 15281 | 13931 | 14248 | 14580 | 15814 | 16847 | 17450 | 16448 | 16569 | 17007 | 18692 | 20530 | 19512 | 19740 | 19295 | 20514 | 21538 | 22340
5884 | 5884 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 4 | 12487 | 14506 | 15188 | 13894 | 14070 | 14357 | 15713 | 16625 | 17154 | 16064 | 16150 | 16538 | 18262 | 19943 | 18943 | 19045 | 18667 | 19906 | 20824 | 21607
5885 | 5885 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 5 | 12470 | 14896 | 15493 | 14204 | 14046 | 14313 | 16011 | 16856 | 17222 | 15766 | 15844 | 16202 | 18173 | 19694 | 18606 | 18370 | 18048 | 19622 | 20541 | 21174
5886 | 5886 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 6 | 12601 | 15801 | 16322 | 15090 | 14261 | 14337 | 16855 | 17650 | 17813 | 15713 | 15746 | 15914 | 18605 | 19941 | 18789 | 17891 | 17665 | 19844 | 20735 | 21242
5887 | 5887 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 7 | 12780 | 16901 | 17305 | 16125 | 14524 | 14429 | 17731 | 18532 | 18582 | 15756 | 15701 | 15755 | 19056 | 20379 | 19249 | 17576 | 17440 | 20125 | 21201 | 21581
5888 | 5888 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 8 | 13436 | 17873 | 18241 | 16788 | 15181 | 15081 | 18410 | 19376 | 19465 | 16311 | 16224 | 16302 | 19536 | 21095 | 19737 | 18016 | 17872 | 20507 | 21769 | 22254
5889 | 5889 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 9 | 14312 | 18493 | 19009 | 17334 | 15992 | 16013 | 18925 | 19940 | 20180 | 17059 | 17026 | 17137 | 19969 | 21820 | 20187 | 18684 | 18602 | 20882 | 22183 | 23003
5890 | 5890 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 10 | 15037 | 18958 | 19452 | 17637 | 16431 | 16807 | 19404 | 20469 | 20678 | 17586 | 17773 | 18010 | 20523 | 22413 | 20466 | 19103 | 19231 | 21489 | 22847 | 23651
5891 | 5891 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 11 | 15776 | 19418 | 19968 | 17962 | 16914 | 17559 | 19860 | 20970 | 21258 | 18126 | 18462 | 18825 | 21046 | 23082 | 20834 | 19622 | 19884 | 22067 | 23505 | 24386
5892 | 5892 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 12 | 16377 | 19884 | 20361 | 18237 | 17255 | 18191 | 20273 | 21495 | 21705 | 18498 | 19070 | 19493 | 21501 | 23532 | 21172 | 19991 | 20483 | 22541 | 24105 | 24879
5893 | 5893 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 13 | 16695 | 20295 | 20746 | 18534 | 17505 | 18520 | 20664 | 21925 | 22132 | 18761 | 19450 | 19820 | 21892 | 23951 | 21481 | 20237 | 20841 | 22938 | 24497 | 25341
5894 | 5894 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 14 | 17028 | 20634 | 21044 | 18789 | 17670 | 18873 | 21006 | 22267 | 22418 | 18911 | 19767 | 20160 | 22205 | 24264 | 21703 | 20367 | 21139 | 23236 | 24797 | 25641
5895 | 5895 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 15 | 17317 | 20895 | 21287 | 19005 | 17874 | 19144 | 21275 | 22566 | 22661 | 19098 | 20025 | 20408 | 22456 | 24349 | 21877 | 20548 | 21396 | 23468 | 25077 | 25712
5896 | 5896 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 16 | 17873 | 21300 | 21672 | 19312 | 18256 | 19657 | 21927 | 22936 | 22988 | 19434 | 20474 | 20875 | 23199 | 24449 | 21979 | 20772 | 21755 | 24188 | 25342 | 25781
5897 | 5897 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 17 | 18499 | 21694 | 21988 | 19661 | 18649 | 20332 | 22395 | 23300 | 23341 | 19904 | 21039 | 21609 | 23711 | 24724 | 22354 | 21241 | 22376 | 24711 | 25813 | 26061
5898 | 5898 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 18 | 18571 | 21548 | 21956 | 19681 | 18888 | 20663 | 22255 | 23216 | 23563 | 20287 | 21523 | 22180 | 23780 | 25129 | 22855 | 21884 | 22957 | 24851 | 25779 | 26499
5899 | 5899 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 19 | 18249 | 21000 | 21442 | 19344 | 18606 | 20389 | 21861 | 22875 | 23163 | 20185 | 21403 | 22086 | 23679 | 25105 | 22974 | 22097 | 23061 | 24928 | 25870 | 26624
5900 | 5900 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 20 | 18418 | 21178 | 21539 | 19389 | 18798 | 20606 | 22180 | 23279 | 23541 | 20610 | 21927 | 22648 | 24357 | 25860 | 23667 | 22874 | 23866 | 25812 | 26904 | 27528
5901 | 5901 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 21 | 17969 | 20717 | 21152 | 18983 | 18559 | 20250 | 21917 | 23030 | 23394 | 20654 | 21967 | 22647 | 24570 | 26170 | 24037 | 23415 | 24258 | 26287 | 27413 | 28036
5902 | 5902 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 22 | 16770 | 19425 | 19840 | 17852 | 17708 | 19099 | 20719 | 21911 | 22252 | 20004 | 21158 | 21699 | 23638 | 25262 | 23368 | 23038 | 23641 | 25511 | 26732 | 27234
5903 | 5903 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 23 | 15551 | 17962 | 18376 | 16611 | 16765 | 17837 | 19295 | 20473 | 20789 | 19124 | 20050 | 20497 | 22332 | 23866 | 22283 | 22283 | 22633 | 24273 | 25486 | 25864
5904 | 5904 | 246 | 9 | 3 | Summer | 9 | 2 | Summer | 24 | 14556 | 16738 | 17128 | 15525 | 15911 | 16740 | 18140 | 19231 | 19593 | 18322 | 19063 | 19424 | 21258 | 22818 | 21450 | 21699 | 21824 | 23229 | 24324 | 24847
5905 | 5905 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 1 | 14034 | 15586 | 14361 | 14834 | 15079 | 16193 | 17398 | 18047 | 16775 | 17122 | 17568 | 19190 | 20623 | 19988 | 20428 | 20027 | 20111 | 22677 | 23437 | 21962
5906 | 5906 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 2 | 13601 | 15034 | 13940 | 14362 | 14567 | 15710 | 16855 | 17422 | 16227 | 16562 | 16931 | 18599 | 19956 | 19362 | 19757 | 19382 | 19372 | 21954 | 22647 | 21279
5907 | 5907 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 3 | 13342 | 14682 | 13691 | 14018 | 14205 | 15433 | 16460 | 17001 | 15889 | 16120 | 16489 | 18195 | 19445 | 19036 | 19337 | 18981 | 18837 | 21359 | 22166 | 20879
5908 | 5908 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 4 | 13331 | 14598 | 13681 | 13866 | 14006 | 15362 | 16288 | 16760 | 15667 | 15759 | 16078 | 17831 | 18939 | 18520 | 18698 | 18383 | 18200 | 20668 | 21449 | 20197
5909 | 5909 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 5 | 13793 | 14948 | 14016 | 13875 | 13931 | 15700 | 16568 | 16905 | 15768 | 15517 | 15801 | 17818 | 18893 | 18244 | 18069 | 17800 | 17663 | 20399 | 21031 | 19738
5910 | 5910 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 6 | 14726 | 15780 | 14931 | 14111 | 14057 | 16578 | 17415 | 17565 | 16398 | 15483 | 15571 | 18307 | 19334 | 18479 | 17632 | 17439 | 17158 | 20626 | 21110 | 19796
5911 | 5911 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 7 | 15727 | 16776 | 16015 | 14409 | 14296 | 17498 | 18356 | 18407 | 17186 | 15494 | 15463 | 18819 | 19996 | 18973 | 17351 | 17231 | 16847 | 21100 | 21433 | 20172
5912 | 5912 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 8 | 16596 | 17758 | 16712 | 15089 | 14978 | 18223 | 19237 | 19343 | 17846 | 16061 | 16034 | 19367 | 20699 | 19496 | 17824 | 17688 | 17340 | 21694 | 22124 | 20640
5913 | 5913 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 9 | 17217 | 18537 | 17314 | 15938 | 15867 | 18768 | 19855 | 20113 | 18444 | 16922 | 16912 | 19842 | 21219 | 19986 | 18532 | 18467 | 18182 | 22150 | 22891 | 21124
5914 | 5914 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 10 | 17658 | 19033 | 17674 | 16431 | 16588 | 19294 | 20420 | 20662 | 18850 | 17721 | 17818 | 20458 | 21879 | 20303 | 18999 | 19148 | 19156 | 22866 | 23593 | 21486
5915 | 5915 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 11 | 18013 | 19466 | 17940 | 16849 | 17157 | 19668 | 20852 | 21170 | 19151 | 18345 | 18565 | 20909 | 22420 | 20600 | 19452 | 19734 | 19962 | 23460 | 24261 | 21831
5916 | 5916 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 12 | 18350 | 19819 | 18173 | 17145 | 17684 | 20034 | 21327 | 21570 | 19443 | 18910 | 19184 | 21316 | 22944 | 20897 | 19778 | 20289 | 20602 | 24001 | 24714 | 22169
5917 | 5917 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 13 | 18762 | 20237 | 18498 | 17428 | 18084 | 20448 | 21787 | 22023 | 19792 | 19320 | 19547 | 21740 | 23367 | 21237 | 20055 | 20683 | 20951 | 24433 | 25194 | 22521
5918 | 5918 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 14 | 19018 | 20502 | 18703 | 17550 | 18365 | 20746 | 22083 | 22271 | 19994 | 19592 | 19841 | 22010 | 23635 | 21423 | 20140 | 20943 | 21222 | 24675 | 25447 | 22698
5919 | 5919 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 15 | 19298 | 20773 | 18952 | 17788 | 18678 | 21050 | 22414 | 22551 | 20228 | 19887 | 20133 | 22300 | 23970 | 21637 | 20360 | 21236 | 21504 | 24988 | 25552 | 22887
5920 | 5920 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 16 | 19816 | 21182 | 19317 | 18228 | 19216 | 21736 | 22845 | 22947 | 20513 | 20396 | 20668 | 23072 | 24317 | 21804 | 20645 | 21645 | 21970 | 25302 | 25672 | 23004
5921 | 5921 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 17 | 20195 | 21512 | 19663 | 18619 | 19801 | 22224 | 23212 | 23297 | 20880 | 20960 | 21398 | 23581 | 24760 | 22184 | 21134 | 22274 | 22718 | 25775 | 25966 | 23384
5922 | 5922 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 18 | 20060 | 21391 | 19563 | 18771 | 20026 | 22046 | 23070 | 23410 | 21125 | 21355 | 21886 | 23590 | 24607 | 22613 | 21709 | 22797 | 23352 | 25698 | 26356 | 23877
5923 | 5923 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 19 | 19559 | 20832 | 19173 | 18446 | 19648 | 21593 | 22664 | 22933 | 20919 | 21153 | 21712 | 23412 | 24481 | 22661 | 21862 | 22846 | 23406 | 25757 | 26447 | 24074
5924 | 5924 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 20 | 19686 | 20899 | 19162 | 18590 | 19915 | 21857 | 23003 | 23228 | 21090 | 21587 | 22201 | 24001 | 25266 | 23283 | 22579 | 23608 | 24166 | 26768 | 27337 | 24857
5925 | 5925 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 21 | 19230 | 20463 | 18712 | 18307 | 19650 | 21544 | 22690 | 22999 | 20912 | 21523 | 22113 | 24122 | 25473 | 23570 | 23048 | 23954 | 24437 | 27247 | 27828 | 25357
5926 | 5926 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 22 | 17948 | 19174 | 17549 | 17437 | 18638 | 20313 | 21515 | 21823 | 19944 | 20670 | 21118 | 23161 | 24595 | 22865 | 22638 | 23320 | 23624 | 26539 | 27029 | 24769
5927 | 5927 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 23 | 16539 | 17705 | 16304 | 16499 | 17489 | 18883 | 20057 | 20324 | 18729 | 19538 | 19898 | 21841 | 23282 | 21766 | 21866 | 22296 | 22489 | 25307 | 25656 | 23718
5928 | 5928 | 247 | 9 | 4 | Summer | 9 | 3 | Summer | 24 | 15433 | 16501 | 15229 | 15660 | 16490 | 17734 | 18811 | 19113 | 17710 | 18575 | 18850 | 20757 | 22093 | 20940 | 21291 | 21498 | 21450 | 24147 | 24658 | 22937
5929 | 5929 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 1 | 14737 | 13732 | 14523 | 14848 | 15054 | 16920 | 17577 | 16253 | 16833 | 17058 | 19266 | 20040 | 21114 | 19904 | 19634 | 19752 | 22320 | 23221 | 21779 | 21816
5930 | 5930 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 2 | 14265 | 13329 | 14072 | 14355 | 14481 | 16384 | 16962 | 15734 | 16287 | 16430 | 18639 | 19408 | 20395 | 19257 | 18998 | 19034 | 21606 | 22438 | 21090 | 21108
5931 | 5931 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 3 | 13954 | 13102 | 13763 | 14010 | 14150 | 16021 | 16578 | 15428 | 15887 | 16025 | 18183 | 18917 | 20025 | 18879 | 18629 | 18520 | 21193 | 21977 | 20715 | 20659
5932 | 5932 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 4 | 13909 | 13110 | 13636 | 13836 | 13950 | 15886 | 16386 | 15266 | 15566 | 15666 | 17818 | 18471 | 19506 | 18288 | 18069 | 17906 | 20582 | 21265 | 20040 | 19913
5933 | 5933 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 5 | 14301 | 13473 | 13694 | 13805 | 13909 | 16256 | 16642 | 15496 | 15326 | 15536 | 17889 | 18469 | 19310 | 17693 | 17499 | 17377 | 20336 | 20845 | 19575 | 19136
5934 | 5934 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 6 | 15221 | 14411 | 13973 | 13973 | 13943 | 17161 | 17377 | 16225 | 15351 | 15385 | 18571 | 18994 | 19625 | 17319 | 17189 | 16909 | 20700 | 20948 | 19634 | 18583
5935 | 5935 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 7 | 16336 | 15544 | 14334 | 14265 | 14042 | 18172 | 18306 | 17127 | 15456 | 15367 | 19371 | 19725 | 20110 | 17082 | 17016 | 16619 | 21249 | 21291 | 20025 | 18221
5936 | 5936 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 8 | 17394 | 16308 | 15100 | 15005 | 14769 | 19135 | 19319 | 17877 | 16119 | 16030 | 19921 | 20521 | 20933 | 17640 | 17545 | 17189 | 21652 | 22048 | 20558 | 18716
5937 | 5937 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 9 | 18085 | 16910 | 15991 | 15918 | 15752 | 19781 | 20111 | 18521 | 16945 | 16942 | 20398 | 21078 | 21720 | 18377 | 18354 | 18042 | 22022 | 22841 | 21066 | 19413
5938 | 5938 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 10 | 18516 | 17172 | 16404 | 16549 | 16483 | 20250 | 20574 | 18841 | 17431 | 17773 | 20970 | 21636 | 22275 | 18744 | 18935 | 18919 | 22668 | 23453 | 21330 | 19838
5939 | 5939 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 11 | 18968 | 17514 | 16901 | 17200 | 17219 | 20755 | 21160 | 19234 | 17956 | 18615 | 21519 | 22227 | 22908 | 19244 | 19573 | 19780 | 23255 | 24173 | 21728 | 20388
5940 | 5940 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 12 | 19350 | 17745 | 17189 | 17717 | 17785 | 21211 | 21544 | 19513 | 18270 | 19227 | 21913 | 22737 | 23307 | 19563 | 20119 | 20416 | 23675 | 24602 | 22057 | 20717
5941 | 5941 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 13 | 19736 | 18025 | 17400 | 18050 | 18090 | 21592 | 21903 | 19776 | 18508 | 19496 | 22210 | 23112 | 23695 | 19794 | 20469 | 20716 | 23925 | 25027 | 22358 | 20946
5942 | 5942 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 14 | 20033 | 18269 | 17558 | 18359 | 18423 | 21918 | 22180 | 20012 | 18640 | 19824 | 22473 | 23411 | 23994 | 19911 | 20758 | 21020 | 24222 | 25309 | 22562 | 21044
5943 | 5943 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 15 | 20313 | 18510 | 17798 | 18676 | 18723 | 22261 | 22475 | 20261 | 18856 | 20143 | 22690 | 23738 | 24107 | 20133 | 21052 | 21297 | 24278 | 25399 | 22738 | 21251
5944 | 5944 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 16 | 20759 | 18878 | 18230 | 19219 | 19304 | 22692 | 22876 | 20564 | 19246 | 20681 | 23337 | 24097 | 24261 | 20421 | 21465 | 21775 | 24748 | 25502 | 22848 | 21507
5945 | 5945 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 17 | 21157 | 19217 | 18600 | 19798 | 20001 | 23051 | 23218 | 20935 | 19728 | 21407 | 23736 | 24541 | 24550 | 20885 | 22071 | 22524 | 25142 | 25783 | 23218 | 21997
5946 | 5946 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 18 | 20964 | 19008 | 18611 | 19904 | 20246 | 22808 | 23171 | 20983 | 20015 | 21707 | 23571 | 24346 | 24866 | 21439 | 22577 | 23127 | 25084 | 26166 | 23701 | 22598
5947 | 5947 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 19 | 20391 | 18583 | 18242 | 19488 | 19954 | 22344 | 22619 | 20678 | 19844 | 21428 | 23393 | 24169 | 24770 | 21553 | 22611 | 23156 | 25132 | 26251 | 23897 | 22856
5948 | 5948 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 20 | 20509 | 18549 | 18346 | 19722 | 20137 | 22637 | 22869 | 20777 | 20168 | 21837 | 23889 | 24864 | 25438 | 22211 | 23336 | 23883 | 26011 | 27134 | 24672 | 23664
5949 | 5949 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 21 | 20022 | 18083 | 18041 | 19422 | 19769 | 22284 | 22604 | 20519 | 20114 | 21683 | 23712 | 24981 | 25665 | 22619 | 23641 | 24120 | 26237 | 27627 | 25173 | 24285
5950 | 5950 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 22 | 18716 | 16908 | 17149 | 18391 | 18613 | 21069 | 21379 | 19489 | 19421 | 20644 | 22677 | 24076 | 24731 | 22165 | 22968 | 23280 | 25417 | 26834 | 24582 | 23956
5951 | 5951 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 23 | 17238 | 15657 | 16194 | 17241 | 17335 | 19594 | 19860 | 18233 | 18511 | 19395 | 21299 | 22720 | 23327 | 21362 | 21920 | 22121 | 24175 | 25452 | 23518 | 23208
5952 | 5952 | 248 | 9 | 5 | Summer | 9 | 4 | Summer | 24 | 16040 | 14599 | 15354 | 16253 | 16265 | 18341 | 18634 | 17196 | 17702 | 18348 | 20147 | 21510 | 22287 | 20784 | 21122 | 21084 | 23211 | 24449 | 22767 | 22683
5953 | 5953 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 1 | 14931 | 14026 | 14674 | 14944 | 16418 | 17244 | 15938 | 16520 | 16587 | 18901 | 19589 | 20536 | 19425 | 19213 | 19396 | 21943 | 22612 | 21575 | 21663 | 20868
5954 | 5954 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 2 | 14399 | 13577 | 14204 | 14380 | 15894 | 16649 | 15440 | 15995 | 16049 | 18294 | 19013 | 19830 | 18824 | 18591 | 18689 | 21248 | 21888 | 20892 | 20951 | 20199
5955 | 5955 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 3 | 14066 | 13333 | 13938 | 14137 | 15543 | 16391 | 15278 | 15748 | 15640 | 18023 | 18750 | 19483 | 18535 | 18239 | 18189 | 20854 | 21417 | 20524 | 20507 | 19799
5956 | 5956 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 4 | 13990 | 13207 | 13779 | 13958 | 15424 | 16246 | 15169 | 15493 | 15327 | 17734 | 18458 | 19020 | 18065 | 17708 | 17598 | 20265 | 20772 | 19855 | 19762 | 19142
5957 | 5957 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 5 | 14369 | 13242 | 13709 | 13931 | 15762 | 16457 | 15369 | 15309 | 15214 | 17774 | 18443 | 18885 | 17846 | 17180 | 17103 | 20049 | 20498 | 19411 | 18993 | 18466
5958 | 5958 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 6 | 15230 | 13541 | 13893 | 13991 | 16776 | 17224 | 16154 | 15416 | 15256 | 18522 | 19188 | 19288 | 18155 | 16913 | 16673 | 20451 | 20920 | 19498 | 18450 | 18058
5959 | 5959 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 7 | 16243 | 13883 | 14179 | 14104 | 17915 | 18136 | 17063 | 15583 | 15338 | 19335 | 20140 | 19829 | 18679 | 16750 | 16388 | 21018 | 21566 | 19876 | 18072 | 17804
5960 | 5960 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 8 | 17290 | 14686 | 14948 | 14843 | 18634 | 19156 | 17850 | 16289 | 15978 | 19942 | 20862 | 20686 | 19298 | 17296 | 16972 | 21436 | 22112 | 20409 | 18573 | 18308
5961 | 5961 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 9 | 18104 | 15629 | 15932 | 15863 | 19200 | 19988 | 18550 | 17176 | 16915 | 20484 | 21385 | 21518 | 19857 | 18158 | 17895 | 21852 | 22613 | 20947 | 19322 | 19146
5962 | 5962 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 10 | 18497 | 16040 | 16543 | 16572 | 19657 | 20411 | 18837 | 17635 | 17623 | 21021 | 21927 | 22040 | 20068 | 18723 | 18758 | 22482 | 23185 | 21206 | 19735 | 19766
5963 | 5963 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 11 | 18940 | 16444 | 17116 | 17249 | 20058 | 20886 | 19115 | 18089 | 18299 | 21436 | 22374 | 22614 | 20369 | 19304 | 19563 | 23026 | 23752 | 21551 | 20233 | 20393
5964 | 5964 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 12 | 19260 | 16703 | 17598 | 17792 | 20377 | 21227 | 19355 | 18378 | 18822 | 21802 | 22824 | 22994 | 20628 | 19817 | 20163 | 23422 | 24277 | 21842 | 20538 | 20923
5965 | 5965 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 13 | 19605 | 16891 | 17922 | 18067 | 20682 | 21569 | 19597 | 18568 | 19139 | 22092 | 23149 | 23378 | 20909 | 20163 | 20460 | 23671 | 24617 | 22130 | 20761 | 21268
5966 | 5966 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 14 | 19895 | 17070 | 18241 | 18419 | 20956 | 21871 | 19866 | 18743 | 19434 | 22406 | 23391 | 23670 | 21122 | 20443 | 20753 | 23957 | 24882 | 22319 | 20847 | 21533
5967 | 5967 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 15 | 20195 | 17262 | 18523 | 18687 | 21204 | 22090 | 20027 | 18884 | 19779 | 22498 | 23440 | 23826 | 21373 | 20769 | 21052 | 24054 | 25009 | 22539 | 21083 | 21848
5968 | 5968 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 16 | 20615 | 17644 | 19005 | 19191 | 21790 | 22388 | 20221 | 19147 | 20309 | 22973 | 23517 | 24001 | 21567 | 21199 | 21545 | 24523 | 25116 | 22662 | 21347 | 22249
5969 | 5969 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 17 | 20927 | 18029 | 19575 | 19863 | 22170 | 22715 | 20575 | 19593 | 20873 | 23342 | 23769 | 24273 | 21937 | 21823 | 22310 | 24919 | 25499 | 23047 | 21831 | 22890
5970 | 5970 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 18 | 20745 | 18062 | 19685 | 20082 | 21904 | 22764 | 20689 | 19823 | 21117 | 23280 | 23561 | 24563 | 22335 | 22317 | 22912 | 24865 | 25406 | 23533 | 22444 | 23426
5971 | 5971 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 19 | 20148 | 17709 | 19282 | 19782 | 21506 | 22243 | 20398 | 19605 | 20818 | 23104 | 23485 | 24413 | 22318 | 22325 | 22926 | 24887 | 25602 | 23726 | 22696 | 23545
5972 | 5972 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 20 | 20196 | 17800 | 19495 | 19959 | 21728 | 22468 | 20451 | 19878 | 21191 | 23516 | 24015 | 25022 | 22876 | 23019 | 23629 | 25746 | 26394 | 24506 | 23516 | 24345
5973 | 5973 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 21 | 19741 | 17461 | 19166 | 19563 | 21203 | 22158 | 20135 | 19749 | 21058 | 23243 | 23884 | 25158 | 23092 | 23263 | 23811 | 25929 | 26713 | 24997 | 24125 | 24754
5974 | 5974 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 22 | 18454 | 16575 | 18125 | 18382 | 19917 | 20905 | 19078 | 18999 | 20165 | 22138 | 22875 | 24170 | 22346 | 22570 | 22953 | 25076 | 25904 | 24410 | 23799 | 24147
5975 | 5975 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 23 | 17003 | 15635 | 16985 | 17119 | 18476 | 19407 | 17814 | 18070 | 19018 | 20752 | 21525 | 22729 | 21220 | 21523 | 21788 | 23801 | 24623 | 23346 | 23062 | 23144
5976 | 5976 | 249 | 9 | 6 | Summer | 9 | 5 | Summer | 24 | 15818 | 14829 | 16053 | 16134 | 17247 | 18272 | 16867 | 17375 | 18035 | 19743 | 20494 | 21675 | 20379 | 20707 | 20734 | 22838 | 23561 | 22566 | 22525 | 22365
5977 | 5977 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 1 | 13042 | 14012 | 14576 | 16162 | 16472 | 15349 | 15974 | 16244 | 16607 | 18922 | 19545 | 18709 | 19283 | 18880 | 21436 | 22117 | 22618 | 21363 | 20619 | 20520
5978 | 5978 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 2 | 12656 | 13550 | 14030 | 15641 | 15934 | 14866 | 15462 | 15716 | 16002 | 18323 | 18951 | 18120 | 18656 | 18187 | 20751 | 21408 | 21912 | 20656 | 19953 | 19781
5979 | 5979 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 3 | 12493 | 13284 | 13789 | 15395 | 15657 | 14712 | 15224 | 15471 | 15772 | 18020 | 18642 | 17871 | 18302 | 17710 | 20380 | 20972 | 21476 | 20226 | 19558 | 19251
5980 | 5980 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 4 | 12520 | 13135 | 13632 | 15310 | 15565 | 14642 | 15013 | 15226 | 15487 | 17726 | 18222 | 17469 | 17763 | 17163 | 19828 | 20365 | 20755 | 19499 | 18912 | 18582
5981 | 5981 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 5 | 12874 | 13102 | 13629 | 15631 | 15894 | 14898 | 14896 | 15083 | 15317 | 17780 | 18237 | 17336 | 17239 | 16721 | 19673 | 20142 | 20391 | 18762 | 18259 | 17996
5982 | 5982 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 6 | 13815 | 13281 | 13693 | 16656 | 16999 | 15701 | 15048 | 15172 | 15213 | 18627 | 18919 | 17719 | 16923 | 16319 | 20100 | 20590 | 20719 | 18221 | 17842 | 17459
5983 | 5983 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 7 | 14940 | 13593 | 13843 | 17815 | 18183 | 16641 | 15280 | 15289 | 15193 | 19613 | 19699 | 18329 | 16720 | 16066 | 20693 | 21260 | 21272 | 17856 | 17591 | 17122
5984 | 5984 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 8 | 15755 | 14397 | 14627 | 18605 | 19045 | 17468 | 16043 | 16006 | 15922 | 20353 | 20343 | 19013 | 17333 | 16691 | 21176 | 21864 | 21792 | 18394 | 18125 | 17712
5985 | 5985 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 9 | 16400 | 15390 | 15697 | 19188 | 19698 | 18171 | 16956 | 16976 | 16913 | 20924 | 20908 | 19607 | 18157 | 17638 | 21623 | 22406 | 22327 | 19177 | 18992 | 18631
5986 | 5986 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 10 | 16722 | 16035 | 16421 | 19623 | 20174 | 18421 | 17356 | 17596 | 17782 | 21321 | 21255 | 19889 | 18590 | 18575 | 22335 | 23057 | 22747 | 19666 | 19694 | 19628
5987 | 5987 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 11 | 16946 | 16543 | 17026 | 19881 | 20519 | 18597 | 17697 | 18086 | 18457 | 21645 | 21649 | 20116 | 18985 | 19322 | 22819 | 23562 | 23234 | 20106 | 20266 | 20423
5988 | 5988 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 12 | 17193 | 17054 | 17594 | 20228 | 20970 | 18847 | 17999 | 18623 | 19081 | 22131 | 21957 | 20412 | 19317 | 19964 | 23259 | 24113 | 23575 | 20451 | 20839 | 21087
5989 | 5989 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 13 | 17466 | 17385 | 17887 | 20545 | 21365 | 19111 | 18218 | 18964 | 19340 | 22549 | 22245 | 20690 | 19543 | 20261 | 23500 | 24443 | 23867 | 20672 | 21179 | 21376
5990 | 5990 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 14 | 17743 | 17711 | 18235 | 20846 | 21661 | 19367 | 18379 | 19290 | 19733 | 22816 | 22454 | 20927 | 19675 | 20581 | 23817 | 24732 | 24038 | 20784 | 21469 | 21684
5991 | 5991 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 15 | 17962 | 18061 | 18582 | 21089 | 21872 | 19651 | 18654 | 19633 | 19938 | 23116 | 22648 | 21197 | 19933 | 20894 | 23916 | 24868 | 24200 | 21020 | 21784 | 21988
5992 | 5992 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 16 | 18278 | 18606 | 19159 | 21614 | 22167 | 19963 | 19041 | 20124 | 20319 | 23424 | 22917 | 21396 | 20224 | 21380 | 24399 | 24968 | 24371 | 21281 | 22174 | 22464
5993 | 5993 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 17 | 18583 | 19124 | 19789 | 21956 | 22417 | 20287 | 19449 | 20621 | 20973 | 23746 | 23095 | 21746 | 20672 | 22101 | 24750 | 25317 | 24618 | 21724 | 22776 | 23202
5994 | 5994 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 18 | 18328 | 19123 | 19876 | 21698 | 22156 | 20316 | 19570 | 20864 | 21318 | 23524 | 23153 | 22041 | 21149 | 22638 | 24616 | 25157 | 24794 | 22271 | 23251 | 23779
5995 | 5995 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 19 | 17819 | 18634 | 19464 | 21241 | 21783 | 19907 | 19227 | 20508 | 20974 | 23336 | 23090 | 21871 | 21135 | 22530 | 24505 | 25249 | 25009 | 22425 | 23269 | 23769
5996 | 5996 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 20 | 17750 | 18801 | 19585 | 21401 | 21903 | 19908 | 19429 | 20808 | 21317 | 23698 | 23733 | 22326 | 21709 | 23161 | 25296 | 25982 | 26011 | 23217 | 24054 | 24508
5997 | 5997 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 21 | 17265 | 18449 | 19170 | 20848 | 21368 | 19561 | 19254 | 20618 | 21078 | 23464 | 23595 | 22457 | 22030 | 23287 | 25435 | 26255 | 26308 | 23821 | 24465 | 24804
5998 | 5998 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 22 | 16089 | 17387 | 17964 | 19544 | 20031 | 18466 | 18456 | 19674 | 19995 | 22345 | 22605 | 21656 | 21534 | 22396 | 24553 | 25399 | 25560 | 23479 | 23851 | 23986
5999 | 5999 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 23 | 14848 | 16259 | 16701 | 18094 | 18542 | 17196 | 17510 | 18505 | 18738 | 20944 | 21327 | 20491 | 20721 | 21221 | 23259 | 24133 | 24391 | 22733 | 22836 | 22840
6000 | 6000 | 250 | 9 | 7 | Summer | 9 | 6 | Summer | 24 | 13862 | 15326 | 15702 | 16956 | 17309 | 16234 | 16791 | 17646 | 17827 | 19811 | 20311 | 19648 | 20122 | 20171 | 22292 | 23054 | 23395 | 22193 | 22069 | 21820
6001 | 6001 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 1 | 13144 | 13297 | 15751 | 16103 | 16309 | 15392 | 15756 | 15492 | 18064 | 18833 | 19380 | 18607 | 18540 | 20846 | 21579 | 22126 | 22486 | 20329 | 19813 | 22674
6002 | 6002 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 2 | 12727 | 13002 | 15264 | 15589 | 15824 | 14907 | 15253 | 15150 | 17489 | 18271 | 18770 | 18002 | 17949 | 20199 | 20900 | 21454 | 21788 | 19682 | 19338 | 21986
6003 | 6003 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 3 | 12487 | 12901 | 15005 | 15301 | 15559 | 14660 | 14998 | 15084 | 17221 | 17979 | 18441 | 17667 | 17606 | 19836 | 20469 | 21026 | 21316 | 19281 | 19129 | 21555
6004 | 6004 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 4 | 12366 | 12965 | 14927 | 15218 | 15414 | 14468 | 14777 | 15041 | 16981 | 17617 | 18032 | 17171 | 17116 | 19318 | 19892 | 20334 | 20606 | 18639 | 18698 | 20889
6005 | 6005 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 5 | 12415 | 13350 | 15240 | 15553 | 15710 | 14367 | 14651 | 15296 | 17086 | 17685 | 17912 | 16700 | 16629 | 19189 | 19689 | 19986 | 20268 | 17973 | 18610 | 20584
6006 | 6006 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 6 | 12724 | 14216 | 16288 | 16699 | 16720 | 14573 | 14811 | 16048 | 17898 | 18480 | 18371 | 16478 | 16415 | 19686 | 20203 | 20366 | 20387 | 17591 | 18933 | 20910
6007 | 6007 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 7 | 13103 | 15270 | 17496 | 17928 | 17851 | 14851 | 14992 | 16971 | 18788 | 19347 | 18939 | 16356 | 16312 | 20337 | 20922 | 20944 | 20690 | 17359 | 19482 | 21430
6008 | 6008 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 8 | 13982 | 16333 | 18338 | 18819 | 18664 | 15651 | 15750 | 18008 | 19490 | 20045 | 19410 | 17030 | 16929 | 20849 | 21570 | 21492 | 20982 | 17920 | 20310 | 21868
6009 | 6009 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 9 | 15223 | 17431 | 19224 | 19738 | 19556 | 16840 | 17009 | 19062 | 20320 | 20899 | 19921 | 18148 | 18105 | 21582 | 22401 | 22306 | 21464 | 19061 | 21260 | 22561
6010 | 6010 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 10 | 15980 | 18076 | 19990 | 20435 | 20221 | 17550 | 17939 | 19673 | 21086 | 21537 | 20245 | 18885 | 19055 | 22595 | 23355 | 23032 | 21888 | 20064 | 21968 | 23634
6011 | 6011 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 11 | 16597 | 18621 | 20552 | 21026 | 20880 | 18177 | 18719 | 20218 | 21675 | 22204 | 20512 | 19555 | 19861 | 23359 | 24141 | 23788 | 22294 | 20919 | 22637 | 24455
6012 | 6012 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 12 | 16877 | 18904 | 20876 | 21428 | 21123 | 18450 | 19225 | 20540 | 22036 | 22484 | 20612 | 19849 | 20399 | 23768 | 24664 | 24089 | 22438 | 21462 | 23004 | 24890
6013 | 6013 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 13 | 16979 | 19152 | 21107 | 21753 | 21313 | 18579 | 19480 | 20779 | 22274 | 22689 | 20692 | 19982 | 20660 | 23924 | 24911 | 24290 | 22474 | 21716 | 23202 | 25043
6014 | 6014 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 14 | 17159 | 19445 | 21386 | 21996 | 21517 | 18724 | 19786 | 21062 | 22549 | 22874 | 20722 | 20105 | 20948 | 24211 | 25184 | 24448 | 22469 | 21987 | 23444 | 25320
6015 | 6015 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 15 | 17319 | 19709 | 21544 | 22216 | 21659 | 18919 | 20047 | 21339 | 22721 | 22994 | 20686 | 20287 | 21201 | 24234 | 25244 | 24525 | 22416 | 22207 | 23704 | 25334
6016 | 6016 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 16 | 17601 | 20019 | 21857 | 22455 | 21892 | 19164 | 20393 | 21593 | 23185 | 23135 | 20625 | 20446 | 21488 | 24578 | 25197 | 24561 | 22266 | 22456 | 23863 | 25650
6017 | 6017 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 17 | 17745 | 20279 | 21980 | 22503 | 21898 | 19368 | 20674 | 21884 | 23317 | 23107 | 20567 | 20685 | 21863 | 24724 | 25331 | 24602 | 22164 | 22848 | 24152 | 25809
6018 | 6018 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 18 | 17438 | 19947 | 21466 | 21994 | 21460 | 19219 | 20632 | 21795 | 22919 | 22885 | 20543 | 20864 | 22028 | 24333 | 24913 | 24524 | 22179 | 23081 | 24235 | 25472
6019 | 6019 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 19 | 16889 | 19287 | 20914 | 21520 | 21013 | 18771 | 20172 | 21160 | 22509 | 22674 | 20561 | 20706 | 21822 | 24101 | 24888 | 24639 | 22494 | 23018 | 23972 | 25384
6020 | 6020 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 20 | 16931 | 19195 | 21036 | 21590 | 21314 | 18933 | 20428 | 21275 | 22821 | 23216 | 21075 | 21201 | 22431 | 24829 | 25564 | 25599 | 23377 | 23794 | 24549 | 26270
6021 | 6021 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 21 | 16566 | 18776 | 20461 | 21026 | 20782 | 18727 | 20201 | 20994 | 22473 | 22978 | 21052 | 21453 | 22613 | 24909 | 25781 | 25869 | 23792 | 24204 | 24850 | 26543
6022 | 6022 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 22 | 15708 | 17535 | 19158 | 19696 | 19557 | 17930 | 19249 | 19871 | 21364 | 21956 | 20358 | 20933 | 21928 | 24025 | 24925 | 25132 | 23381 | 23620 | 24051 | 25775
6023 | 6023 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 23 | 14768 | 16201 | 17707 | 18219 | 18195 | 16980 | 18076 | 18521 | 19945 | 20642 | 19404 | 20086 | 20863 | 22731 | 23625 | 23954 | 22523 | 22608 | 22805 | 24520
6024 | 6024 | 251 | 9 | 8 | Summer | 9 | 7 | Summer | 24 | 13960 | 15137 | 16544 | 16965 | 17057 | 16224 | 17176 | 17490 | 18914 | 19608 | 18680 | 19460 | 20032 | 21738 | 22539 | 22946 | 21841 | 21810 | 21865 | 23567
6025 | 6025 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 1 | 13298 | 15206 | 15852 | 16104 | 16251 | 15402 | 15173 | 17679 | 18240 | 18815 | 18220 | 18112 | 17943 | 21148 | 21742 | 22176 | 21327 | 19690 | 22556 | 23019
6026 | 6026 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 2 | 12852 | 14720 | 15342 | 15613 | 15728 | 14898 | 14830 | 17106 | 17659 | 18216 | 17623 | 17525 | 17510 | 20457 | 21072 | 21461 | 20607 | 19208 | 21857 | 22283
6027 | 6027 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 3 | 12581 | 14466 | 15048 | 15349 | 15470 | 14639 | 14760 | 16847 | 17364 | 17912 | 17331 | 17205 | 17366 | 20042 | 20655 | 21012 | 20191 | 18999 | 21427 | 21805
6028 | 6028 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 4 | 12433 | 14414 | 14985 | 15232 | 15355 | 14448 | 14755 | 16666 | 17121 | 17578 | 16869 | 16770 | 17096 | 19514 | 20012 | 20343 | 19447 | 18587 | 20781 | 21125
6029 | 6029 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 5 | 12399 | 14756 | 15358 | 15574 | 15600 | 14370 | 15069 | 16843 | 17243 | 17556 | 16544 | 16357 | 17221 | 19386 | 19727 | 20059 | 18891 | 18544 | 20500 | 20812
6030 | 6030 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 6 | 12593 | 15824 | 16495 | 16615 | 16415 | 14550 | 15864 | 17718 | 18175 | 18099 | 16493 | 16211 | 17697 | 19945 | 20146 | 20223 | 18514 | 18872 | 20830 | 21182
6031 | 6031 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 7 | 12915 | 17054 | 17720 | 17769 | 17253 | 14751 | 16831 | 18674 | 19229 | 18740 | 16508 | 16154 | 18348 | 20713 | 20750 | 20541 | 18320 | 19405 | 21350 | 21787
6032 | 6032 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 8 | 13899 | 18069 | 18771 | 18742 | 17985 | 15668 | 18037 | 19572 | 20184 | 19400 | 17207 | 16948 | 19388 | 21530 | 21468 | 20986 | 18887 | 20392 | 21942 | 22511
6033 | 6033 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 9 | 15172 | 18999 | 19725 | 19657 | 18605 | 16953 | 19132 | 20461 | 21070 | 19949 | 18060 | 18157 | 20400 | 22397 | 22311 | 21493 | 19687 | 21368 | 22663 | 23322
6034 | 6034 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 10 | 16101 | 19705 | 20407 | 20294 | 18900 | 17846 | 19710 | 21191 | 21752 | 20219 | 18578 | 19067 | 21025 | 23311 | 22997 | 21875 | 20494 | 22032 | 23686 | 24293
6035 | 6035 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 11 | 16827 | 20204 | 20938 | 20882 | 19063 | 18553 | 20183 | 21709 | 22285 | 20403 | 18949 | 19802 | 21572 | 24021 | 23678 | 22200 | 21050 | 22628 | 24433 | 25053
6036 | 6036 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 12 | 17253 | 20476 | 21301 | 21064 | 19060 | 19005 | 20451 | 22006 | 22686 | 20451 | 19120 | 20278 | 21860 | 24485 | 23925 | 22279 | 21285 | 22942 | 24810 | 25561
6037 | 6037 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 13 | 17598 | 20833 | 21738 | 21363 | 19229 | 19371 | 20801 | 22359 | 23121 | 20645 | 19220 | 20648 | 22167 | 24842 | 24240 | 22435 | 21306 | 23251 | 25084 | 25918
6038 | 6038 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 14 | 17813 | 21003 | 21893 | 21480 | 19184 | 19589 | 20997 | 22547 | 23273 | 20596 | 19155 | 20854 | 22349 | 25032 | 24313 | 22346 | 21245 | 23410 | 25279 | 26096
6039 | 6039 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 15 | 18057 | 21111 | 22075 | 21576 | 19136 | 19809 | 21233 | 22671 | 23456 | 20527 | 19122 | 21067 | 22590 | 25055 | 24354 | 22253 | 21072 | 23635 | 25252 | 26107
6040 | 6040 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 16 | 18363 | 21299 | 22245 | 21723 | 19093 | 20080 | 21416 | 23006 | 23535 | 20402 | 19133 | 21275 | 22683 | 24937 | 24318 | 22020 | 20864 | 23698 | 25482 | 25958
6041 | 6041 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 17 | 18613 | 21345 | 22224 | 21659 | 18953 | 20290 | 21635 | 23061 | 23587 | 20276 | 19327 | 21573 | 22889 | 25003 | 24291 | 21853 | 21068 | 23916 | 25569 | 26048
6042 | 6042 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 18 | 18417 | 20896 | 21779 | 21269 | 18754 | 20307 | 21578 | 22730 | 23151 | 20282 | 19528 | 21776 | 22973 | 24638 | 24275 | 21943 | 21275 | 24078 | 25315 | 25752
6043 | 6043 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 19 | 17901 | 20395 | 21332 | 20857 | 18631 | 19881 | 20966 | 22337 | 22880 | 20281 | 19746 | 21579 | 22627 | 24613 | 24403 | 22277 | 21680 | 23861 | 25274 | 25887
6044 | 6044 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 20 | 18076 | 20497 | 21386 | 21144 | 18780 | 20143 | 21070 | 22597 | 23191 | 20718 | 20280 | 22153 | 23081 | 25256 | 25339 | 23135 | 22649 | 24463 | 26179 | 26703
6045 | 6045 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 21 | 17714 | 19906 | 20813 | 20597 | 18364 | 19906 | 20766 | 22198 | 22898 | 20598 | 20215 | 22288 | 23177 | 25421 | 25560 | 23528 | 22981 | 24775 | 26457 | 27096
6046 | 6046 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 22 | 16639 | 18548 | 19437 | 19309 | 17376 | 18892 | 19573 | 20997 | 21726 | 19811 | 19695 | 21492 | 22214 | 24505 | 24742 | 23028 | 22684 | 23925 | 25634 | 26297
6047 | 6047 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 23 | 15541 | 17133 | 17965 | 17972 | 16358 | 17737 | 18234 | 19578 | 20307 | 18850 | 18947 | 20428 | 20951 | 23204 | 23584 | 22193 | 22026 | 22705 | 24428 | 25067
6048 | 6048 | 252 | 9 | 9 | Summer | 9 | 8 | Summer | 24 | 14634 | 16010 | 16716 | 16843 | 15524 | 16838 | 17193 | 18531 | 19158 | 18132 | 18378 | 19601 | 19990 | 22117 | 22585 | 21518 | 21511 | 21772 | 23492 | 24022
6049 | 6049 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 1 | 12859 | 15417 | 15982 | 16131 | 15199 | 14934 | 17418 | 17923 | 18400 | 17789 | 17184 | 17615 | 20556 | 21395 | 21896 | 21097 | 19796 | 22532 | 23034 | 23351
6050 | 6050 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 2 | 12568 | 14922 | 15513 | 15623 | 14737 | 14605 | 16859 | 17362 | 17853 | 17220 | 16692 | 17205 | 19914 | 20747 | 21200 | 20412 | 19201 | 21835 | 22299 | 22644
6051 | 6051 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 3 | 12474 | 14630 | 15259 | 15368 | 14522 | 14543 | 16614 | 17080 | 17587 | 16965 | 16436 | 17087 | 19574 | 20361 | 20779 | 20009 | 18842 | 21420 | 21814 | 22169
6052 | 6052 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 4 | 12553 | 14571 | 15158 | 15277 | 14329 | 14558 | 16468 | 16890 | 17290 | 16571 | 16084 | 16863 | 19112 | 19760 | 20146 | 19290 | 18252 | 20785 | 21141 | 21408
6053 | 6053 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 5 | 12950 | 15017 | 15554 | 15591 | 14302 | 14956 | 16760 | 17149 | 17435 | 16404 | 15913 | 17032 | 19040 | 19517 | 19896 | 18760 | 17814 | 20507 | 20826 | 20977
6054 | 6054 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 6 | 13806 | 16149 | 16628 | 16438 | 14612 | 15779 | 17691 | 18141 | 18300 | 16439 | 15908 | 17580 | 19593 | 19987 | 20106 | 18408 | 17512 | 20853 | 21197 | 21266
6055 | 6055 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 7 | 14882 | 17415 | 17860 | 17346 | 14998 | 16809 | 18755 | 19296 | 19251 | 16573 | 15833 | 18308 | 20313 | 20660 | 20475 | 18261 | 17185 | 21404 | 21826 | 21828
6056 | 6056 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 8 | 16061 | 18429 | 18801 | 18035 | 15742 | 17970 | 19643 | 20231 | 20085 | 17250 | 16252 | 19325 | 20976 | 21343 | 20898 | 18805 | 17548 | 21970 | 22525 | 22469
6057 | 6057 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 9 | 17112 | 19358 | 19706 | 18620 | 16585 | 19027 | 20516 | 21105 | 20922 | 18095 | 16959 | 20313 | 21705 | 22156 | 21375 | 19569 | 18226 | 22661 | 23303 | 23268
6058 | 6058 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 10 | 17738 | 20068 | 20380 | 18937 | 17062 | 19628 | 21276 | 21816 | 21539 | 18633 | 17406 | 20937 | 22679 | 22844 | 21763 | 20372 | 18731 | 23697 | 24284 | 23993
6059 | 6059 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 11 | 18185 | 20592 | 20968 | 19104 | 17365 | 20102 | 21793 | 22370 | 22103 | 19010 | 17883 | 21456 | 23330 | 23489 | 22053 | 20901 | 19267 | 24407 | 25015 | 24686
6060 | 6060 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 12 | 18542 | 21073 | 21287 | 19238 | 17631 | 20501 | 22221 | 22904 | 22469 | 19312 | 18238 | 21878 | 23823 | 23861 | 22265 | 21268 | 19649 | 24917 | 25656 | 25111
6061 | 6061 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 13 | 18791 | 21350 | 21455 | 19281 | 17608 | 20711 | 22429 | 23197 | 22672 | 19265 | 18352 | 22079 | 23982 | 24066 | 22305 | 21183 | 19763 | 25078 | 25903 | 25326
6062 | 6062 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 14 | 19111 | 21631 | 21690 | 19359 | 17675 | 21027 | 22739 | 23476 | 22902 | 19314 | 18400 | 22379 | 24312 | 24263 | 22339 | 21237 | 19781 | 25387 | 26199 | 25510
6063 | 6063 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 15 | 19369 | 21847 | 21834 | 19358 | 17669 | 21317 | 22911 | 23712 | 23027 | 19343 | 18562 | 22664 | 24329 | 24351 | 22291 | 21100 | 19918 | 25395 | 26249 | 25574
6064 | 6064 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 16 | 19669 | 22103 | 22059 | 19407 | 17834 | 21578 | 23290 | 23886 | 23168 | 19438 | 18759 | 22858 | 24656 | 24397 | 22140 | 20976 | 20064 | 25694 | 26168 | 25569
6065 | 6065 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 17 | 19882 | 22094 | 22002 | 19279 | 18021 | 21815 | 23364 | 23951 | 23084 | 19644 | 19054 | 23066 | 24740 | 24385 | 21991 | 21194 | 20382 | 25792 | 26270 | 25564
6066 | 6066 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 18 | 19513 | 21505 | 21392 | 18884 | 17872 | 21562 | 22832 | 23310 | 22808 | 19595 | 19098 | 23013 | 24325 | 24266 | 21969 | 21328 | 20609 | 25442 | 25876 | 25495
6067 | 6067 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 19 | 18837 | 20947 | 20875 | 18648 | 17783 | 20840 | 22307 | 22882 | 22534 | 19637 | 19374 | 22565 | 24043 | 24297 | 22213 | 21640 | 21123 | 25333 | 25944 | 25659
6068 | 6068 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 20 | 18726 | 20970 | 21104 | 18732 | 18018 | 20903 | 22505 | 23110 | 22991 | 20056 | 20025 | 22931 | 24710 | 25152 | 23010 | 22531 | 21992 | 26210 | 26732 | 26677
6069 | 6069 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 21 | 18319 | 20332 | 20517 | 18274 | 17617 | 20565 | 22048 | 22722 | 22689 | 19879 | 19998 | 22948 | 24745 | 25298 | 23330 | 22814 | 22325 | 26471 | 27104 | 27030
6070 | 6070 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 22 | 17034 | 18964 | 19222 | 17284 | 16865 | 19367 | 20814 | 21505 | 21575 | 19324 | 19358 | 21965 | 23771 | 24452 | 22809 | 22504 | 21860 | 25658 | 26320 | 26309
6071 | 6071 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 23 | 15693 | 17485 | 17866 | 16261 | 16038 | 18024 | 19374 | 20050 | 20235 | 18549 | 18490 | 20671 | 22438 | 23266 | 21933 | 21831 | 21060 | 24437 | 25054 | 25183
6072 | 6072 | 253 | 9 | 10 | Summer | 9 | 9 | Summer | 24 | 14691 | 16277 | 16710 | 15429 | 15332 | 16971 | 18301 | 18879 | 19206 | 17978 | 17890 | 19698 | 21465 | 22265 | 21266 | 21329 | 20511 | 23494 | 24012 | 24226
6073 | 6073 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 1 | 14735 | 15415 | 15868 | 14986 | 14581 | 17014 | 17535 | 17955 | 18365 | 16734 | 17172 | 20050 | 20821 | 21423 | 20703 | 19511 | 19727 | 22883 | 23186 | 23407
6074 | 6074 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 2 | 14252 | 14934 | 15369 | 14515 | 14159 | 16453 | 16971 | 17405 | 17774 | 16246 | 16712 | 19414 | 20136 | 20728 | 20018 | 18909 | 19184 | 22138 | 22467 | 22649
6075 | 6075 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 3 | 14018 | 14662 | 15123 | 14300 | 13941 | 16215 | 16700 | 17152 | 17499 | 16020 | 16538 | 19100 | 19755 | 20331 | 19645 | 18563 | 18906 | 21668 | 22019 | 22167
6076 | 6076 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 4 | 13974 | 14584 | 15052 | 14128 | 13804 | 16097 | 16553 | 16906 | 17227 | 15721 | 16361 | 18693 | 19280 | 19744 | 18963 | 17999 | 18499 | 21006 | 21266 | 21416
6077 | 6077 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 5 | 14361 | 15010 | 15400 | 14196 | 13889 | 16432 | 16866 | 17223 | 17378 | 15628 | 16674 | 18704 | 19214 | 19563 | 18483 | 17598 | 18528 | 20718 | 20869 | 21044
6078 | 6078 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 6 | 15429 | 16080 | 16274 | 14528 | 14137 | 17396 | 17910 | 18162 | 17996 | 15682 | 17596 | 19315 | 19828 | 19821 | 18166 | 17311 | 19182 | 21111 | 21155 | 21118
6079 | 6079 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 7 | 16695 | 17317 | 17216 | 14948 | 14253 | 18491 | 19104 | 19193 | 18735 | 15652 | 18538 | 20078 | 20653 | 20218 | 18040 | 16988 | 19960 | 21752 | 21701 | 21395
6080 | 6080 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 8 | 17565 | 18156 | 17808 | 15583 | 14657 | 19288 | 19950 | 19949 | 19257 | 15985 | 19146 | 20674 | 21351 | 20563 | 18488 | 17250 | 20484 | 22342 | 22236 | 21684
6081 | 6081 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 9 | 18248 | 18836 | 18209 | 16239 | 15224 | 19963 | 20637 | 20630 | 19569 | 16511 | 19554 | 21214 | 21991 | 20805 | 19043 | 17724 | 20823 | 22907 | 22805 | 21925
6082 | 6082 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 10 | 18756 | 19387 | 18418 | 16626 | 15451 | 20635 | 21275 | 21220 | 19669 | 16925 | 20045 | 21985 | 22696 | 20986 | 19638 | 18027 | 21207 | 23680 | 23335 | 22160
6083 | 6083 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 11 | 19143 | 19888 | 18521 | 16897 | 15795 | 21093 | 21778 | 21782 | 19767 | 17367 | 20445 | 22536 | 23278 | 21168 | 20064 | 18462 | 21598 | 24309 | 23929 | 22391
6084 | 6084 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 12 | 19467 | 20202 | 18606 | 17113 | 16048 | 21472 | 22269 | 22105 | 19873 | 17689 | 20789 | 22957 | 23811 | 21313 | 20365 | 18776 | 21928 | 24880 | 24290 | 22572
6085 | 6085 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 13 | 19663 | 20339 | 18598 | 17009 | 16123 | 21614 | 22497 | 22194 | 19877 | 17717 | 20919 | 23078 | 24024 | 21322 | 20248 | 18860 | 22111 | 25089 | 24460 | 22580
6086 | 6086 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 14 | 19872 | 20500 | 18617 | 17024 | 16108 | 21876 | 22736 | 22394 | 19882 | 17736 | 21049 | 23333 | 24263 | 21281 | 20227 | 18805 | 22182 | 25303 | 24565 | 22519
6087 | 6087 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 15 | 20081 | 20618 | 18595 | 17004 | 16315 | 21993 | 22898 | 22460 | 19923 | 17795 | 21129 | 23417 | 24378 | 21292 | 20137 | 19000 | 22394 | 25406 | 24685 | 22500
6088 | 6088 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 16 | 20456 | 20903 | 18719 | 17236 | 16702 | 22397 | 23097 | 22632 | 20014 | 17994 | 21292 | 23842 | 24462 | 21283 | 20149 | 19278 | 22635 | 25449 | 24810 | 22435
6089 | 6089 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 17 | 20758 | 21086 | 18808 | 17652 | 17148 | 22696 | 23380 | 22769 | 20147 | 18511 | 21572 | 24162 | 24771 | 21374 | 20595 | 19838 | 23009 | 25780 | 25046 | 22539
6090 | 6090 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 18 | 20435 | 20711 | 18610 | 17654 | 17363 | 22428 | 22997 | 22571 | 20164 | 18776 | 21624 | 23983 | 24560 | 21587 | 20974 | 20310 | 23138 | 25652 | 25233 | 22822
6091 | 6091 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 19 | 19962 | 20287 | 18464 | 17622 | 17577 | 21993 | 22651 | 22306 | 20109 | 19103 | 21631 | 23760 | 24539 | 21896 | 21363 | 20907 | 23380 | 25821 | 25500 | 23276
6092 | 6092 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 20 | 20011 | 20477 | 18506 | 17823 | 17986 | 22153 | 22825 | 22696 | 20447 | 19682 | 22225 | 24356 | 25093 | 22629 | 22202 | 21753 | 24235 | 26598 | 26512 | 24174
6093 | 6093 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 21 | 19379 | 19850 | 18002 | 17346 | 17662 | 21645 | 22362 | 22282 | 20215 | 19553 | 21961 | 24270 | 25155 | 22870 | 22416 | 22012 | 24304 | 26937 | 26844 | 24627
6094 | 6094 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 22 | 18020 | 18553 | 16981 | 16580 | 16813 | 20374 | 21091 | 21127 | 19387 | 18858 | 20876 | 23259 | 24183 | 22297 | 22066 | 21534 | 23405 | 26144 | 26118 | 24178
6095 | 6095 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 23 | 16604 | 17185 | 15956 | 15780 | 15889 | 18933 | 19632 | 19775 | 18389 | 17974 | 19554 | 21932 | 22852 | 21413 | 21392 | 20736 | 22154 | 24888 | 24966 | 23342
6096 | 6096 | 254 | 9 | 11 | Summer | 9 | 10 | Summer | 24 | 15496 | 16043 | 15100 | 15064 | 15177 | 17833 | 18423 | 18708 | 17647 | 17370 | 18687 | 20930 | 21758 | 20725 | 20868 | 20178 | 21306 | 23828 | 24032 | 22700
6097 | 6097 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 1 | 14843 | 15291 | 14699 | 14407 | 14596 | 17108 | 17536 | 17902 | 17215 | 16716 | 18489 | 20297 | 20924 | 20233 | 19178 | 19434 | 21451 | 23047 | 23269 | 22205
6098 | 6098 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 2 | 14334 | 14800 | 14238 | 13981 | 14213 | 16544 | 16987 | 17317 | 16647 | 16262 | 17952 | 19622 | 20282 | 19554 | 18577 | 18886 | 20893 | 22317 | 22505 | 21457
6099 | 6099 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 3 | 14050 | 14549 | 14023 | 13762 | 14073 | 16274 | 16739 | 17056 | 16420 | 16110 | 17713 | 19267 | 19923 | 19200 | 18245 | 18621 | 20562 | 21867 | 22040 | 21031
6100 | 6100 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 4 | 14000 | 14486 | 13867 | 13640 | 14094 | 16155 | 16534 | 16835 | 16084 | 15979 | 17400 | 18845 | 19369 | 18562 | 17714 | 18230 | 19975 | 21118 | 21277 | 20228
6101 | 6101 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 5 | 14465 | 14842 | 13934 | 13719 | 14577 | 16489 | 16887 | 17033 | 15988 | 16350 | 17561 | 18834 | 19200 | 18123 | 17341 | 18278 | 19850 | 20723 | 20904 | 19611
6102 | 6102 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 6 | 15587 | 15725 | 14287 | 13990 | 15704 | 17574 | 17885 | 17733 | 16082 | 17331 | 18317 | 19520 | 19722 | 17864 | 17091 | 18955 | 20334 | 21029 | 20984 | 19188
6103 | 6103 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 7 | 16846 | 16693 | 14746 | 14146 | 16912 | 18817 | 18977 | 18554 | 16266 | 18332 | 19100 | 20397 | 20418 | 17784 | 16803 | 19758 | 20820 | 21588 | 21275 | 18986
6104 | 6104 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 8 | 17696 | 17236 | 15354 | 14502 | 17590 | 19634 | 19706 | 19066 | 16807 | 18916 | 19506 | 21086 | 20991 | 18198 | 17021 | 20253 | 21041 | 22077 | 21508 | 19347
6105 | 6105 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 9 | 18240 | 17444 | 15852 | 14905 | 17874 | 20151 | 20223 | 19237 | 17292 | 19159 | 19715 | 21556 | 21414 | 18584 | 17328 | 20407 | 21137 | 22465 | 21568 | 19716
6106 | 6106 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 10 | 18758 | 17606 | 16193 | 15185 | 18229 | 20722 | 20763 | 19443 | 17740 | 19604 | 20115 | 22221 | 21858 | 19121 | 17578 | 20746 | 21328 | 22950 | 21748 | 20332
6107 | 6107 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 11 | 19162 | 17674 | 16430 | 15528 | 18519 | 21174 | 21282 | 19556 | 18038 | 19959 | 20476 | 22754 | 22352 | 19496 | 17972 | 21093 | 21651 | 23504 | 21939 | 20769
6108 | 6108 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 12 | 19592 | 17798 | 16675 | 15839 | 18857 | 21686 | 21627 | 19727 | 18333 | 20337 | 20753 | 23308 | 22702 | 19828 | 18316 | 21468 | 21924 | 23891 | 22148 | 21131
6109 | 6109 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 13 | 19953 | 17932 | 16717 | 16038 | 19150 | 22064 | 21860 | 19837 | 18352 | 20605 | 20973 | 23661 | 23012 | 19848 | 18537 | 21786 | 22192 | 24198 | 22293 | 21151
6110 | 6110 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 14 | 20190 | 17965 | 16751 | 16062 | 19296 | 22324 | 22082 | 19901 | 18400 | 20765 | 21132 | 23921 | 23163 | 19858 | 18508 | 21877 | 22278 | 24327 | 22265 | 21137
6111 | 6111 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 15 | 20454 | 17997 | 16787 | 16230 | 19474 | 22532 | 22201 | 19856 | 18366 | 20890 | 21277 | 24087 | 23348 | 19817 | 18749 | 22137 | 22568 | 24489 | 22295 | 21093
6112 | 6112 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 16 | 20863 | 18200 | 17093 | 16607 | 19822 | 22814 | 22451 | 19906 | 18527 | 21125 | 21891 | 24244 | 23589 | 19891 | 19086 | 22445 | 23309 | 24672 | 22288 | 21135
6113 | 6113 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 17 | 21191 | 18390 | 17615 | 17150 | 20249 | 23211 | 22698 | 20133 | 19070 | 21515 | 22159 | 24666 | 23928 | 20456 | 19758 | 22940 | 23538 | 25020 | 22505 | 21714
6114 | 6114 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 18 | 20844 | 18106 | 17514 | 17300 | 20108 | 22776 | 22418 | 20050 | 19220 | 21481 | 21840 | 24388 | 23990 | 20778 | 20180 | 23002 | 23343 | 25163 | 22745 | 22084
6115 | 6115 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 19 | 20300 | 17880 | 17384 | 17428 | 19810 | 22329 | 22044 | 19869 | 19241 | 21352 | 21918 | 24227 | 23994 | 21049 | 20677 | 23137 | 23753 | 25346 | 23117 | 22501
6116 | 6116 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 20 | 20308 | 17914 | 17557 | 17819 | 20169 | 22471 | 22402 | 20146 | 19590 | 21878 | 22495 | 24715 | 24795 | 21845 | 21496 | 23975 | 24657 | 26363 | 24021 | 23471
6117 | 6117 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 21 | 19639 | 17385 | 17071 | 17475 | 19646 | 21982 | 21944 | 19843 | 19329 | 21555 | 22321 | 24699 | 24854 | 22006 | 21728 | 24027 | 24868 | 26703 | 24485 | 23822
6118 | 6118 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 22 | 18266 | 16373 | 16303 | 16614 | 18403 | 20700 | 20763 | 18976 | 18731 | 20446 | 21395 | 23712 | 23977 | 21637 | 21229 | 23143 | 24171 | 25984 | 24049 | 23559
6119 | 6119 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 23 | 16773 | 15332 | 15481 | 15690 | 17043 | 19216 | 19377 | 17935 | 17934 | 19082 | 20130 | 22333 | 22740 | 20929 | 20406 | 21861 | 23011 | 24809 | 23193 | 22880
6120 | 6120 | 255 | 9 | 12 | Summer | 9 | 11 | Summer | 24 | 15592 | 14501 | 14754 | 14977 | 16074 | 17988 | 18281 | 17165 | 17337 | 18219 | 19223 | 21220 | 21735 | 20388 | 19838 | 21007 | 22143 | 23837 | 22549 | 22388
6121 | 6121 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 1 | 14734 | 14009 | 14040 | 14293 | 15471 | 16973 | 17345 | 16634 | 16146 | 17843 | 18426 | 20261 | 20829 | 18664 | 18983 | 21009 | 21534 | 22958 | 21926 | 20348
6122 | 6122 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 2 | 14269 | 13580 | 13650 | 13930 | 15042 | 16454 | 16789 | 16097 | 15683 | 17344 | 17902 | 19637 | 20157 | 18093 | 18466 | 20480 | 21001 | 22232 | 21209 | 19723
6123 | 6123 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 3 | 13994 | 13339 | 13417 | 13771 | 14844 | 16196 | 16523 | 15864 | 15467 | 17118 | 17656 | 19291 | 19781 | 17766 | 18203 | 20149 | 20664 | 21764 | 20780 | 19341
6124 | 6124 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 4 | 13931 | 13204 | 13301 | 13798 | 14774 | 16021 | 16335 | 15570 | 15214 | 16857 | 17327 | 18795 | 19238 | 17266 | 17837 | 19585 | 20031 | 21021 | 19984 | 18711
6125 | 6125 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 5 | 14344 | 13225 | 13331 | 14228 | 15191 | 16321 | 16495 | 15430 | 15145 | 16979 | 17374 | 18678 | 19105 | 16924 | 17908 | 19481 | 19840 | 20659 | 19362 | 18228
6126 | 6126 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 6 | 15457 | 13611 | 13644 | 15405 | 16276 | 17377 | 17278 | 15626 | 15284 | 17833 | 18182 | 19318 | 19442 | 16743 | 18655 | 20029 | 20328 | 20769 | 18968 | 17900
6127 | 6127 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 7 | 16743 | 14097 | 13832 | 16647 | 17368 | 18492 | 18143 | 15879 | 15332 | 18671 | 18993 | 20109 | 19912 | 16503 | 19486 | 20556 | 20925 | 21080 | 18786 | 17565
6128 | 6128 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 8 | 17597 | 14784 | 14286 | 17390 | 18026 | 19298 | 18760 | 16532 | 15699 | 19190 | 19449 | 20771 | 20309 | 16803 | 20058 | 20850 | 21247 | 21393 | 19217 | 17826
6129 | 6129 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 9 | 18450 | 15656 | 15068 | 18025 | 18729 | 20167 | 19294 | 17381 | 16435 | 19754 | 19883 | 21576 | 20768 | 17488 | 20591 | 21318 | 21549 | 21824 | 19950 | 18486
6130 | 6130 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 10 | 19027 | 16027 | 15350 | 18352 | 19106 | 20644 | 19429 | 17734 | 16873 | 20040 | 20140 | 22080 | 20977 | 17808 | 21002 | 21578 | 21790 | 22085 | 20639 | 18861
6131 | 6131 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 11 | 19674 | 16406 | 15846 | 18783 | 19573 | 21276 | 19643 | 18129 | 17472 | 20478 | 20416 | 22764 | 21306 | 18391 | 21541 | 22096 | 22145 | 22468 | 21267 | 19490
6132 | 6132 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 12 | 20001 | 16597 | 16094 | 19059 | 19776 | 21537 | 19735 | 18346 | 17791 | 20677 | 20752 | 23054 | 21452 | 18688 | 21867 | 22320 | 22549 | 22626 | 21584 | 19806
6133 | 6133 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 13 | 20065 | 16446 | 16114 | 19174 | 19793 | 21613 | 19686 | 18215 | 17738 | 20759 | 20814 | 23140 | 21358 | 18689 | 21965 | 22360 | 22556 | 22548 | 21384 | 19812
6134 | 6134 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 14 | 20136 | 16367 | 16005 | 19185 | 19840 | 21691 | 19606 | 18116 | 17668 | 20771 | 20863 | 23192 | 21240 | 18561 | 21955 | 22340 | 22594 | 22412 | 21262 | 19670
6135 | 6135 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 15 | 20203 | 16368 | 16143 | 19348 | 19927 | 21817 | 19579 | 18109 | 17682 | 20951 | 20951 | 23286 | 21205 | 18704 | 22116 | 22523 | 22694 | 22335 | 21118 | 19805
6136 | 6136 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 16 | 20502 | 16721 | 16569 | 19757 | 20498 | 22157 | 19732 | 18384 | 17924 | 21667 | 21079 | 23519 | 21240 | 19020 | 22403 | 23245 | 22759 | 22305 | 21133 | 20104
6137 | 6137 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 17 | 20612 | 17050 | 16911 | 19988 | 20572 | 22207 | 19765 | 18736 | 18356 | 21739 | 21270 | 23654 | 21256 | 19496 | 22695 | 23290 | 22986 | 22321 | 21516 | 20594
6138 | 6138 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 18 | 20089 | 16859 | 16975 | 19799 | 20118 | 21929 | 19659 | 18858 | 18476 | 21441 | 21007 | 23588 | 21299 | 19826 | 22666 | 23000 | 22713 | 22474 | 21807 | 20958
6139 | 6139 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 19 | 19595 | 16713 | 17114 | 19529 | 20047 | 21588 | 19489 | 18889 | 18704 | 21514 | 21283 | 23547 | 21489 | 20295 | 22782 | 23389 | 23181 | 22845 | 22226 | 21540
6140 | 6140 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 20 | 19758 | 16837 | 17463 | 19848 | 20234 | 21895 | 19703 | 19155 | 19223 | 21991 | 21884 | 24260 | 22161 | 21058 | 23573 | 24246 | 24206 | 23733 | 23178 | 22415
6141 | 6141 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 21 | 19141 | 16368 | 17113 | 19320 | 19733 | 21421 | 19363 | 18845 | 19055 | 21740 | 21704 | 24249 | 22353 | 21253 | 23597 | 24440 | 24459 | 24207 | 23542 | 22765
6142 | 6142 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 22 | 17780 | 15552 | 16201 | 18027 | 18516 | 20167 | 18426 | 18169 | 18267 | 20733 | 20802 | 23288 | 21698 | 20688 | 22644 | 23691 | 23764 | 23735 | 23243 | 22295
6143 | 6143 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 23 | 16435 | 14783 | 15321 | 16716 | 17215 | 18830 | 17411 | 17382 | 17404 | 19492 | 19634 | 22082 | 20818 | 19900 | 21401 | 22562 | 22700 | 22935 | 22615 | 21544
6144 | 6144 | 256 | 9 | 13 | Summer | 9 | 12 | Summer | 24 | 15328 | 14042 | 14592 | 15752 | 16197 | 17719 | 16614 | 16752 | 16794 | 18584 | 18850 | 21061 | 20133 | 19326 | 20550 | 21686 | 21966 | 22291 | 22120 | 21008
6145 | 6145 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 1 | 14569 | 13480 | 14035 | 15232 | 15367 | 16875 | 16181 | 15753 | 16129 | 17858 | 17849 | 20234 | 19633 | 18578 | 20603 | 21160 | 21021 | 21756 | 20202 | 20224
6146 | 6146 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 2 | 14121 | 13096 | 13693 | 14809 | 14951 | 16334 | 15660 | 15301 | 15709 | 17355 | 17387 | 19582 | 18990 | 18071 | 20088 | 20638 | 20524 | 21036 | 19583 | 19663
6147 | 6147 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 3 | 13875 | 12873 | 13544 | 14608 | 14763 | 16081 | 15443 | 15088 | 15560 | 17146 | 17174 | 19228 | 18651 | 17834 | 19783 | 20306 | 20200 | 20609 | 19214 | 19380
6148 | 6148 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 4 | 13810 | 12753 | 13581 | 14546 | 14700 | 15922 | 15185 | 14869 | 15467 | 16877 | 16818 | 18739 | 18056 | 17502 | 19244 | 19709 | 19550 | 19815 | 18586 | 18927
6149 | 6149 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 5 | 14170 | 12844 | 14077 | 15000 | 15089 | 16208 | 15190 | 14858 | 15799 | 17116 | 16935 | 18695 | 17688 | 17625 | 19203 | 19573 | 19333 | 19231 | 18107 | 18909
6150 | 6150 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 6 | 15072 | 13143 | 15258 | 16089 | 16218 | 17010 | 15431 | 15041 | 16842 | 17984 | 17635 | 19112 | 17501 | 18388 | 19770 | 20077 | 19649 | 18834 | 17778 | 19554
6151 | 6151 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 7 | 16046 | 13343 | 16531 | 17199 | 17339 | 17908 | 15750 | 15132 | 17859 | 18873 | 18404 | 19625 | 17468 | 19240 | 20313 | 20693 | 20102 | 18644 | 17432 | 20330
6152 | 6152 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 8 | 16658 | 13826 | 17272 | 17873 | 17906 | 18517 | 16419 | 15533 | 18535 | 19354 | 18686 | 20047 | 17973 | 19814 | 20632 | 21025 | 20290 | 19080 | 17694 | 20873
6153 | 6153 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 9 | 17209 | 14621 | 17943 | 18573 | 18387 | 19060 | 17291 | 16277 | 19145 | 19810 | 18995 | 20526 | 18752 | 20366 | 21116 | 21350 | 20582 | 19828 | 18362 | 21400
6154 | 6154 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 10 | 17479 | 15068 | 18379 | 18946 | 18698 | 19303 | 17738 | 16650 | 19570 | 20164 | 19115 | 20807 | 19450 | 20855 | 21460 | 21672 | 20673 | 20588 | 18822 | 21945
6155 | 6155 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 11 | 17766 | 15619 | 18904 | 19431 | 18994 | 19610 | 18223 | 17244 | 20071 | 20535 | 19349 | 21184 | 20077 | 21449 | 22031 | 22074 | 20940 | 21266 | 19509 | 22584
6156 | 6156 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 12 | 17859 | 15894 | 19203 | 19631 | 19283 | 19718 | 18458 | 17542 | 20388 | 20883 | 19391 | 21336 | 20380 | 21796 | 22277 | 22476 | 21011 | 21605 | 19850 | 22945
6157 | 6157 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 13 | 18041 | 16128 | 19542 | 19921 | 19582 | 19875 | 18532 | 17778 | 20758 | 21147 | 19522 | 21497 | 20417 | 22136 | 22559 | 22732 | 21140 | 21645 | 20095 | 23299
6158 | 6158 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 14 | 18113 | 16200 | 19710 | 20109 | 19782 | 19956 | 18599 | 17833 | 20923 | 21370 | 19587 | 21556 | 20485 | 22289 | 22706 | 22947 | 21161 | 21710 | 20114 | 23448
6159 | 6159 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 15 | 18126 | 16349 | 19919 | 20317 | 19901 | 19983 | 18641 | 18023 | 21117 | 21519 | 19646 | 21559 | 20382 | 22491 | 22934 | 23079 | 21171 | 21603 | 20287 | 23643
6160 | 6160 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 16 | 18145 | 16556 | 20120 | 20724 | 19905 | 19937 | 18711 | 18181 | 21253 | 21448 | 19721 | 21395 | 20228 | 22565 | 23439 | 22931 | 21164 | 21399 | 20364 | 23687
6161 | 6161 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 17 | 17944 | 16688 | 20152 | 20615 | 19894 | 19788 | 18871 | 18423 | 21258 | 21457 | 19794 | 21218 | 20404 | 22671 | 23310 | 22952 | 21241 | 21591 | 20665 | 23813
6162 | 6162 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 18 | 17433 | 16519 | 19689 | 20019 | 19308 | 19418 | 18699 | 18354 | 21095 | 20882 | 19779 | 21077 | 20463 | 22493 | 22852 | 22535 | 21472 | 21703 | 20886 | 23668
6163 | 6163 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 19 | 17173 | 16601 | 19339 | 19889 | 19285 | 19151 | 18613 | 18504 | 20936 | 21000 | 20200 | 21156 | 20639 | 22539 | 23157 | 22926 | 22168 | 22073 | 21429 | 23827
6164 | 6164 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 20 | 17184 | 16948 | 19636 | 20049 | 19602 | 19340 | 18843 | 18974 | 21400 | 21522 | 20810 | 21756 | 21370 | 23292 | 23978 | 23908 | 23085 | 23027 | 22298 | 24688
6165 | 6165 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 21 | 16626 | 16555 | 19067 | 19494 | 19035 | 18944 | 18468 | 18730 | 21003 | 21230 | 20743 | 21839 | 21462 | 23247 | 24105 | 24105 | 23445 | 23367 | 22625 | 24783
6166 | 6166 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 22 | 15608 | 15673 | 17782 | 18311 | 17898 | 18003 | 17782 | 17953 | 19849 | 20298 | 19989 | 21188 | 21047 | 22279 | 23360 | 23445 | 22950 | 23092 | 22184 | 23903
6167 | 6167 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 23 | 14580 | 14765 | 16509 | 17039 | 16608 | 17019 | 16954 | 17037 | 18491 | 19127 | 18959 | 20309 | 20333 | 21064 | 22232 | 22395 | 21971 | 22439 | 21414 | 22724
6168 | 6168 | 257 | 9 | 14 | Summer | 9 | 13 | Summer | 24 | 13789 | 14026 | 15469 | 15944 | 15694 | 16137 | 16297 | 16386 | 17615 | 18273 | 18236 | 19534 | 19788 | 20139 | 21285 | 21580 | 21360 | 21937 | 20866 | 21830
6169 | 6169 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 1 | 13258 | 13408 | 14870 | 15023 | 14676 | 15637 | 15311 | 15650 | 17182 | 17187 | 17365 | 18960 | 18166 | 20065 | 20667 | 20555 | 20568 | 19959 | 20011 | 21925
6170 | 6170 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 2 | 12845 | 13105 | 14466 | 14611 | 14311 | 15128 | 14868 | 15241 | 16699 | 16743 | 16914 | 18338 | 17608 | 19568 | 20158 | 20066 | 20091 | 19342 | 19452 | 21373
6171 | 6171 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 3 | 12637 | 12977 | 14279 | 14445 | 14177 | 14931 | 14675 | 15119 | 16514 | 16577 | 16719 | 18048 | 17328 | 19295 | 19868 | 19789 | 19792 | 18993 | 19186 | 21040
6172 | 6172 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 4 | 12499 | 13016 | 14223 | 14394 | 14091 | 14693 | 14481 | 15059 | 16291 | 16280 | 16420 | 17498 | 16855 | 18791 | 19302 | 19161 | 19187 | 18369 | 18727 | 20386
6173 | 6173 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 5 | 12574 | 13517 | 14686 | 14860 | 14523 | 14735 | 14504 | 15526 | 16595 | 16476 | 16606 | 17202 | 16577 | 18804 | 19213 | 18979 | 18986 | 17924 | 18723 | 20222
6174 | 6174 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 6 | 12937 | 14705 | 15780 | 16022 | 15575 | 15010 | 14739 | 16640 | 17497 | 17274 | 17402 | 17095 | 16426 | 19423 | 19764 | 19334 | 19394 | 17610 | 19379 | 20674
6175 | 6175 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 7 | 13387 | 15953 | 16885 | 17156 | 16563 | 15322 | 14843 | 17718 | 18377 | 18082 | 18177 | 17094 | 16175 | 19972 | 20380 | 19777 | 19927 | 17229 | 20112 | 21080
6176 | 6176 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 8 | 14110 | 16790 | 17674 | 17806 | 16998 | 16025 | 15281 | 18492 | 18947 | 18489 | 18418 | 17658 | 16521 | 20401 | 20812 | 20065 | 19976 | 17517 | 20735 | 21424
6177 | 6177 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 9 | 14960 | 17450 | 18384 | 18271 | 17321 | 16885 | 16029 | 19114 | 19510 | 18808 | 18712 | 18414 | 17195 | 20860 | 21114 | 20324 | 20196 | 18158 | 21228 | 21845
6178 | 6178 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 10 | 15530 | 18071 | 18955 | 18796 | 17539 | 17552 | 16640 | 19813 | 20001 | 19187 | 19053 | 19202 | 17695 | 21306 | 21536 | 20509 | 20324 | 18718 | 21878 | 22352
6179 | 6179 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 11 | 15897 | 18548 | 19393 | 19070 | 17646 | 17989 | 17197 | 20330 | 20450 | 19388 | 19307 | 19731 | 18247 | 21783 | 21851 | 20692 | 20555 | 19316 | 22430 | 22886
6180 | 6180 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 12 | 16106 | 18851 | 19603 | 19373 | 17646 | 18237 | 17509 | 20672 | 20674 | 19460 | 19342 | 20033 | 18568 | 22028 | 22257 | 20762 | 20595 | 19649 | 22797 | 23155
6181 | 6181 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 13 | 15978 | 18976 | 19675 | 19425 | 17583 | 18078 | 17511 | 20766 | 20759 | 19347 | 19217 | 19862 | 18615 | 22098 | 22310 | 20687 | 20519 | 19689 | 22943 | 23232
6182 | 6182 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 14 | 16093 | 19198 | 19906 | 19676 | 17689 | 18206 | 17626 | 21001 | 20962 | 19490 | 19192 | 19973 | 18680 | 22272 | 22541 | 20753 | 20419 | 19733 | 23106 | 23396
6183 | 6183 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 15 | 16161 | 19345 | 20049 | 19738 | 17766 | 18147 | 17703 | 21090 | 21203 | 19405 | 19064 | 19885 | 18872 | 22516 | 22686 | 20782 | 20404 | 19916 | 23311 | 23637
6184 | 6184 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 16 | 16362 | 19557 | 20391 | 19734 | 18065 | 18197 | 17825 | 21177 | 21820 | 19427 | 18995 | 19805 | 19026 | 23098 | 22606 | 20837 | 20428 | 20051 | 23420 | 24182
6185 | 6185 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 17 | 16630 | 19688 | 20394 | 19844 | 18175 | 18470 | 18169 | 21294 | 21834 | 19601 | 19036 | 20102 | 19412 | 23081 | 22756 | 21041 | 20548 | 20468 | 23658 | 24175
6186 | 6186 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 18 | 16220 | 19203 | 19808 | 19191 | 18027 | 18293 | 18079 | 20974 | 21243 | 19550 | 18979 | 20129 | 19592 | 22611 | 22324 | 21241 | 20609 | 20694 | 23525 | 23760
6187 | 6187 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 19 | 15945 | 18813 | 19621 | 19084 | 18192 | 18136 | 18159 | 20698 | 21130 | 19856 | 19385 | 20204 | 19944 | 22831 | 22630 | 21879 | 21320 | 21181 | 23633 | 24131
6188 | 6188 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 20 | 16046 | 19056 | 19749 | 19361 | 18480 | 18331 | 18594 | 21103 | 21543 | 20377 | 20073 | 20853 | 20664 | 23594 | 23565 | 22763 | 22366 | 22063 | 24493 | 25049
6189 | 6189 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 21 | 15555 | 18479 | 19169 | 18758 | 18011 | 17928 | 18314 | 20649 | 21206 | 20195 | 19987 | 20867 | 20782 | 23662 | 23705 | 23083 | 22745 | 22387 | 24586 | 25303
6190 | 6190 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 22 | 14798 | 17211 | 17982 | 17612 | 17030 | 17235 | 17518 | 19472 | 20216 | 19406 | 19320 | 20431 | 20242 | 22896 | 23024 | 22567 | 22343 | 21953 | 23716 | 24656
6191 | 6191 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 23 | 13988 | 15866 | 16635 | 16320 | 15814 | 16394 | 16589 | 18091 | 18896 | 18265 | 18371 | 19670 | 19403 | 21672 | 21881 | 21556 | 21517 | 21170 | 22465 | 23503
6192 | 6192 | 258 | 9 | 15 | Summer | 9 | 14 | Summer | 24 | 13255 | 14820 | 15536 | 15344 | 14979 | 15722 | 15921 | 17132 | 17902 | 17546 | 17651 | 19109 | 18816 | 20734 | 21063 | 20881 | 20812 | 20631 | 21577 | 22597
6193 | 6193 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 1 | 12768 | 14318 | 14735 | 14425 | 14203 | 14922 | 15293 | 16749 | 17176 | 16768 | 16995 | 17689 | 18089 | 20190 | 20142 | 20197 | 20067 | 19867 | 21767 | 22136
6194 | 6194 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 2 | 12386 | 13908 | 14328 | 14057 | 13851 | 14478 | 14883 | 16271 | 16680 | 16326 | 16513 | 17138 | 17587 | 19681 | 19662 | 19721 | 19567 | 19300 | 21200 | 21570
6195 | 6195 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 3 | 12175 | 13693 | 14143 | 13903 | 13711 | 14266 | 14744 | 16076 | 16495 | 16142 | 16288 | 16861 | 17370 | 19396 | 19380 | 19419 | 19240 | 19018 | 20855 | 21219
6196 | 6196 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 4 | 12062 | 13682 | 14123 | 13861 | 13707 | 14115 | 14735 | 15928 | 16286 | 15930 | 15950 | 16459 | 17082 | 18892 | 18811 | 18870 | 18597 | 18591 | 20235 | 20551
6197 | 6197 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 5 | 12158 | 14146 | 14612 | 14324 | 14165 | 14169 | 15244 | 16294 | 16600 | 16206 | 15751 | 16252 | 17257 | 18872 | 18685 | 18723 | 18087 | 18605 | 20088 | 20346
6198 | 6198 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 6 | 12435 | 15242 | 15749 | 15391 | 15259 | 14408 | 16386 | 17243 | 17516 | 17072 | 15770 | 16153 | 18044 | 19453 | 19059 | 19160 | 17790 | 19247 | 20531 | 20748
6199 | 6199 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 7 | 12618 | 16382 | 16892 | 16418 | 16371 | 14547 | 17521 | 18201 | 18437 | 17931 | 15785 | 15966 | 18915 | 20120 | 19547 | 19716 | 17502 | 19997 | 20967 | 21243
6200 | 6200 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 8 | 13127 | 17169 | 17533 | 16899 | 16759 | 14976 | 18294 | 18855 | 19021 | 18191 | 16266 | 16313 | 19580 | 20557 | 19835 | 19821 | 17826 | 20611 | 21290 | 21599
6201 | 6201 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 9 | 13896 | 17869 | 17983 | 17218 | 17089 | 15701 | 18900 | 19445 | 19476 | 18473 | 16953 | 16994 | 20106 | 20868 | 20100 | 20038 | 18441 | 21102 | 21714 | 21864
6202 | 6202 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 10 | 14624 | 18461 | 18521 | 17537 | 17445 | 16264 | 19536 | 20034 | 20183 | 18712 | 17364 | 17582 | 20786 | 21367 | 20361 | 20255 | 18810 | 21828 | 22294 | 22432
6203 | 6203 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 11 | 15042 | 18822 | 18699 | 17580 | 17563 | 16698 | 19925 | 20418 | 20462 | 18816 | 17619 | 18061 | 21226 | 21607 | 20471 | 20414 | 19098 | 22309 | 22760 | 22726
6204 | 6204 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 12 | 15334 | 19064 | 19024 | 17602 | 17554 | 17008 | 20262 | 20659 | 20853 | 18845 | 17755 | 18401 | 21586 | 22032 | 20565 | 20474 | 19245 | 22693 | 23039 | 23184
6205 | 6205 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 13 | 15391 | 19231 | 19151 | 17587 | 17492 | 17095 | 20444 | 20794 | 20919 | 18818 | 17604 | 18492 | 21770 | 22137 | 20549 | 20436 | 19081 | 22893 | 23176 | 23291
6206 | 6206 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 14 | 15490 | 19427 | 19361 | 17676 | 17446 | 17160 | 20624 | 20980 | 21186 | 18740 | 17566 | 18544 | 21934 | 22356 | 20590 | 20316 | 19016 | 23044 | 23329 | 23510
6207 | 6207 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 15 | 15540 | 19567 | 19447 | 17700 | 17345 | 17300 | 20787 | 21159 | 21141 | 18720 | 17547 | 18687 | 22092 | 22449 | 20569 | 20252 | 18972 | 23186 | 23508 | 23590
6208 | 6208 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 16 | 15762 | 19878 | 19512 | 17938 | 17424 | 17519 | 20983 | 21660 | 20997 | 18790 | 17637 | 18848 | 22217 | 22366 | 20621 | 20215 | 18993 | 23273 | 24044 | 23475
6209 | 6209 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 17 | 15999 | 19886 | 19630 | 18043 | 17501 | 17867 | 21101 | 21664 | 21109 | 18839 | 17847 | 19236 | 22426 | 22507 | 20814 | 20338 | 19173 | 23511 | 24030 | 23640
6210 | 6210 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 18 | 15828 | 19324 | 18978 | 17870 | 17254 | 17777 | 20753 | 21072 | 20529 | 18741 | 18004 | 19378 | 22244 | 22060 | 21017 | 20398 | 19490 | 23385 | 23625 | 23257
6211 | 6211 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 19 | 15870 | 19135 | 18868 | 18023 | 17382 | 17857 | 20467 | 20931 | 20556 | 19089 | 18332 | 19685 | 22215 | 22326 | 21627 | 21078 | 20146 | 23501 | 24005 | 23684
6212 | 6212 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 20 | 16207 | 19238 | 19121 | 18284 | 17735 | 18278 | 20851 | 21289 | 21002 | 19692 | 18907 | 20347 | 22928 | 23208 | 22466 | 22107 | 21072 | 24370 | 24927 | 24750
6213 | 6213 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 21 | 15798 | 18627 | 18497 | 17779 | 17259 | 17976 | 20363 | 20879 | 20634 | 19499 | 18931 | 20396 | 22824 | 23279 | 22726 | 22417 | 21529 | 24463 | 25169 | 25032
6214 | 6214 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 22 | 14924 | 17382 | 17334 | 16755 | 16324 | 17150 | 19152 | 19815 | 19674 | 18763 | 18446 | 19794 | 21838 | 22563 | 22180 | 21966 | 21289 | 23575 | 24496 | 24435
6215 | 6215 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 23 | 14022 | 16063 | 16041 | 15560 | 15312 | 16234 | 17777 | 18498 | 18423 | 17795 | 17796 | 18945 | 20559 | 21413 | 21168 | 21144 | 20733 | 22334 | 23359 | 23330
6216 | 6216 | 259 | 9 | 16 | Summer | 9 | 15 | Summer | 24 | 13282 | 14967 | 15036 | 14722 | 14468 | 15532 | 16780 | 17474 | 17556 | 17056 | 17259 | 18346 | 19642 | 20578 | 20481 | 20432 | 20236 | 21430 | 22440 | 22542
6217 | 6217 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 1 | 12862 | 14228 | 14233 | 14017 | 14058 | 14983 | 16413 | 16786 | 16656 | 16506 | 16122 | 17695 | 19684 | 19737 | 19849 | 19774 | 18778 | 21664 | 22033 | 21669
6218 | 6218 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 2 | 12593 | 13844 | 13901 | 13690 | 13679 | 14602 | 15966 | 16321 | 16238 | 16064 | 15723 | 17222 | 19206 | 19283 | 19405 | 19302 | 18374 | 21120 | 21489 | 21165
6219 | 6219 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 3 | 12436 | 13632 | 13720 | 13516 | 13480 | 14435 | 15749 | 16111 | 16043 | 15840 | 15537 | 16996 | 18911 | 18994 | 19093 | 18970 | 18101 | 20755 | 21116 | 20806
6220 | 6220 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 4 | 12511 | 13634 | 13704 | 13551 | 13415 | 14455 | 15645 | 15971 | 15836 | 15578 | 15279 | 16772 | 18476 | 18478 | 18591 | 18397 | 17613 | 20154 | 20464 | 20124
6221 | 6221 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 5 | 13009 | 14110 | 14167 | 14026 | 13485 | 14970 | 16040 | 16335 | 16100 | 15437 | 15113 | 16998 | 18544 | 18392 | 18476 | 17909 | 17175 | 20011 | 20256 | 19850
6222 | 6222 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 6 | 14178 | 15260 | 15278 | 15164 | 13853 | 16148 | 17051 | 17322 | 16961 | 15551 | 15101 | 17872 | 19211 | 18831 | 18964 | 17664 | 16881 | 20482 | 20678 | 20118
6223 | 6223 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 7 | 15467 | 16461 | 16379 | 16335 | 14171 | 17335 | 18101 | 18318 | 17863 | 15667 | 15020 | 18814 | 19851 | 19386 | 19592 | 17430 | 16612 | 20959 | 21217 | 20571
6224 | 6224 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 8 | 16297 | 17116 | 16885 | 16729 | 14787 | 18118 | 18801 | 18936 | 18290 | 16184 | 15300 | 19506 | 20291 | 19700 | 19724 | 17750 | 16793 | 21309 | 21585 | 20827
6225 | 6225 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 9 | 16865 | 17466 | 17141 | 16953 | 15499 | 18632 | 19317 | 19298 | 18501 | 16801 | 15918 | 19955 | 20684 | 19875 | 19855 | 18280 | 17369 | 21642 | 21758 | 20987
6226 | 6226 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 10 | 17410 | 17918 | 17376 | 17109 | 15774 | 19164 | 19801 | 19750 | 18692 | 17104 | 16345 | 20522 | 21101 | 20026 | 19964 | 18536 | 18023 | 22116 | 22228 | 21185
6227 | 6227 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 11 | 17769 | 18066 | 17380 | 17141 | 15942 | 19504 | 20133 | 19918 | 18712 | 17312 | 16632 | 20911 | 21465 | 20083 | 20072 | 18776 | 18438 | 22532 | 22480 | 21292
6228 | 6228 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 12 | 18101 | 18388 | 17414 | 17131 | 16064 | 19846 | 20379 | 20298 | 18796 | 17454 | 16899 | 21284 | 21735 | 20183 | 20139 | 18942 | 18764 | 22824 | 22934 | 21414
6229 | 6229 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 13 | 18264 | 18526 | 17390 | 17092 | 15904 | 20019 | 20505 | 20400 | 18764 | 17291 | 16910 | 21462 | 21854 | 20159 | 20091 | 18782 | 18686 | 22950 | 23027 | 21407
6230 | 6230 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 14 | 18520 | 18789 | 17551 | 17092 | 15946 | 20271 | 20764 | 20694 | 18916 | 17328 | 16969 | 21704 | 22080 | 20283 | 20048 | 18786 | 18768 | 23169 | 23316 | 21508
6231 | 6231 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 15 | 18750 | 18923 | 17644 | 17157 | 16011 | 20504 | 21008 | 20861 | 19014 | 17388 | 17085 | 21940 | 22348 | 20341 | 20061 | 18817 | 18718 | 23412 | 23477 | 21535
6232 | 6232 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 16 | 18986 | 18982 | 17868 | 17308 | 16163 | 20689 | 21466 | 20843 | 19154 | 17472 | 17299 | 22059 | 22893 | 20387 | 20016 | 18823 | 18746 | 23928 | 23344 | 21527
6233 | 6233 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 17 | 19117 | 19082 | 17963 | 17394 | 16352 | 20808 | 21469 | 20963 | 19336 | 17682 | 17693 | 22272 | 22867 | 20580 | 20142 | 19001 | 19020 | 23915 | 23510 | 21737
6234 | 6234 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 18 | 18681 | 18518 | 17789 | 17179 | 16389 | 20519 | 20942 | 20436 | 19322 | 17866 | 17891 | 22111 | 22454 | 20826 | 20251 | 19390 | 19329 | 23574 | 23189 | 22050
6235 | 6235 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 19 | 18299 | 18400 | 17927 | 17296 | 16561 | 20227 | 20777 | 20428 | 19597 | 18136 | 18286 | 22043 | 22647 | 21402 | 20898 | 20028 | 19895 | 23947 | 23614 | 22766
6236 | 6236 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 20 | 18492 | 18576 | 18123 | 17589 | 16735 | 20565 | 21062 | 20783 | 20026 | 18597 | 18735 | 22674 | 23333 | 22167 | 21852 | 20888 | 20683 | 24836 | 24645 | 23688
6237 | 6237 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 21 | 17905 | 17923 | 17584 | 17070 | 16375 | 20051 | 20596 | 20342 | 19749 | 18510 | 18662 | 22496 | 23324 | 22354 | 22098 | 21291 | 20965 | 25067 | 24915 | 24086
6238 | 6238 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 22 | 16610 | 16742 | 16527 | 16101 | 15621 | 18807 | 19487 | 19319 | 18877 | 17953 | 18125 | 21449 | 22488 | 21751 | 21613 | 21010 | 20609 | 24387 | 24305 | 23609
6239 | 6239 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 23 | 15282 | 15449 | 15323 | 15092 | 14895 | 17437 | 18154 | 18036 | 17733 | 17278 | 17371 | 20142 | 21272 | 20718 | 20778 | 20446 | 19944 | 23233 | 23201 | 22624
6240 | 6240 | 260 | 9 | 17 | Summer | 9 | 16 | Summer | 24 | 14238 | 14443 | 14464 | 14246 | 14261 | 16430 | 17111 | 17139 | 16994 | 16743 | 16844 | 19208 | 20313 | 20027 | 20060 | 19944 | 19516 | 22312 | 22420 | 21982
6241 | 6241 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 1 | 13575 | 13465 | 13581 | 13665 | 13345 | 15844 | 16225 | 16056 | 16037 | 15534 | 16195 | 18961 | 19573 | 19164 | 19187 | 18286 | 18757 | 21671 | 21329 | 21146
6242 | 6242 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 2 | 13192 | 13169 | 13307 | 13332 | 13029 | 15462 | 15833 | 15718 | 15628 | 15229 | 15959 | 18498 | 19105 | 18733 | 18725 | 17886 | 18420 | 21132 | 20815 | 20653
6243 | 6243 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 3 | 12968 | 12996 | 13155 | 13157 | 12893 | 15273 | 15657 | 15565 | 15452 | 15101 | 15916 | 18239 | 18831 | 18453 | 18423 | 17638 | 18277 | 20776 | 20472 | 20300
6244 | 6244 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 4 | 12959 | 12987 | 13183 | 13083 | 12823 | 15173 | 15538 | 15379 | 15295 | 14869 | 15785 | 17846 | 18377 | 17973 | 17854 | 17148 | 17934 | 20120 | 19771 | 19652
6245 | 6245 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 5 | 13414 | 13447 | 13676 | 13169 | 12878 | 15598 | 15942 | 15698 | 15634 | 14767 | 16089 | 17978 | 18409 | 17915 | 17414 | 16742 | 17979 | 19927 | 19516 | 19404
6246 | 6246 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 6 | 14529 | 14568 | 14846 | 13571 | 13162 | 16646 | 16983 | 16638 | 16594 | 14818 | 17074 | 18718 | 19057 | 18467 | 17213 | 16480 | 18670 | 20370 | 19794 | 19771
6247 | 6247 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 7 | 15702 | 15687 | 16062 | 13924 | 13356 | 17738 | 18033 | 17617 | 17541 | 14795 | 18006 | 19426 | 19803 | 19127 | 17015 | 16232 | 19357 | 20933 | 20250 | 20338
6248 | 6248 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 8 | 16483 | 16199 | 16461 | 14534 | 13688 | 18444 | 18656 | 18072 | 17814 | 15088 | 18393 | 19894 | 20257 | 19262 | 17352 | 16411 | 19667 | 21292 | 20491 | 20412
6249 | 6249 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 9 | 17073 | 16418 | 16697 | 15223 | 14310 | 18943 | 19009 | 18270 | 18000 | 15695 | 18562 | 20284 | 20480 | 19384 | 17879 | 16970 | 19847 | 21462 | 20637 | 20518
6250 | 6250 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 10 | 17572 | 16627 | 16816 | 15446 | 14723 | 19340 | 19362 | 18372 | 18142 | 16000 | 18732 | 20686 | 20873 | 19479 | 18126 | 17617 | 20364 | 21906 | 20824 | 20653
6251 | 6251 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 11 | 17874 | 16598 | 16818 | 15575 | 14952 | 19616 | 19477 | 18337 | 18175 | 16225 | 18883 | 21021 | 21043 | 19560 | 18343 | 18009 | 20671 | 22132 | 20908 | 20782
6252 | 6252 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 12 | 18082 | 16637 | 16760 | 15639 | 15143 | 19809 | 19797 | 18361 | 18162 | 16441 | 19026 | 21243 | 21407 | 19573 | 18458 | 18276 | 20866 | 22542 | 20993 | 20833
6253 | 6253 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 13 | 18298 | 16673 | 16775 | 15542 | 15221 | 19985 | 19955 | 18381 | 18174 | 16500 | 19120 | 21413 | 21567 | 19588 | 18341 | 18249 | 20883 | 22686 | 21016 | 20843
6254 | 6254 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 14 | 18387 | 16632 | 16585 | 15398 | 15104 | 20058 | 20054 | 18353 | 17987 | 16372 | 19149 | 21466 | 21671 | 19360 | 18160 | 18149 | 20945 | 22781 | 20932 | 20601
6255 | 6255 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 15 | 18565 | 16677 | 16623 | 15430 | 15191 | 20275 | 20196 | 18424 | 18017 | 16468 | 19286 | 21702 | 21812 | 19358 | 18170 | 18073 | 20906 | 22918 | 20947 | 20576
6256 | 6256 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 16 | 18916 | 16974 | 16863 | 15674 | 15564 | 20817 | 20269 | 18667 | 18181 | 16774 | 19569 | 22314 | 21811 | 19411 | 18267 | 18189 | 21009 | 22862 | 21029 | 20576
6257 | 6257 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 17 | 18992 | 17111 | 16982 | 15905 | 15979 | 20869 | 20431 | 18897 | 18283 | 17211 | 19847 | 22334 | 21995 | 19584 | 18492 | 18517 | 21178 | 23061 | 21285 | 20759
6258 | 6258 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 18 | 18571 | 16937 | 16760 | 15975 | 16012 | 20408 | 19966 | 18886 | 18282 | 17431 | 19852 | 21963 | 21656 | 19733 | 18927 | 18886 | 21359 | 22802 | 21642 | 20973
6259 | 6259 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 19 | 18406 | 17108 | 16897 | 16172 | 16274 | 20259 | 19972 | 19155 | 18612 | 17811 | 20250 | 22140 | 21916 | 20370 | 19566 | 19461 | 21972 | 23258 | 22391 | 21762
6260 | 6260 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 20 | 18499 | 17335 | 17199 | 16363 | 16574 | 20555 | 20323 | 19562 | 19151 | 18236 | 20636 | 22804 | 22756 | 21315 | 20426 | 20273 | 22583 | 24328 | 23358 | 22857
6261 | 6261 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 21 | 17837 | 16750 | 16625 | 15939 | 16176 | 20030 | 19800 | 19180 | 18843 | 18049 | 20369 | 22687 | 22721 | 21474 | 20746 | 20496 | 22671 | 24558 | 23725 | 23230
6262 | 6262 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 22 | 16578 | 15703 | 15655 | 15193 | 15453 | 18905 | 18743 | 18292 | 18057 | 17481 | 19439 | 21820 | 21959 | 20960 | 20449 | 20151 | 21919 | 23949 | 23272 | 22844
6263 | 6263 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 23 | 15266 | 14509 | 14652 | 14481 | 14656 | 17577 | 17462 | 17116 | 17068 | 16718 | 18294 | 20588 | 20802 | 20121 | 19879 | 19480 | 20837 | 22856 | 22299 | 22054
6264 | 6264 | 261 | 9 | 18 | Summer | 9 | 17 | Summer | 24 | 14191 | 13679 | 13793 | 13846 | 14025 | 16519 | 16541 | 16350 | 16318 | 16194 | 17560 | 19629 | 19965 | 19409 | 19379 | 19062 | 20212 | 22089 | 21670 | 21394
6265 | 6265 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 1 | 13445 | 13003 | 13405 | 13209 | 13645 | 15787 | 15633 | 15639 | 15822 | 15745 | 17075 | 19044 | 19052 | 18739 | 17960 | 18481 | 19951 | 21178 | 21010 | 20640
6266 | 6266 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 2 | 13099 | 12737 | 13082 | 12943 | 13457 | 15399 | 15302 | 15316 | 15476 | 15523 | 16761 | 18586 | 18618 | 18291 | 17570 | 18144 | 19538 | 20669 | 20519 | 20135
6267 | 6267 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 3 | 12908 | 12579 | 12902 | 12811 | 13429 | 15223 | 15153 | 15166 | 15298 | 15504 | 16582 | 18334 | 18372 | 18002 | 17336 | 18008 | 19283 | 20333 | 20172 | 19787
6268 | 6268 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 4 | 12891 | 12618 | 12835 | 12741 | 13487 | 15131 | 15004 | 15045 | 15064 | 15415 | 16364 | 17923 | 17877 | 17472 | 16875 | 17668 | 19011 | 19642 | 19528 | 19101
6269 | 6269 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 5 | 13382 | 13123 | 12953 | 12818 | 14050 | 15587 | 15386 | 15456 | 15006 | 15804 | 16596 | 18037 | 17873 | 17104 | 16521 | 17765 | 18796 | 19411 | 19299 | 18550
6270 | 6270 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 6 | 14518 | 14277 | 13361 | 13103 | 15277 | 16649 | 16369 | 16475 | 15176 | 16832 | 17558 | 18745 | 18370 | 16938 | 16280 | 18466 | 19373 | 19684 | 19661 | 18206
6271 | 6271 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 7 | 15747 | 15513 | 13746 | 13329 | 16417 | 17739 | 17399 | 17498 | 15365 | 17814 | 18381 | 19538 | 18979 | 16776 | 16058 | 19171 | 19932 | 20143 | 20218 | 17921
6272 | 6272 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 8 | 16279 | 15833 | 14280 | 13570 | 16787 | 18277 | 17774 | 17715 | 15793 | 18126 | 18440 | 19933 | 19204 | 17027 | 16141 | 19404 | 19811 | 20290 | 20192 | 18113
6273 | 6273 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 9 | 16314 | 15780 | 14716 | 13906 | 16746 | 18353 | 17703 | 17627 | 16109 | 18022 | 18337 | 19886 | 19087 | 17273 | 16424 | 19304 | 19637 | 20146 | 20011 | 18327
6274 | 6274 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 10 | 16328 | 15503 | 14571 | 13864 | 16547 | 18314 | 17428 | 17273 | 15907 | 17796 | 18320 | 19864 | 18836 | 17115 | 16668 | 19418 | 19797 | 19939 | 19750 | 18226
6275 | 6275 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 11 | 16395 | 15451 | 14665 | 14030 | 16622 | 18373 | 17345 | 17225 | 16003 | 17890 | 18526 | 19977 | 18812 | 17274 | 17006 | 19675 | 20024 | 19971 | 19827 | 18438
6276 | 6276 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 12 | 16566 | 15332 | 14661 | 14148 | 16671 | 18613 | 17290 | 17136 | 16019 | 17965 | 18663 | 20274 | 18788 | 17317 | 17201 | 19801 | 20058 | 19979 | 19805 | 18503
6277 | 6277 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 13 | 16841 | 15458 | 14651 | 14312 | 16853 | 18857 | 17393 | 17229 | 15987 | 18140 | 18842 | 20492 | 18880 | 17286 | 17263 | 19893 | 20219 | 20081 | 19895 | 18474
6278 | 6278 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 14 | 16949 | 15312 | 14555 | 14239 | 16945 | 19005 | 17417 | 17091 | 15887 | 18224 | 19005 | 20659 | 18869 | 17160 | 17214 | 20005 | 20367 | 20047 | 19707 | 18319
6279 | 6279 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 15 | 17097 | 15398 | 14641 | 14381 | 17125 | 19194 | 17544 | 17181 | 15963 | 18421 | 19210 | 20863 | 18952 | 17230 | 17196 | 20029 | 20578 | 20118 | 19738 | 18376
6280 | 6280 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 16 | 17377 | 15758 | 15015 | 14866 | 17596 | 19401 | 17925 | 17474 | 16261 | 18839 | 19886 | 20990 | 19214 | 17461 | 17439 | 20249 | 21298 | 20326 | 19864 | 18575
6281 | 6281 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 17 | 17765 | 16104 | 15474 | 15510 | 18043 | 19803 | 18388 | 17808 | 16758 | 19355 | 20336 | 21417 | 19708 | 17923 | 18001 | 20658 | 21773 | 20820 | 20284 | 19047
6282 | 6282 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 18 | 17544 | 16130 | 15741 | 15779 | 18204 | 19596 | 18597 | 18010 | 17238 | 19580 | 20212 | 21311 | 20247 | 18598 | 18613 | 21071 | 21630 | 21433 | 20750 | 19784
6283 | 6283 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 19 | 17571 | 16371 | 16024 | 16147 | 18548 | 19679 | 18942 | 18404 | 17615 | 20019 | 20507 | 21628 | 20917 | 19298 | 19273 | 21779 | 22249 | 22282 | 21639 | 20629
6284 | 6284 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 20 | 17748 | 16617 | 16162 | 16407 | 18676 | 19970 | 19276 | 18857 | 18032 | 20318 | 21068 | 22374 | 21648 | 20092 | 20030 | 22342 | 23146 | 23227 | 22723 | 21565
6285 | 6285 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 21 | 17066 | 16054 | 15734 | 16002 | 18138 | 19435 | 18863 | 18487 | 17848 | 19993 | 20876 | 22275 | 21758 | 20370 | 20223 | 22415 | 23362 | 23610 | 23113 | 22047
6286 | 6286 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 22 | 15886 | 15046 | 14954 | 15247 | 17019 | 18336 | 17926 | 17648 | 17259 | 19013 | 19958 | 21448 | 21140 | 20022 | 19834 | 21642 | 22689 | 23135 | 22712 | 21820
6287 | 6287 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 23 | 14592 | 14018 | 14218 | 14452 | 15797 | 17033 | 16718 | 16617 | 16554 | 17826 | 18711 | 20244 | 20081 | 19415 | 19138 | 20532 | 21555 | 22156 | 21895 | 21270
6288 | 6288 | 262 | 9 | 19 | Summer | 9 | 18 | Summer | 24 | 13613 | 13199 | 13572 | 13833 | 14981 | 16098 | 15928 | 15846 | 16017 | 17096 | 17961 | 19418 | 19399 | 18924 | 18730 | 19937 | 20928 | 21518 | 21239 | 20824
6289 | 6289 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 1 | 12887 | 12799 | 12952 | 13430 | 14182 | 15158 | 15171 | 15343 | 15059 | 16528 | 17294 | 18482 | 18678 | 17538 | 18125 | 19598 | 20285 | 20809 | 20461 | 19199
6290 | 6290 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 2 | 12595 | 12489 | 12698 | 13238 | 13918 | 14838 | 14859 | 15002 | 14759 | 16238 | 16895 | 18065 | 18257 | 17165 | 17801 | 19192 | 19780 | 20327 | 19964 | 18780
6291 | 6291 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 3 | 12435 | 12307 | 12561 | 13207 | 13786 | 14690 | 14713 | 14837 | 14651 | 16085 | 16695 | 17835 | 18009 | 16947 | 17678 | 18955 | 19523 | 19974 | 19617 | 18507
6292 | 6292 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 4 | 12455 | 12256 | 12514 | 13291 | 13817 | 14592 | 14646 | 14666 | 14475 | 15940 | 16459 | 17417 | 17584 | 16537 | 17382 | 18724 | 19211 | 19355 | 18952 | 17971
6293 | 6293 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 5 | 12937 | 12392 | 12584 | 13858 | 14274 | 14989 | 15098 | 14656 | 14435 | 16232 | 16660 | 17472 | 17609 | 16213 | 17501 | 18536 | 19021 | 19147 | 18400 | 17493
6294 | 6294 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 6 | 14063 | 12813 | 12897 | 15112 | 15503 | 16016 | 16186 | 14910 | 14532 | 17274 | 17606 | 18051 | 18198 | 16022 | 18244 | 19150 | 19603 | 19530 | 18073 | 17159
6295 | 6295 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 7 | 15178 | 13222 | 13140 | 16254 | 16656 | 17060 | 17248 | 15147 | 14537 | 18150 | 18576 | 18712 | 18897 | 15817 | 18961 | 19703 | 20222 | 20078 | 17778 | 16864
6296 | 6296 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 8 | 15455 | 13620 | 13266 | 16489 | 16819 | 17298 | 17354 | 15476 | 14614 | 18108 | 18730 | 18830 | 18829 | 15776 | 19054 | 19471 | 20175 | 19923 | 17833 | 16779
6297 | 6297 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 9 | 15373 | 14074 | 13646 | 16475 | 16832 | 17251 | 17303 | 15845 | 14956 | 18048 | 18617 | 18749 | 18679 | 16083 | 18985 | 19327 | 19945 | 19762 | 18069 | 17061
6298 | 6298 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 10 | 15235 | 14047 | 13684 | 16351 | 16877 | 17047 | 17025 | 15715 | 14924 | 18082 | 18539 | 18539 | 18425 | 16376 | 19151 | 19538 | 19911 | 19561 | 18024 | 17410
6299 | 6299 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 11 | 15187 | 14160 | 13889 | 16462 | 17069 | 16992 | 17002 | 15842 | 15135 | 18305 | 18673 | 18533 | 18479 | 16732 | 19429 | 19789 | 20030 | 19660 | 18258 | 17812
6300 | 6300 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 12 | 15224 | 14207 | 14065 | 16575 | 17224 | 16984 | 16965 | 15918 | 15330 | 18499 | 18756 | 18564 | 18473 | 16984 | 19613 | 19882 | 20000 | 19691 | 18380 | 18082
6301 | 6301 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 13 | 15311 | 14170 | 14201 | 16735 | 17375 | 17058 | 17023 | 15863 | 15438 | 18646 | 18892 | 18648 | 18520 | 17016 | 19674 | 20018 | 20158 | 19745 | 18316 | 18126
6302 | 6302 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 14 | 15286 | 14035 | 14102 | 16801 | 17529 | 17055 | 16861 | 15739 | 15336 | 18793 | 19022 | 18617 | 18326 | 16947 | 19765 | 20142 | 20257 | 19530 | 18149 | 18043
6303 | 6303 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 15 | 15564 | 14275 | 14415 | 17168 | 17922 | 17357 | 17127 | 16002 | 15671 | 19179 | 19391 | 18896 | 18572 | 17108 | 19966 | 20547 | 20650 | 19736 | 18380 | 18192
6304 | 6304 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 16 | 15859 | 14518 | 14784 | 17521 | 18415 | 17624 | 17310 | 16192 | 15988 | 19730 | 19692 | 19053 | 18644 | 17230 | 20065 | 21161 | 20952 | 19739 | 18450 | 18295
6305 | 6305 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 17 | 16232 | 14976 | 15427 | 17966 | 18915 | 18090 | 17647 | 16680 | 16662 | 20182 | 20150 | 19534 | 19058 | 17796 | 20478 | 21630 | 21430 | 20168 | 18928 | 18861
6306 | 6306 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 18 | 16283 | 15230 | 15649 | 18106 | 18738 | 18305 | 17818 | 17111 | 17117 | 20041 | 20210 | 20035 | 19430 | 18415 | 20906 | 21486 | 21555 | 20640 | 19678 | 19530
6307 | 6307 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 19 | 16546 | 15497 | 15996 | 18424 | 18757 | 18631 | 18175 | 17430 | 17559 | 20265 | 20552 | 20644 | 20115 | 19039 | 21580 | 22058 | 22279 | 21519 | 20514 | 20263
6308 | 6308 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 20 | 16735 | 15604 | 16220 | 18516 | 18991 | 18924 | 18572 | 17771 | 17904 | 20724 | 21166 | 21283 | 20966 | 19744 | 22102 | 22918 | 23264 | 22586 | 21442 | 21086
6309 | 6309 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 21 | 16146 | 15137 | 15785 | 17950 | 18437 | 18464 | 18143 | 17512 | 17661 | 20428 | 21068 | 21302 | 21068 | 19879 | 22123 | 23082 | 23612 | 22963 | 21911 | 21379
6310 | 6310 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 22 | 15064 | 14358 | 15016 | 16808 | 17283 | 17494 | 17264 | 16866 | 17035 | 19468 | 20146 | 20608 | 20515 | 19459 | 21328 | 22376 | 22960 | 22563 | 21683 | 21050
6311 | 6311 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 23 | 13858 | 13616 | 14222 | 15532 | 15972 | 16225 | 16149 | 16137 | 16247 | 18132 | 18869 | 19460 | 19622 | 18754 | 20156 | 21171 | 21849 | 21680 | 21142 | 20384
6312 | 6312 | 263 | 9 | 20 | Summer | 9 | 19 | Summer | 24 | 13060 | 12975 | 13582 | 14776 | 15105 | 15479 | 15409 | 15564 | 15721 | 17436 | 18094 | 18829 | 18910 | 18331 | 19605 | 20590 | 21073 | 21077 | 20692 | 19997
6313 | 6313 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 1 | 12489 | 12507 | 13314 | 14049 | 14410 | 14821 | 15037 | 14781 | 15360 | 16861 | 17437 | 18197 | 18347 | 17849 | 19334 | 20037 | 20486 | 20411 | 19184 | 19489
6314 | 6314 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 2 | 12237 | 12257 | 13128 | 13790 | 14051 | 14515 | 14698 | 14492 | 15147 | 16479 | 17013 | 17802 | 17928 | 17535 | 18935 | 19549 | 19986 | 19919 | 18764 | 19131
6315 | 6315 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 3 | 12075 | 12113 | 13086 | 13638 | 13882 | 14364 | 14528 | 14371 | 15126 | 16300 | 16834 | 17565 | 17648 | 17421 | 18707 | 19291 | 19792 | 19561 | 18489 | 18967
6316 | 6316 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 4 | 12147 | 12065 | 13187 | 13691 | 13912 | 14334 | 14401 | 14243 | 15111 | 16131 | 16542 | 17208 | 17194 | 17167 | 18510 | 19016 | 19346 | 18914 | 17962 | 18592
6317 | 6317 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 5 | 12647 | 12135 | 13750 | 14159 | 14388 | 14814 | 14431 | 14236 | 15530 | 16403 | 16679 | 17296 | 16872 | 17319 | 18364 | 18852 | 19037 | 18374 | 17482 | 18602
6318 | 6318 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 6 | 13827 | 12459 | 15044 | 15435 | 15670 | 15954 | 14766 | 14422 | 16637 | 17445 | 17452 | 18007 | 16783 | 18120 | 19036 | 19482 | 19385 | 18082 | 17177 | 19269
6319 | 6319 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 7 | 15076 | 12730 | 16222 | 16633 | 16898 | 17042 | 15061 | 14497 | 17662 | 18474 | 18290 | 18771 | 16662 | 18865 | 19633 | 20140 | 19957 | 17796 | 16882 | 19936
6320 | 6320 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 8 | 15435 | 13033 | 16550 | 16901 | 17356 | 17240 | 15570 | 14753 | 18010 | 18745 | 18565 | 18817 | 16957 | 19068 | 19512 | 20202 | 20163 | 18009 | 16950 | 20094
6321 | 6321 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 9 | 15312 | 13321 | 16478 | 16849 | 17311 | 17104 | 15874 | 15050 | 17877 | 18565 | 18514 | 18608 | 17172 | 18926 | 19292 | 19919 | 20031 | 18164 | 17147 | 19912
6322 | 6322 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 10 | 14991 | 13303 | 16281 | 16822 | 17162 | 16743 | 15652 | 14944 | 17624 | 18382 | 18399 | 18248 | 16969 | 18984 | 19401 | 19788 | 20014 | 18011 | 17394 | 20018
6323 | 6323 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 11 | 14900 | 13479 | 16364 | 16963 | 17210 | 16679 | 15734 | 15109 | 17691 | 18465 | 18504 | 18237 | 17091 | 19215 | 19603 | 19851 | 20201 | 18196 | 17751 | 20290
6324 | 6324 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 12 | 14851 | 13648 | 16480 | 17134 | 17269 | 16639 | 15812 | 15314 | 17826 | 18552 | 18632 | 18239 | 17196 | 19400 | 19703 | 19831 | 20365 | 18320 | 18026 | 20494
6325 | 6325 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 13 | 14982 | 13791 | 16681 | 17329 | 17446 | 16730 | 15793 | 15469 | 18004 | 18722 | 18816 | 18333 | 17176 | 19499 | 19871 | 20032 | 20599 | 18290 | 18104 | 20608
6326 | 6326 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 14 | 14858 | 13749 | 16797 | 17537 | 17636 | 16620 | 15724 | 15422 | 18111 | 18910 | 18944 | 18202 | 17077 | 19647 | 20054 | 20188 | 20666 | 18176 | 18074 | 20741
6327 | 6327 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 15 | 14945 | 13874 | 16978 | 17733 | 17829 | 16705 | 15803 | 15562 | 18306 | 19101 | 19186 | 18262 | 17149 | 19669 | 20281 | 20390 | 20830 | 18225 | 18042 | 20751
6328 | 6328 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 16 | 15323 | 14451 | 17554 | 18412 | 18350 | 17122 | 16223 | 16098 | 18748 | 19629 | 19547 | 18564 | 17471 | 19993 | 21121 | 20909 | 21014 | 18514 | 18361 | 21052
6329 | 6329 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 17 | 15657 | 15087 | 17980 | 18907 | 18773 | 17447 | 16698 | 16755 | 19244 | 20075 | 20049 | 18965 | 17910 | 20393 | 21569 | 21376 | 21494 | 18984 | 18919 | 21454
6330 | 6330 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 18 | 15624 | 15222 | 18008 | 18688 | 18718 | 17548 | 17034 | 17118 | 19416 | 20052 | 20299 | 19245 | 18523 | 20742 | 21349 | 21456 | 21804 | 19675 | 19531 | 21863
6331 | 6331 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 19 | 15826 | 15552 | 18294 | 18672 | 18863 | 17863 | 17301 | 17509 | 19788 | 20306 | 20707 | 19858 | 19161 | 21364 | 21864 | 22129 | 22525 | 20487 | 20237 | 22586
6332 | 6332 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 20 | 16040 | 15760 | 18356 | 18866 | 19062 | 18228 | 17598 | 17795 | 20018 | 20828 | 21240 | 20637 | 19879 | 21846 | 22670 | 23065 | 23473 | 21410 | 21061 | 23177
6333 | 6333 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 21 | 15460 | 15300 | 17760 | 18270 | 18580 | 17752 | 17279 | 17482 | 19623 | 20620 | 21138 | 20639 | 20075 | 21803 | 22775 | 23356 | 23823 | 21864 | 21344 | 23293
6334 | 6334 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 22 | 14441 | 14522 | 16596 | 17104 | 17386 | 16849 | 16593 | 16818 | 18595 | 19645 | 20249 | 20021 | 19685 | 20973 | 22057 | 22669 | 23178 | 21630 | 21018 | 22555
6335 | 6335 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 23 | 13408 | 13730 | 15386 | 15789 | 16085 | 15797 | 15847 | 16005 | 17392 | 18411 | 19088 | 19090 | 19055 | 19861 | 20885 | 21551 | 22134 | 21079 | 20349 | 21471
6336 | 6336 | 264 | 9 | 21 | Summer | 9 | 20 | Summer | 24 | 12686 | 13096 | 14619 | 14976 | 15167 | 15038 | 15243 | 15445 | 16702 | 17630 | 18341 | 18432 | 18537 | 19303 | 20301 | 20818 | 21435 | 20613 | 19959 | 20949
6337 | 6337 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 1 | 12274 | 12749 | 13775 | 14161 | 14272 | 14574 | 14416 | 14978 | 16062 | 16846 | 17575 | 17790 | 17215 | 18873 | 19619 | 20111 | 20749 | 19021 | 19329 | 20686
6338 | 6338 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 2 | 11991 | 12576 | 13538 | 13815 | 13948 | 14251 | 14140 | 14783 | 15798 | 16453 | 17126 | 17389 | 16871 | 18499 | 19163 | 19636 | 20186 | 18616 | 18984 | 20261
6339 | 6339 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 3 | 11819 | 12532 | 13396 | 13662 | 13835 | 14097 | 14033 | 14784 | 15666 | 16318 | 16895 | 17159 | 16677 | 18304 | 18935 | 19476 | 19912 | 18360 | 18838 | 20006
6340 | 6340 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 4 | 11769 | 12654 | 13469 | 13713 | 13827 | 14003 | 13944 | 14808 | 15578 | 16098 | 16586 | 16760 | 16321 | 18156 | 18706 | 19064 | 19432 | 17852 | 18476 | 19712
6341 | 6341 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 5 | 11916 | 13224 | 13947 | 14212 | 14254 | 14072 | 13974 | 15275 | 15930 | 16316 | 16708 | 16517 | 16049 | 18064 | 18590 | 18801 | 19099 | 17389 | 18500 | 19447
6342 | 6342 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 6 | 12351 | 14496 | 15201 | 15501 | 15392 | 14415 | 14184 | 16426 | 17034 | 17161 | 17519 | 16497 | 15909 | 18760 | 19253 | 19167 | 19482 | 17071 | 19156 | 19973
6343 | 6343 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 7 | 12787 | 15723 | 16451 | 16765 | 16580 | 14758 | 14325 | 17522 | 17982 | 18086 | 18343 | 16456 | 15758 | 19412 | 19951 | 19772 | 20002 | 16799 | 19839 | 20496
6344 | 6344 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 8 | 13303 | 15996 | 16706 | 17116 | 16895 | 15236 | 14555 | 17781 | 18020 | 18350 | 18525 | 16734 | 15837 | 19269 | 19989 | 19879 | 20176 | 16826 | 19951 | 20260
6345 | 6345 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 9 | 13723 | 16039 | 16769 | 17145 | 16963 | 15628 | 14958 | 17742 | 17963 | 18402 | 18605 | 17026 | 16133 | 19146 | 19807 | 19820 | 20317 | 17114 | 19859 | 20091
6346 | 6346 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 10 | 13802 | 16075 | 16963 | 17201 | 17075 | 15607 | 15055 | 17691 | 18092 | 18463 | 18574 | 17004 | 16507 | 19441 | 19866 | 19983 | 20685 | 17545 | 20156 | 20441
6347 | 6347 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 11 | 13881 | 16180 | 17130 | 17280 | 17167 | 15697 | 15233 | 17788 | 18281 | 18563 | 18762 | 17139 | 16827 | 19647 | 19936 | 20189 | 21040 | 17910 | 20440 | 20698
6348 | 6348 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 12 | 13940 | 16298 | 17310 | 17344 | 17260 | 15776 | 15437 | 17926 | 18488 | 18694 | 18927 | 17248 | 17091 | 19747 | 19918 | 20355 | 21273 | 18184 | 20646 | 20821
6349 | 6349 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 13 | 13885 | 16445 | 17443 | 17466 | 17401 | 15691 | 15531 | 18047 | 18621 | 18816 | 19015 | 17158 | 17112 | 19850 | 20055 | 20529 | 21344 | 18198 | 20688 | 20926
6350 | 6350 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 14 | 13796 | 16547 | 17639 | 17650 | 17537 | 15614 | 15474 | 18151 | 18822 | 18942 | 19089 | 17063 | 17097 | 20027 | 20204 | 20595 | 21389 | 18158 | 20810 | 21087
6351 | 6351 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 15 | 13854 | 16723 | 17832 | 17834 | 17790 | 15692 | 15611 | 18338 | 19023 | 19191 | 19209 | 17136 | 17075 | 20259 | 20410 | 20758 | 21188 | 18125 | 20821 | 21302
6352 | 6352 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 16 | 14317 | 17278 | 18443 | 18427 | 18250 | 16114 | 16146 | 18856 | 19783 | 19556 | 19440 | 17475 | 17415 | 21099 | 20926 | 21015 | 21094 | 18433 | 21111 | 22116
6353 | 6353 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 17 | 14808 | 17702 | 18944 | 18866 | 18765 | 16602 | 16806 | 19365 | 20261 | 20070 | 19817 | 17943 | 18004 | 21571 | 21401 | 21517 | 21317 | 18999 | 21527 | 22602
6354 | 6354 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 18 | 14862 | 17572 | 18608 | 18689 | 18641 | 16805 | 17018 | 19362 | 19919 | 20162 | 19842 | 18377 | 18423 | 21218 | 21348 | 21691 | 21405 | 19495 | 21823 | 22301
6355 | 6355 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 19 | 14995 | 17761 | 18487 | 18727 | 18729 | 16956 | 17293 | 19620 | 19963 | 20415 | 20424 | 18861 | 18892 | 21583 | 21892 | 22290 | 22353 | 20107 | 22449 | 22815
6356 | 6356 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 20 | 15087 | 17807 | 18644 | 18886 | 18968 | 17217 | 17538 | 19790 | 20366 | 20849 | 20920 | 19496 | 19554 | 22331 | 22780 | 23200 | 23172 | 20927 | 23035 | 23733
6357 | 6357 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 21 | 14585 | 17173 | 18014 | 18349 | 18469 | 16860 | 17181 | 19314 | 19985 | 20635 | 20773 | 19596 | 19611 | 22382 | 23003 | 23490 | 23476 | 21201 | 23141 | 23970
6358 | 6358 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 22 | 13805 | 15994 | 16823 | 17135 | 17332 | 16148 | 16480 | 18253 | 18980 | 19683 | 19952 | 19158 | 19156 | 21610 | 22281 | 22822 | 22918 | 20862 | 22398 | 23319
6359 | 6359 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 23 | 13058 | 14789 | 15515 | 15850 | 16091 | 15403 | 15670 | 17045 | 17688 | 18505 | 18823 | 18513 | 18440 | 20431 | 21151 | 21789 | 21912 | 20205 | 21324 | 22200
6360 | 6360 | 265 | 9 | 22 | Summer | 9 | 21 | Summer | 24 | 12431 | 14004 | 14678 | 14920 | 15176 | 14769 | 15071 | 16324 | 16963 | 17740 | 18046 | 17979 | 17996 | 19823 | 20397 | 21078 | 21299 | 19794 | 20790 | 21635
6361 | 6361 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 1 | 11840 | 13129 | 13831 | 13985 | 14327 | 13982 | 14585 | 15610 | 16199 | 16961 | 17314 | 16710 | 17363 | 19089 | 19631 | 20340 | 20344 | 19118 | 20472 | 20963
6362 | 6362 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 2 | 11600 | 12868 | 13479 | 13638 | 13942 | 13691 | 14373 | 15325 | 15832 | 16505 | 16914 | 16366 | 17064 | 18630 | 19167 | 19772 | 19864 | 18769 | 20044 | 20451
6363 | 6363 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 3 | 11476 | 12722 | 13313 | 13512 | 13768 | 13568 | 14359 | 15184 | 15682 | 16286 | 16716 | 16189 | 16980 | 18415 | 19016 | 19502 | 19647 | 18614 | 19785 | 20175
6364 | 6364 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 4 | 11432 | 12808 | 13377 | 13535 | 13748 | 13508 | 14419 | 15158 | 15575 | 16051 | 16370 | 15884 | 16775 | 18231 | 18649 | 19064 | 19150 | 18268 | 19509 | 19836
6365 | 6365 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 5 | 11500 | 13283 | 13882 | 13983 | 14202 | 13553 | 14913 | 15557 | 15916 | 16248 | 16225 | 15661 | 16973 | 18166 | 18425 | 18770 | 18544 | 18298 | 19242 | 19589
6366 | 6366 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 6 | 11782 | 14541 | 15153 | 15128 | 15361 | 13771 | 16096 | 16701 | 16995 | 17133 | 16277 | 15565 | 17786 | 18863 | 18814 | 19166 | 18213 | 18949 | 19763 | 20099
6367 | 6367 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 7 | 12094 | 15837 | 16435 | 16369 | 16469 | 13954 | 17257 | 17741 | 18113 | 18048 | 16297 | 15492 | 18601 | 19621 | 19470 | 19739 | 18016 | 19656 | 20311 | 20700
6368 | 6368 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 8 | 12378 | 16116 | 16809 | 16703 | 16792 | 14202 | 17544 | 17832 | 18388 | 18275 | 16498 | 15618 | 18791 | 19705 | 19609 | 19942 | 18198 | 19789 | 20091 | 20686
6369 | 6369 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 9 | 13154 | 16615 | 17280 | 17228 | 17372 | 15052 | 17970 | 18277 | 18725 | 18826 | 17007 | 16361 | 19172 | 19948 | 19972 | 20510 | 18644 | 20117 | 20342 | 20863
6370 | 6370 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 10 | 13720 | 17294 | 17862 | 17888 | 17769 | 15726 | 18520 | 19047 | 19129 | 19436 | 17588 | 17109 | 19801 | 20377 | 20501 | 21255 | 19176 | 20780 | 21058 | 21346
6371 | 6371 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 11 | 13915 | 17489 | 17985 | 18027 | 17935 | 15961 | 18686 | 19320 | 19230 | 19700 | 17713 | 17408 | 20047 | 20425 | 20686 | 21596 | 19293 | 21045 | 21300 | 21445
6372 | 6372 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 12 | 14134 | 17730 | 18124 | 18190 | 18109 | 16241 | 18903 | 19603 | 19376 | 19953 | 17872 | 17722 | 20290 | 20463 | 20906 | 21883 | 19441 | 21305 | 21475 | 21506
6373 | 6373 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 13 | 14153 | 17808 | 18166 | 18231 | 18153 | 16236 | 18918 | 19611 | 19433 | 19916 | 17634 | 17682 | 20278 | 20553 | 21036 | 21891 | 19275 | 21305 | 21539 | 21597
6374 | 6374 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 14 | 14103 | 18006 | 18382 | 18396 | 18242 | 16223 | 19071 | 19859 | 19617 | 20056 | 17633 | 17673 | 20436 | 20715 | 21112 | 21936 | 19140 | 21436 | 21706 | 21744
6375 | 6375 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 15 | 14203 | 18128 | 18470 | 18547 | 18345 | 16229 | 19114 | 19905 | 19779 | 20007 | 17504 | 17631 | 20432 | 20897 | 21249 | 21714 | 19001 | 21417 | 21893 | 21913
6376 | 6376 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 16 | 14576 | 18451 | 18799 | 18729 | 18478 | 16462 | 19321 | 20294 | 20112 | 19907 | 17567 | 17764 | 20547 | 21209 | 21301 | 21415 | 19045 | 21489 | 22489 | 22194
6377 | 6377 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 17 | 14909 | 18579 | 18888 | 18843 | 18455 | 16723 | 19416 | 20320 | 20241 | 19838 | 17676 | 18021 | 20632 | 21382 | 21502 | 21304 | 19173 | 21594 | 22663 | 22382
6378 | 6378 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 18 | 14626 | 17963 | 18413 | 18395 | 18055 | 16624 | 19073 | 19669 | 19797 | 19509 | 17832 | 18121 | 20561 | 21012 | 21381 | 21116 | 19317 | 21601 | 22078 | 22099
6379 | 6379 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 19 | 14835 | 17818 | 18402 | 18444 | 18379 | 16861 | 19282 | 19663 | 19881 | 19994 | 18352 | 18514 | 21028 | 21479 | 21916 | 22011 | 20216 | 22202 | 22573 | 22725
6380 | 6380 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 20 | 14999 | 17919 | 18505 | 18629 | 18505 | 17067 | 19405 | 19976 | 20294 | 20378 | 18834 | 19090 | 21432 | 22300 | 22761 | 22764 | 21051 | 22771 | 23469 | 23716
6381 | 6381 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 21 | 14511 | 17277 | 17944 | 18093 | 17953 | 16683 | 18890 | 19516 | 19991 | 20125 | 18785 | 19075 | 21313 | 22460 | 22992 | 23021 | 21415 | 22871 | 23693 | 24100
6382 | 6382 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 22 | 13725 | 16064 | 16725 | 16923 | 16873 | 15960 | 17794 | 18457 | 18983 | 19252 | 18456 | 18579 | 20453 | 21697 | 22292 | 22437 | 21336 | 22123 | 23032 | 23480
6383 | 6383 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 23 | 12961 | 14791 | 15446 | 15708 | 15658 | 15170 | 16598 | 17163 | 17737 | 18118 | 17874 | 17860 | 19337 | 20568 | 21237 | 21425 | 20892 | 21067 | 21945 | 22406
6384 | 6384 | 266 | 9 | 23 | Summer | 9 | 22 | Summer | 24 | 12346 | 13964 | 14540 | 14828 | 14752 | 14609 | 15915 | 16477 | 16923 | 17410 | 17479 | 17404 | 18764 | 19804 | 20536 | 20802 | 20564 | 20523 | 21365 | 21691
6385 | 6385 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 1 | 12011 | 13105 | 13588 | 13964 | 14095 | 14078 | 15086 | 15649 | 16110 | 16634 | 16298 | 16795 | 18262 | 19031 | 19799 | 19879 | 18949 | 20186 | 20689 | 20978
6386 | 6386 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 2 | 11833 | 12791 | 13264 | 13584 | 13759 | 13880 | 14816 | 15286 | 15710 | 16262 | 15960 | 16522 | 17895 | 18587 | 19255 | 19415 | 18535 | 19771 | 20182 | 20483
6387 | 6387 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 3 | 11787 | 12642 | 13147 | 13408 | 13607 | 13873 | 14688 | 15141 | 15583 | 16097 | 15817 | 16464 | 17721 | 18475 | 19027 | 19222 | 18400 | 19531 | 19923 | 20288
6388 | 6388 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 4 | 11895 | 12685 | 13162 | 13388 | 13482 | 13929 | 14672 | 15063 | 15407 | 15789 | 15589 | 16283 | 17606 | 18128 | 18595 | 18734 | 18082 | 19242 | 19575 | 19776
6389 | 6389 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 5 | 12469 | 13200 | 13631 | 13868 | 13581 | 14449 | 15119 | 15465 | 15697 | 15723 | 15480 | 16542 | 17570 | 17964 | 18353 | 18174 | 17634 | 18993 | 19344 | 19427
6390 | 6390 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 6 | 13741 | 14488 | 14823 | 15068 | 13945 | 15670 | 16329 | 16611 | 16616 | 15870 | 15485 | 17427 | 18310 | 18425 | 18804 | 17886 | 17362 | 19544 | 19878 | 19716
6391 | 6391 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 7 | 14981 | 15769 | 16097 | 16199 | 14307 | 16841 | 17417 | 17770 | 17611 | 15958 | 15394 | 18285 | 19016 | 19092 | 19399 | 17709 | 17033 | 20092 | 20474 | 20284
6392 | 6392 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 8 | 15240 | 16124 | 16419 | 16497 | 14680 | 17102 | 17520 | 18042 | 17888 | 16162 | 15473 | 18471 | 18889 | 19223 | 19591 | 17865 | 17092 | 19857 | 20432 | 20345
6393 | 6393 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 9 | 15271 | 16157 | 16505 | 16641 | 14850 | 17074 | 17528 | 17978 | 17959 | 16246 | 15635 | 18406 | 18751 | 19137 | 19715 | 17861 | 17234 | 19659 | 20163 | 20236
6394 | 6394 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 10 | 15187 | 16142 | 16566 | 16597 | 14740 | 17011 | 17686 | 18038 | 18067 | 16221 | 15755 | 18423 | 18810 | 19062 | 19858 | 17778 | 17446 | 19771 | 20048 | 20206
6395 | 6395 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 11 | 15383 | 16336 | 16781 | 16878 | 14869 | 17242 | 18022 | 18290 | 18320 | 16415 | 15933 | 18717 | 19065 | 19312 | 20262 | 17947 | 17640 | 20082 | 20220 | 20495
6396 | 6396 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 12 | 15489 | 16410 | 16869 | 16994 | 14914 | 17377 | 18224 | 18388 | 18462 | 16492 | 16110 | 18884 | 19143 | 19454 | 20471 | 18015 | 17833 | 20179 | 20209 | 20660
6397 | 6397 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 13 | 15665 | 16572 | 17024 | 17108 | 14819 | 17507 | 18346 | 18485 | 18560 | 16354 | 15966 | 18979 | 19305 | 19689 | 20585 | 17975 | 17731 | 20346 | 20404 | 20904
6398 | 6398 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 14 | 15764 | 16736 | 17158 | 17201 | 14785 | 17629 | 18562 | 18694 | 18721 | 16328 | 16029 | 19105 | 19463 | 19746 | 20608 | 17815 | 17715 | 20486 | 20523 | 20947
6399 | 6399 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 15 | 15899 | 16849 | 17344 | 17257 | 14759 | 17709 | 18644 | 18758 | 18836 | 16232 | 16027 | 19135 | 19702 | 19918 | 20418 | 17710 | 17562 | 20700 | 20719 | 21096
6400 | 6400 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 16 | 16350 | 17349 | 17709 | 17487 | 15108 | 18103 | 19182 | 19143 | 19035 | 16473 | 16359 | 19418 | 20479 | 20156 | 20296 | 17915 | 17736 | 21461 | 21163 | 21283
6401 | 6401 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 17 | 16757 | 17776 | 18150 | 17737 | 15619 | 18536 | 19544 | 19504 | 19439 | 16905 | 17014 | 19844 | 20962 | 20681 | 20515 | 18372 | 18294 | 21962 | 21679 | 21824
6402 | 6402 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 18 | 16734 | 17710 | 18053 | 17703 | 16009 | 18602 | 19307 | 19426 | 19605 | 17423 | 17624 | 20158 | 20735 | 20960 | 20728 | 18915 | 18951 | 21803 | 21806 | 22162
6403 | 6403 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 19 | 16991 | 17815 | 18186 | 18107 | 16369 | 18893 | 19380 | 19567 | 19882 | 17993 | 18219 | 20661 | 21143 | 21544 | 21682 | 19887 | 19914 | 22377 | 22527 | 22903
6404 | 6404 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 20 | 17016 | 17911 | 18360 | 18224 | 16536 | 19015 | 19661 | 19942 | 20233 | 18400 | 18787 | 21034 | 21837 | 22353 | 22408 | 20720 | 20776 | 23286 | 23531 | 23873
6405 | 6405 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 21 | 16375 | 17342 | 17815 | 17657 | 16127 | 18505 | 19168 | 19587 | 19946 | 18279 | 18785 | 20875 | 21819 | 22535 | 22630 | 21075 | 21112 | 23523 | 23926 | 24269
6406 | 6406 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 22 | 15179 | 16096 | 16609 | 16546 | 15525 | 17378 | 18064 | 18521 | 18937 | 17878 | 18213 | 19972 | 20992 | 21793 | 22005 | 20953 | 20737 | 22856 | 23291 | 23652
6407 | 6407 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 23 | 13984 | 14800 | 15371 | 15328 | 14835 | 16171 | 16743 | 17241 | 17754 | 17262 | 17466 | 18824 | 19831 | 20715 | 20971 | 20475 | 20072 | 21747 | 22207 | 22623
6408 | 6408 | 267 | 9 | 24 | Summer | 9 | 23 | Summer | 24 | 13230 | 13870 | 14467 | 14451 | 14271 | 15462 | 16021 | 16462 | 17038 | 16859 | 16993 | 18233 | 19206 | 19982 | 20338 | 20134 | 19647 | 21165 | 21487 | 21937
6409 | 6409 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 1 | 12573 | 13154 | 13840 | 13978 | 13779 | 14823 | 15398 | 15770 | 16406 | 15985 | 16707 | 17883 | 18678 | 19473 | 19653 | 18772 | 19303 | 20706 | 20994 | 21441
6410 | 6410 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 2 | 12329 | 12841 | 13467 | 13643 | 13484 | 14549 | 15031 | 15380 | 15977 | 15654 | 16460 | 17535 | 18247 | 18944 | 19193 | 18369 | 19002 | 20202 | 20493 | 20845
6411 | 6411 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 3 | 12196 | 12726 | 13311 | 13509 | 13352 | 14452 | 14924 | 15304 | 15778 | 15580 | 16476 | 17384 | 18056 | 18732 | 19003 | 18242 | 18930 | 19931 | 20299 | 20564
6412 | 6412 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 4 | 12268 | 12830 | 13410 | 13516 | 13323 | 14617 | 15061 | 15362 | 15590 | 15621 | 16519 | 17330 | 17912 | 18363 | 18561 | 17955 | 18616 | 19601 | 19799 | 20030
6413 | 6413 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 5 | 12741 | 13254 | 13854 | 13566 | 13405 | 15013 | 15412 | 15614 | 15851 | 15463 | 16795 | 17343 | 17898 | 18164 | 18034 | 17542 | 18705 | 19370 | 19452 | 19641
6414 | 6414 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 6 | 14001 | 14422 | 15045 | 13910 | 13649 | 16200 | 16547 | 16536 | 16809 | 15450 | 17603 | 18154 | 18639 | 18664 | 17779 | 17285 | 19315 | 19915 | 19733 | 19962
6415 | 6415 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 7 | 15291 | 15682 | 16193 | 14280 | 13779 | 17291 | 17716 | 17560 | 17774 | 15367 | 18579 | 18916 | 19447 | 19272 | 17624 | 16967 | 20163 | 20522 | 20286 | 20472
6416 | 6416 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 8 | 15612 | 16070 | 16570 | 14723 | 14035 | 17478 | 18072 | 17934 | 18059 | 15536 | 18926 | 18885 | 19582 | 19546 | 17865 | 17091 | 20454 | 20558 | 20413 | 20675
6417 | 6417 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 9 | 16022 | 16518 | 17099 | 15260 | 14693 | 17849 | 18379 | 18365 | 18533 | 16069 | 18962 | 19141 | 19762 | 20055 | 18247 | 17601 | 20429 | 20676 | 20674 | 21151
6418 | 6418 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 10 | 16758 | 17175 | 17649 | 15726 | 15408 | 18533 | 18951 | 18989 | 19196 | 16679 | 19062 | 19861 | 20250 | 20841 | 18821 | 18480 | 20763 | 21213 | 21303 | 21984
6419 | 6419 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 11 | 17054 | 17396 | 17901 | 15821 | 15574 | 18786 | 19114 | 19149 | 19557 | 16738 | 18965 | 20151 | 20401 | 21289 | 19025 | 18720 | 20842 | 21419 | 21634 | 22463
6420 | 6420 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 12 | 17289 | 17511 | 18021 | 15855 | 15800 | 18943 | 19152 | 19222 | 19806 | 16830 | 18876 | 20299 | 20433 | 21571 | 19169 | 18987 | 20926 | 21479 | 21886 | 22780
6421 | 6421 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 13 | 17378 | 17612 | 18076 | 15714 | 15617 | 19023 | 19217 | 19297 | 19787 | 16659 | 18770 | 20365 | 20541 | 21584 | 19028 | 18796 | 20772 | 21575 | 22027 | 22816
6422 | 6422 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 14 | 17540 | 17723 | 18141 | 15647 | 15672 | 19198 | 19379 | 19412 | 19905 | 16672 | 18635 | 20525 | 20675 | 21608 | 18869 | 18780 | 20637 | 21689 | 22064 | 22812
6423 | 6423 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 15 | 17566 | 17841 | 18149 | 15589 | 15591 | 19286 | 19465 | 19566 | 19758 | 16731 | 18592 | 20626 | 20749 | 21285 | 18630 | 18486 | 20306 | 21745 | 22077 | 22474
6424 | 6424 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 16 | 17842 | 18089 | 18269 | 15858 | 15831 | 19754 | 19812 | 19764 | 19638 | 17056 | 18775 | 21190 | 21014 | 20966 | 18631 | 18464 | 20193 | 21976 | 22056 | 22094
6425 | 6425 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 17 | 17973 | 18233 | 18210 | 16079 | 16173 | 19842 | 19896 | 19908 | 19570 | 17448 | 19073 | 21338 | 21174 | 20852 | 18755 | 18702 | 20390 | 22145 | 22263 | 21990
6426 | 6426 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 18 | 17445 | 17753 | 17755 | 16073 | 16269 | 19244 | 19456 | 19633 | 19293 | 17631 | 19244 | 20750 | 20883 | 20707 | 18945 | 19003 | 20706 | 21947 | 22266 | 21921
6427 | 6427 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 19 | 17281 | 17782 | 18045 | 16323 | 16617 | 19212 | 19487 | 19782 | 19712 | 18094 | 19914 | 20994 | 21293 | 21509 | 19764 | 19824 | 21602 | 22539 | 22878 | 22859
6428 | 6428 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 20 | 17388 | 17929 | 18134 | 16476 | 16887 | 19471 | 19815 | 20072 | 20053 | 18594 | 20312 | 21620 | 22077 | 22188 | 20562 | 20664 | 22325 | 23542 | 23855 | 23704
6429 | 6429 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 21 | 16743 | 17353 | 17520 | 16012 | 16572 | 18926 | 19388 | 19702 | 19720 | 18487 | 19996 | 21506 | 22167 | 22319 | 20849 | 20952 | 22343 | 23906 | 24230 | 24056
6430 | 6430 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 22 | 15508 | 16141 | 16384 | 15379 | 15798 | 17779 | 18257 | 18650 | 18783 | 17866 | 19161 | 20623 | 21337 | 21642 | 20684 | 20550 | 21689 | 23245 | 23612 | 23520
6431 | 6431 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 23 | 14227 | 14884 | 15165 | 14685 | 14954 | 16458 | 16974 | 17419 | 17607 | 17087 | 18146 | 19427 | 20177 | 20592 | 20195 | 19865 | 20747 | 22161 | 22571 | 22524
6432 | 6432 | 268 | 9 | 25 | Summer | 9 | 24 | Summer | 24 | 13421 | 13969 | 14285 | 14121 | 14349 | 15721 | 16173 | 16681 | 16883 | 16627 | 17547 | 18805 | 19416 | 19973 | 19857 | 19452 | 20175 | 21449 | 21903 | 21961
6433 | 6433 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 1 | 12514 | 13062 | 13500 | 13371 | 13829 | 14768 | 15143 | 15719 | 16061 | 16036 | 17566 | 17958 | 18555 | 19013 | 18276 | 18818 | 20496 | 20658 | 21121 | 20936
6434 | 6434 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 2 | 12213 | 12717 | 13192 | 13081 | 13643 | 14426 | 14781 | 15311 | 15696 | 15833 | 17239 | 17543 | 18121 | 18576 | 17893 | 18524 | 20056 | 20162 | 20539 | 20444
6435 | 6435 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 3 | 12089 | 12556 | 13055 | 12977 | 13666 | 14324 | 14715 | 15179 | 15594 | 15891 | 17164 | 17380 | 18023 | 18413 | 17777 | 18467 | 19864 | 19980 | 20264 | 20217
6436 | 6436 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 4 | 12211 | 12647 | 13063 | 13073 | 13814 | 14480 | 14806 | 15228 | 15549 | 15991 | 17115 | 17299 | 17736 | 18021 | 17527 | 18180 | 19479 | 19503 | 19743 | 19663
6437 | 6437 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 5 | 12689 | 13106 | 13134 | 13116 | 14339 | 14875 | 15116 | 15468 | 15447 | 16326 | 17320 | 17357 | 17632 | 17542 | 17139 | 18300 | 19412 | 19172 | 19369 | 19007
6438 | 6438 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 6 | 13969 | 14333 | 13524 | 13371 | 15490 | 16075 | 16121 | 16469 | 15604 | 17212 | 18233 | 18209 | 18163 | 17357 | 16937 | 18966 | 20050 | 19486 | 19715 | 18647
6439 | 6439 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 7 | 15221 | 15513 | 13932 | 13507 | 16748 | 17287 | 17201 | 17469 | 15698 | 18246 | 19059 | 19060 | 18872 | 17239 | 16647 | 19818 | 20610 | 20048 | 20222 | 18402
6440 | 6440 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 8 | 15628 | 15899 | 14391 | 13755 | 17132 | 17644 | 17578 | 17776 | 15985 | 18601 | 19002 | 19202 | 19081 | 17476 | 16759 | 20102 | 20425 | 20167 | 20410 | 18581
6441 | 6441 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 9 | 15948 | 16315 | 14853 | 14320 | 17107 | 17866 | 17928 | 18153 | 16350 | 18550 | 18915 | 19318 | 19295 | 17790 | 17207 | 19999 | 20289 | 20341 | 20791 | 18838
6442 | 6442 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 10 | 16052 | 16355 | 14783 | 14376 | 16739 | 17849 | 17963 | 18058 | 16330 | 18027 | 18635 | 19295 | 19395 | 17858 | 17573 | 19833 | 20297 | 20467 | 21126 | 18956
6443 | 6443 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 11 | 16119 | 16470 | 14754 | 14327 | 16556 | 17860 | 17972 | 18127 | 16297 | 17765 | 18491 | 19321 | 19559 | 17931 | 17685 | 19796 | 20333 | 20672 | 21485 | 19074
6444 | 6444 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 12 | 16179 | 16564 | 14769 | 14435 | 16471 | 17876 | 18019 | 18201 | 16260 | 17629 | 18363 | 19325 | 19741 | 18047 | 17924 | 19853 | 20297 | 20890 | 21772 | 19205
6445 | 6445 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 13 | 16345 | 16734 | 14718 | 14389 | 16479 | 18041 | 18195 | 18351 | 16173 | 17634 | 18298 | 19491 | 19949 | 17963 | 17793 | 19759 | 20165 | 21092 | 21861 | 19131
6446 | 6446 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 14 | 16648 | 16970 | 14814 | 14571 | 16530 | 18368 | 18473 | 18581 | 16264 | 17669 | 18338 | 19800 | 20172 | 17979 | 17946 | 19794 | 20186 | 21295 | 22042 | 19127
6447 | 6447 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 15 | 16844 | 17136 | 14916 | 14763 | 16635 | 18609 | 18784 | 18772 | 16381 | 17785 | 18463 | 20047 | 20360 | 17913 | 17826 | 19629 | 20151 | 21469 | 21866 | 19044
6448 | 6448 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 16 | 17290 | 17352 | 15279 | 15214 | 16969 | 19048 | 19085 | 18943 | 16706 | 18080 | 19055 | 20430 | 20493 | 18019 | 17903 | 19619 | 20620 | 21544 | 21584 | 19119
6449 | 6449 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 17 | 17563 | 17467 | 15685 | 15792 | 17411 | 19351 | 19456 | 19182 | 17014 | 18624 | 19434 | 20724 | 20832 | 18289 | 18277 | 19943 | 20849 | 21888 | 21610 | 19403
6450 | 6450 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 18 | 17229 | 17084 | 15723 | 15924 | 17462 | 19025 | 19259 | 18918 | 17196 | 18863 | 19310 | 20489 | 20810 | 18545 | 18640 | 20336 | 20825 | 21965 | 21610 | 19710
6451 | 6451 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 19 | 17245 | 17350 | 15963 | 16296 | 17963 | 19043 | 19387 | 19340 | 17659 | 19488 | 20092 | 20855 | 21251 | 19325 | 19442 | 21233 | 21880 | 22589 | 22578 | 20645
6452 | 6452 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 20 | 17303 | 17379 | 16077 | 16528 | 18134 | 19324 | 19614 | 19588 | 17986 | 19806 | 20626 | 21547 | 21985 | 20056 | 20246 | 21913 | 22739 | 23553 | 23403 | 21543
6453 | 6453 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 21 | 16718 | 16766 | 15598 | 16206 | 17531 | 18876 | 19206 | 19184 | 17782 | 19434 | 20435 | 21564 | 22100 | 20299 | 20522 | 21908 | 22944 | 23941 | 23775 | 21980
6454 | 6454 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 22 | 15466 | 15652 | 14969 | 15438 | 16523 | 17737 | 18145 | 18223 | 17341 | 18597 | 19700 | 20709 | 21330 | 20127 | 20113 | 21266 | 22435 | 23340 | 23262 | 21935
6455 | 6455 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 23 | 14169 | 14432 | 14255 | 14585 | 15423 | 16437 | 16890 | 17010 | 16683 | 17544 | 18719 | 19518 | 20217 | 19615 | 19406 | 20300 | 21585 | 22284 | 22251 | 21477
6456 | 6456 | 269 | 9 | 26 | Summer | 9 | 25 | Summer | 24 | 13256 | 13525 | 13650 | 13939 | 14673 | 15560 | 16064 | 16192 | 16269 | 16866 | 18038 | 18751 | 19489 | 19283 | 19007 | 19736 | 21033 | 21625 | 21686 | 21192
6457 | 6457 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 1 | 12486 | 13003 | 13214 | 13682 | 14663 | 14799 | 15381 | 15663 | 15394 | 17137 | 18027 | 18101 | 18901 | 17980 | 18599 | 20259 | 21171 | 21055 | 20887 | 19652
6458 | 6458 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 2 | 12195 | 12674 | 12914 | 13491 | 14383 | 14429 | 14967 | 15314 | 15089 | 16824 | 17719 | 17664 | 18380 | 17582 | 18287 | 19808 | 20743 | 20450 | 20370 | 19207
6459 | 6459 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 3 | 12082 | 12538 | 12825 | 13533 | 14315 | 14398 | 14878 | 15268 | 15029 | 16831 | 17650 | 17587 | 18193 | 17481 | 18243 | 19623 | 20478 | 20177 | 20147 | 19056
6460 | 6460 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 4 | 12198 | 12495 | 12863 | 13627 | 14406 | 14444 | 14879 | 15182 | 15100 | 16753 | 17464 | 17355 | 17872 | 17251 | 17971 | 19258 | 20041 | 19654 | 19598 | 18721
6461 | 6461 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 5 | 12632 | 12582 | 12917 | 14168 | 14942 | 14787 | 15176 | 15140 | 15001 | 17020 | 17540 | 17316 | 17747 | 16904 | 18123 | 19223 | 19775 | 19301 | 18950 | 18233
6462 | 6462 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 6 | 13813 | 12976 | 13167 | 15321 | 16180 | 15805 | 16216 | 15354 | 15045 | 17982 | 18319 | 17905 | 18306 | 16716 | 18781 | 19861 | 20231 | 19633 | 18576 | 17907
6463 | 6463 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 7 | 15112 | 13433 | 13350 | 16628 | 17332 | 16928 | 17283 | 15547 | 15033 | 18881 | 19155 | 18706 | 18985 | 16470 | 19670 | 20467 | 20798 | 20157 | 18348 | 17567
6464 | 6464 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 8 | 15504 | 13951 | 13659 | 17036 | 17510 | 17337 | 17648 | 15893 | 15230 | 18896 | 19242 | 18953 | 19296 | 16626 | 19997 | 20321 | 20735 | 20388 | 18558 | 17683
6465 | 6465 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 9 | 15751 | 14316 | 14127 | 16885 | 17412 | 17578 | 17920 | 16152 | 15571 | 18720 | 19027 | 19066 | 19613 | 16969 | 19786 | 20074 | 20427 | 20660 | 18701 | 17978
6466 | 6466 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 10 | 15851 | 14272 | 14232 | 16481 | 17168 | 17654 | 17873 | 16052 | 15567 | 18466 | 18749 | 19143 | 19905 | 17341 | 19628 | 20074 | 20279 | 21005 | 18822 | 18393
6467 | 6467 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 11 | 15919 | 14277 | 14217 | 16302 | 17005 | 17708 | 17992 | 16035 | 15446 | 18380 | 18676 | 19251 | 20180 | 17410 | 19551 | 20060 | 20232 | 21317 | 18900 | 18499
6468 | 6468 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 12 | 15873 | 14195 | 14253 | 16169 | 16774 | 17706 | 18033 | 15987 | 15370 | 18230 | 18554 | 19289 | 20293 | 17500 | 19461 | 19871 | 20040 | 21454 | 18885 | 18599
6469 | 6469 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 13 | 16085 | 14193 | 14260 | 16252 | 16750 | 17939 | 18235 | 15994 | 15336 | 18231 | 18596 | 19533 | 20393 | 17411 | 19409 | 19773 | 20002 | 21576 | 18852 | 18505
6470 | 6470 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 14 | 16288 | 14183 | 14346 | 16209 | 16742 | 18117 | 18368 | 15984 | 15433 | 18175 | 18606 | 19682 | 20518 | 17483 | 19361 | 19714 | 20015 | 21670 | 18762 | 18560
6471 | 6471 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 15 | 16610 | 14298 | 14536 | 16309 | 16905 | 18409 | 18533 | 16066 | 15692 | 18261 | 18759 | 19938 | 20414 | 17407 | 19241 | 19732 | 20167 | 21536 | 18721 | 18471
6472 | 6472 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 16 | 17187 | 14861 | 15198 | 16850 | 17648 | 18911 | 18901 | 16582 | 16350 | 19028 | 19054 | 20327 | 20440 | 17727 | 19471 | 20446 | 20393 | 21499 | 19029 | 18773
6473 | 6473 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 17 | 17595 | 15322 | 15828 | 17412 | 18033 | 19316 | 19177 | 17020 | 17078 | 19432 | 19323 | 20758 | 20557 | 18199 | 19899 | 20772 | 20688 | 21636 | 19399 | 19264
6474 | 6474 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 18 | 17142 | 15267 | 15806 | 17368 | 17882 | 19005 | 18752 | 17066 | 17294 | 19136 | 19199 | 20645 | 20406 | 18491 | 20215 | 20689 | 20756 | 21572 | 19662 | 19613
6475 | 6475 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 19 | 17145 | 15466 | 16134 | 17830 | 18408 | 19101 | 19126 | 17473 | 17703 | 19844 | 20019 | 20994 | 21134 | 19236 | 21048 | 21680 | 21864 | 22482 | 20560 | 20463
6476 | 6476 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 20 | 17262 | 15554 | 16339 | 17983 | 18609 | 19299 | 19329 | 17744 | 18143 | 20292 | 20622 | 21662 | 21746 | 19991 | 21689 | 22521 | 22869 | 23307 | 21458 | 21356
6477 | 6477 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 21 | 16651 | 15042 | 15963 | 17326 | 18006 | 18832 | 18848 | 17437 | 17962 | 19984 | 20458 | 21658 | 21788 | 20190 | 21619 | 22662 | 23148 | 23645 | 21856 | 21705
6478 | 6478 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 22 | 15446 | 14357 | 15169 | 16304 | 17007 | 17717 | 17837 | 16947 | 17320 | 19197 | 19791 | 20823 | 21106 | 19742 | 20944 | 22133 | 22761 | 23119 | 21798 | 21353
6479 | 6479 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 23 | 14166 | 13641 | 14316 | 15212 | 15885 | 16474 | 16610 | 16265 | 16499 | 18204 | 18787 | 19689 | 20003 | 19022 | 19988 | 21266 | 21867 | 22103 | 21346 | 20684
6480 | 6480 | 270 | 9 | 27 | Summer | 9 | 26 | Summer | 24 | 13209 | 13014 | 13636 | 14399 | 15069 | 15600 | 15739 | 15730 | 15934 | 17491 | 18137 | 18934 | 19360 | 18584 | 19396 | 20693 | 21323 | 21505 | 21036 | 20286
6481 | 6481 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 1 | 12124 | 12190 | 12987 | 14004 | 14381 | 14507 | 14825 | 14614 | 15231 | 17051 | 17727 | 17907 | 18226 | 17756 | 19445 | 20371 | 20903 | 20275 | 19089 | 19431
6482 | 6482 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 2 | 11782 | 11891 | 12808 | 13716 | 14116 | 14096 | 14473 | 14304 | 15033 | 16750 | 17400 | 17396 | 17782 | 17465 | 19010 | 19943 | 20470 | 19771 | 18655 | 19102
6483 | 6483 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 3 | 11642 | 11773 | 12824 | 13660 | 14045 | 13985 | 14404 | 14277 | 15139 | 16693 | 17277 | 17228 | 17632 | 17430 | 18823 | 19698 | 20198 | 19554 | 18503 | 19020
6484 | 6484 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 4 | 11709 | 11814 | 12931 | 13721 | 14081 | 14024 | 14359 | 14317 | 15198 | 16586 | 17059 | 16981 | 17287 | 17210 | 18509 | 19306 | 19687 | 19035 | 18177 | 18683
6485 | 6485 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 5 | 12165 | 11874 | 13461 | 14261 | 14449 | 14342 | 14349 | 14248 | 15563 | 16717 | 17021 | 16908 | 16849 | 17382 | 18496 | 19058 | 19312 | 18388 | 17676 | 18706
6486 | 6486 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 6 | 13401 | 12193 | 14673 | 15564 | 15595 | 15464 | 14676 | 14407 | 16501 | 17637 | 17589 | 17567 | 16719 | 18110 | 19199 | 19567 | 19500 | 18043 | 17375 | 19306
6487 | 6487 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 7 | 14670 | 12480 | 16090 | 16833 | 16836 | 16650 | 15025 | 14557 | 17649 | 18629 | 18291 | 18370 | 16717 | 19075 | 19883 | 20218 | 19862 | 17874 | 17084 | 20195
6488 | 6488 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 8 | 15113 | 12867 | 16582 | 17121 | 17138 | 17120 | 15508 | 14908 | 18062 | 18884 | 18643 | 18745 | 17010 | 19423 | 19783 | 20201 | 19948 | 18114 | 17224 | 20526
6489 | 6489 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 9 | 15772 | 13773 | 16882 | 17451 | 17396 | 17841 | 16243 | 15731 | 18289 | 19176 | 18977 | 19437 | 17586 | 19612 | 19924 | 20280 | 20110 | 18630 | 17889 | 20677
6490 | 6490 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 10 | 16357 | 14547 | 17162 | 17937 | 17666 | 18550 | 16921 | 16571 | 18320 | 19733 | 19490 | 20247 | 18171 | 19967 | 20444 | 20659 | 20405 | 19271 | 18823 | 21061
6491 | 6491 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 11 | 16571 | 14689 | 17136 | 17969 | 17675 | 18823 | 17059 | 16703 | 18239 | 19826 | 19748 | 20599 | 18310 | 19989 | 20531 | 20697 | 20646 | 19447 | 19031 | 21114
6492 | 6492 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 12 | 16780 | 14927 | 17224 | 18043 | 17749 | 19081 | 17236 | 16984 | 18307 | 19936 | 19948 | 20911 | 18493 | 20102 | 20549 | 20707 | 20813 | 19638 | 19341 | 21221
6493 | 6493 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 13 | 16965 | 14890 | 17231 | 17967 | 17745 | 19175 | 17131 | 16873 | 18343 | 19839 | 20031 | 20994 | 18412 | 20014 | 20410 | 20638 | 20969 | 19562 | 19205 | 21126
6494 | 6494 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 14 | 17020 | 14850 | 17095 | 17859 | 17684 | 19226 | 17042 | 16869 | 18182 | 19775 | 20022 | 21018 | 18258 | 19868 | 20258 | 20546 | 20910 | 19376 | 19162 | 20963
6495 | 6495 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 15 | 16981 | 14753 | 16873 | 17622 | 17644 | 19009 | 16721 | 16623 | 18041 | 19481 | 19894 | 20694 | 18018 | 19528 | 20052 | 20472 | 20993 | 19109 | 18849 | 20607
6496 | 6496 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 16 | 17054 | 14971 | 16969 | 17827 | 17666 | 18880 | 16717 | 16681 | 18154 | 19206 | 19739 | 20380 | 18005 | 19408 | 20411 | 20346 | 20956 | 19059 | 18789 | 20464
6497 | 6497 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 17 | 16862 | 15140 | 17064 | 17702 | 17617 | 18645 | 16630 | 16807 | 18345 | 18921 | 19636 | 20114 | 17992 | 19456 | 20349 | 20272 | 21011 | 19055 | 18893 | 20531
6498 | 6498 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 18 | 16233 | 14928 | 16812 | 17365 | 17340 | 18062 | 16490 | 16739 | 18294 | 18596 | 19769 | 19779 | 18029 | 19610 | 20119 | 20186 | 21377 | 19184 | 19108 | 20746
6499 | 6499 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 19 | 16419 | 15198 | 17230 | 17860 | 17803 | 18378 | 16832 | 17104 | 18844 | 19308 | 20439 | 20413 | 18704 | 20385 | 21046 | 21224 | 22385 | 20032 | 19940 | 21627
6500 | 6500 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 20 | 16400 | 15353 | 17342 | 17994 | 18013 | 18536 | 17039 | 17464 | 19089 | 19802 | 20833 | 20923 | 19354 | 20969 | 21832 | 22162 | 23169 | 20903 | 20807 | 22340
6501 | 6501 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 21 | 15754 | 14967 | 16672 | 17359 | 17427 | 18026 | 16681 | 17236 | 18636 | 19540 | 20707 | 20888 | 19507 | 20863 | 21920 | 22413 | 23495 | 21304 | 21158 | 22386
6502 | 6502 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 22 | 14630 | 14168 | 15630 | 16340 | 16467 | 16989 | 16154 | 16549 | 17743 | 18820 | 20057 | 20140 | 19284 | 20157 | 21364 | 21994 | 23112 | 21239 | 20815 | 21778
6503 | 6503 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 23 | 13440 | 13325 | 14542 | 15242 | 15367 | 15772 | 15467 | 15733 | 16697 | 17807 | 19189 | 19048 | 18766 | 19188 | 20494 | 21112 | 22383 | 20794 | 20155 | 20843
6504 | 6504 | 271 | 9 | 28 | Summer | 9 | 27 | Summer | 24 | 12543 | 12695 | 13763 | 14466 | 14606 | 14946 | 14979 | 15221 | 16003 | 17249 | 18727 | 18385 | 18417 | 18596 | 19918 | 20560 | 21939 | 20482 | 19760 | 20281
6505 | 6505 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 1 | 12160 | 12607 | 13908 | 14314 | 14684 | 14565 | 14446 | 15064 | 16409 | 17322 | 18003 | 17847 | 17358 | 19198 | 20161 | 20714 | 21288 | 19134 | 19494 | 21039
6506 | 6506 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 2 | 11850 | 12443 | 13652 | 14062 | 14411 | 14236 | 14157 | 14876 | 16105 | 17039 | 17588 | 17444 | 16987 | 18795 | 19765 | 20315 | 20749 | 18730 | 19184 | 20590
6507 | 6507 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 3 | 11710 | 12429 | 13582 | 13972 | 14311 | 14155 | 14117 | 14962 | 16107 | 16941 | 17428 | 17322 | 16909 | 18640 | 19537 | 20067 | 20459 | 18582 | 19105 | 20377
6508 | 6508 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 4 | 11704 | 12578 | 13673 | 14049 | 14350 | 14151 | 14204 | 15079 | 16113 | 16822 | 17189 | 17065 | 16766 | 18397 | 19212 | 19625 | 19923 | 18296 | 18802 | 19991
6509 | 6509 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 5 | 11766 | 13091 | 14211 | 14435 | 14657 | 14170 | 14162 | 15484 | 16411 | 16857 | 17106 | 16689 | 16435 | 18421 | 19000 | 19279 | 19481 | 17796 | 18828 | 19838
6510 | 6510 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 6 | 12236 | 14372 | 15557 | 15673 | 15658 | 14570 | 14410 | 16560 | 17530 | 17553 | 17571 | 16677 | 16353 | 19210 | 19594 | 19544 | 19573 | 17546 | 19471 | 20456
6511 | 6511 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 7 | 12735 | 15758 | 16816 | 16931 | 16616 | 14906 | 14566 | 17775 | 18567 | 18287 | 18245 | 16695 | 16163 | 19889 | 20239 | 19879 | 19946 | 17217 | 20314 | 21003
6512 | 6512 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 8 | 13370 | 16263 | 17154 | 17341 | 17097 | 15424 | 14954 | 18346 | 18775 | 18687 | 18623 | 17069 | 16393 | 19818 | 20264 | 20014 | 20127 | 17381 | 20662 | 20862
6513 | 6513 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 9 | 14141 | 16552 | 17473 | 17635 | 17507 | 16119 | 15744 | 18645 | 19073 | 18986 | 18936 | 17657 | 17104 | 19950 | 20338 | 20172 | 20330 | 18043 | 20792 | 20945
6514 | 6514 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 10 | 14664 | 16709 | 17819 | 17943 | 17859 | 16595 | 16371 | 18767 | 19591 | 19251 | 19245 | 18176 | 17931 | 20396 | 20646 | 20402 | 20738 | 18903 | 21108 | 21432
6515 | 6515 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 11 | 14705 | 16597 | 17751 | 17874 | 17935 | 16598 | 16366 | 18609 | 19577 | 19356 | 19327 | 18219 | 17999 | 20397 | 20600 | 20551 | 20885 | 19029 | 21083 | 21480
6516 | 6516 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 12 | 14767 | 16621 | 17754 | 17886 | 18028 | 16692 | 16560 | 18612 | 19593 | 19471 | 19394 | 18339 | 18230 | 20369 | 20550 | 20652 | 20966 | 19277 | 21131 | 21448
6517 | 6517 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 13 | 14607 | 16572 | 17628 | 17776 | 18069 | 16541 | 16411 | 18527 | 19395 | 19524 | 19359 | 18176 | 18036 | 20155 | 20404 | 20727 | 20925 | 19064 | 20960 | 21228
6518 | 6518 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 14 | 14610 | 16532 | 17624 | 17824 | 18199 | 16548 | 16496 | 18469 | 19382 | 19605 | 19243 | 18146 | 18128 | 20133 | 20440 | 20797 | 20802 | 19146 | 20922 | 21185
6519 | 6519 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 15 | 14500 | 16430 | 17525 | 17789 | 18264 | 16408 | 16440 | 18309 | 19085 | 19691 | 19113 | 17957 | 17889 | 19981 | 20419 | 20929 | 20608 | 18882 | 20617 | 21015
6520 | 6520 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 16 | 14626 | 16584 | 17740 | 17771 | 18301 | 16522 | 16623 | 18355 | 19271 | 19680 | 18983 | 17961 | 17849 | 20330 | 20294 | 20901 | 20354 | 18815 | 20466 | 21353
6521 | 6521 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 17 | 14712 | 16756 | 17702 | 17709 | 18314 | 16533 | 16840 | 18471 | 19185 | 19653 | 18992 | 18014 | 17994 | 20336 | 20287 | 21023 | 20423 | 18986 | 20601 | 21374
6522 | 6522 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 18 | 14560 | 16554 | 17431 | 17484 | 18359 | 16447 | 16806 | 18410 | 18777 | 19784 | 19074 | 18057 | 18187 | 20150 | 20247 | 21440 | 20725 | 19259 | 20874 | 21240
6523 | 6523 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 19 | 14711 | 16951 | 17890 | 17926 | 18823 | 16756 | 17137 | 18915 | 19402 | 20389 | 19779 | 18670 | 18850 | 21026 | 21243 | 22412 | 21731 | 20073 | 21750 | 22264
6524 | 6524 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 20 | 14781 | 17046 | 18019 | 18106 | 18802 | 16951 | 17482 | 19122 | 19781 | 20697 | 20088 | 19261 | 19556 | 21766 | 22147 | 23172 | 22470 | 20955 | 22480 | 23180
6525 | 6525 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 21 | 14252 | 16331 | 17350 | 17453 | 18235 | 16542 | 17197 | 18590 | 19385 | 20448 | 20055 | 19299 | 19693 | 21792 | 22322 | 23433 | 22911 | 21290 | 22500 | 23385
6526 | 6526 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 22 | 13605 | 15329 | 16353 | 16525 | 17350 | 16040 | 16529 | 17710 | 18610 | 19782 | 19563 | 19081 | 19268 | 21249 | 21913 | 23075 | 22703 | 20984 | 21943 | 22969
6527 | 6527 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 23 | 12845 | 14208 | 15207 | 15374 | 16296 | 15295 | 15659 | 16595 | 17548 | 18850 | 18772 | 18491 | 18496 | 20314 | 20985 | 22281 | 22038 | 20285 | 20971 | 22106
6528 | 6528 | 272 | 9 | 29 | Summer | 9 | 28 | Summer | 24 | 12267 | 13429 | 14422 | 14643 | 15643 | 14783 | 15120 | 15946 | 16905 | 18389 | 18243 | 18115 | 18058 | 19744 | 20434 | 21816 | 21533 | 19888 | 20418 | 21585
6529 | 6529 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 1 | 11758 | 13302 | 13994 | 14372 | 14588 | 14035 | 14686 | 15926 | 16631 | 17381 | 17424 | 16853 | 17548 | 19663 | 20291 | 20871 | 20555 | 19335 | 20881 | 21641
6530 | 6530 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 2 | 11474 | 13042 | 13737 | 14098 | 14237 | 13734 | 14482 | 15629 | 16348 | 16970 | 17040 | 16496 | 17273 | 19268 | 19891 | 20339 | 20064 | 19010 | 20423 | 21194
6531 | 6531 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 3 | 11360 | 12952 | 13636 | 13979 | 14107 | 13683 | 14560 | 15619 | 16301 | 16841 | 16947 | 16426 | 17258 | 19060 | 19639 | 20058 | 19845 | 18927 | 20210 | 20921
6532 | 6532 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 4 | 11386 | 13001 | 13674 | 13991 | 14067 | 13738 | 14654 | 15623 | 16240 | 16633 | 16691 | 16290 | 17072 | 18741 | 19198 | 19513 | 19310 | 18594 | 19792 | 20444
6533 | 6533 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 5 | 11469 | 13564 | 14098 | 14357 | 14372 | 13749 | 15126 | 16008 | 16459 | 16656 | 16392 | 16042 | 17301 | 18602 | 18924 | 19140 | 18682 | 18660 | 19673 | 20111
6534 | 6534 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 6 | 11797 | 14867 | 15307 | 15361 | 15245 | 13991 | 16223 | 17157 | 17456 | 17189 | 16354 | 15995 | 18079 | 19217 | 19201 | 19237 | 18263 | 19282 | 20265 | 20521
6535 | 6535 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 7 | 12043 | 16159 | 16566 | 16345 | 16283 | 14172 | 17484 | 18253 | 18465 | 17927 | 16383 | 15852 | 19025 | 19906 | 19576 | 19626 | 17970 | 20128 | 20806 | 21035
6536 | 6536 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 8 | 12442 | 16505 | 16939 | 16782 | 16724 | 14526 | 18025 | 18455 | 18750 | 18304 | 16637 | 16063 | 19404 | 19923 | 19694 | 19783 | 18088 | 20446 | 20643 | 20957
6537 | 6537 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 9 | 13084 | 16594 | 17007 | 16936 | 16829 | 15092 | 18103 | 18531 | 18763 | 18413 | 17056 | 16549 | 19342 | 19766 | 19615 | 19743 | 18382 | 20331 | 20495 | 20736
6538 | 6538 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 10 | 13425 | 16697 | 17093 | 16955 | 16789 | 15516 | 18042 | 18712 | 18770 | 18564 | 17431 | 17046 | 19307 | 19758 | 19525 | 19827 | 18666 | 20331 | 20662 | 20770
6539 | 6539 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 11 | 13501 | 16686 | 17091 | 17072 | 16839 | 15579 | 17960 | 18738 | 18736 | 18728 | 17581 | 17152 | 19266 | 19729 | 19689 | 20012 | 18818 | 20325 | 20728 | 20784
6540 | 6540 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 12 | 13621 | 16646 | 17073 | 17121 | 16830 | 15742 | 17937 | 18708 | 18718 | 18772 | 17678 | 17341 | 19263 | 19625 | 19737 | 20049 | 18909 | 20323 | 20642 | 20695
6541 | 6541 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 13 | 13627 | 16628 | 17041 | 17259 | 16898 | 15661 | 17920 | 18612 | 18682 | 18788 | 17492 | 17231 | 19200 | 19573 | 19904 | 20084 | 18750 | 20251 | 20518 | 20639
6542 | 6542 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 14 | 13678 | 16636 | 17112 | 17400 | 16817 | 15783 | 17904 | 18609 | 18698 | 18723 | 17394 | 17338 | 19176 | 19616 | 19979 | 19980 | 18584 | 20214 | 20473 | 20663
6543 | 6543 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 15 | 13813 | 16619 | 17159 | 17620 | 16877 | 15765 | 17775 | 18468 | 18728 | 18586 | 17214 | 17233 | 19009 | 19739 | 20259 | 19923 | 18493 | 20052 | 20448 | 20772
6544 | 6544 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 16 | 14282 | 16950 | 17293 | 17886 | 17102 | 16062 | 17926 | 18829 | 18800 | 18531 | 17180 | 17398 | 19091 | 19815 | 20434 | 19872 | 18516 | 20092 | 20976 | 20819
6545 | 6545 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 17 | 14679 | 17067 | 17386 | 18073 | 17327 | 16429 | 18189 | 18905 | 18757 | 18671 | 17358 | 17697 | 19354 | 19955 | 20707 | 20114 | 18776 | 20369 | 21132 | 20973
6546 | 6546 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 18 | 14510 | 16820 | 17193 | 18115 | 17226 | 16414 | 18126 | 18508 | 18488 | 18724 | 17519 | 17860 | 19572 | 19912 | 21123 | 20413 | 19148 | 20659 | 21011 | 21004
6547 | 6547 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 19 | 14783 | 17315 | 17639 | 18582 | 17685 | 16759 | 18644 | 19127 | 19177 | 19390 | 18354 | 18513 | 20329 | 20901 | 22091 | 21417 | 20276 | 21569 | 22082 | 22153
6548 | 6548 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 20 | 14943 | 17442 | 17811 | 18539 | 17667 | 17096 | 18825 | 19459 | 19617 | 19613 | 18698 | 19168 | 20891 | 21743 | 22812 | 22127 | 20988 | 22307 | 23008 | 23215
6549 | 6549 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 21 | 14518 | 16743 | 17127 | 17916 | 17186 | 16785 | 18246 | 18996 | 19236 | 19469 | 18770 | 19230 | 20706 | 21848 | 23012 | 22503 | 21485 | 22325 | 23212 | 23538
6550 | 6550 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 22 | 13709 | 15665 | 16128 | 16956 | 16370 | 16048 | 17286 | 18112 | 18475 | 18868 | 18516 | 18715 | 19973 | 21353 | 22577 | 22221 | 21482 | 21712 | 22737 | 23195
6551 | 6551 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 23 | 12861 | 14545 | 15006 | 15944 | 15484 | 15210 | 16198 | 17066 | 17426 | 18087 | 17991 | 17961 | 18986 | 20430 | 21799 | 21585 | 21093 | 20771 | 21907 | 22343
6552 | 6552 | 273 | 9 | 30 | Summer | 9 | 29 | Summer | 24 | 12265 | 13760 | 14273 | 15303 | 14771 | 14659 | 15534 | 16414 | 16859 | 17571 | 17612 | 17535 | 18407 | 19885 | 21340 | 21099 | 20764 | 20225 | 21390 | 21852
6553 | 6553 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 1 | 11631 | 13146 | 13862 | 14078 | 13869 | 14072 | 15299 | 15926 | 16354 | 16642 | 17129 | 16874 | 18389 | 19804 | 20440 | 20203 | 19684 | 20731 | 21491 | 21807
6554 | 6554 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 2 | 11486 | 12924 | 13634 | 13771 | 13563 | 13909 | 15051 | 15699 | 16094 | 16331 | 16711 | 16678 | 18017 | 19567 | 20086 | 19861 | 19153 | 20440 | 21221 | 21527
6555 | 6555 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 3 | 11474 | 12869 | 13565 | 13696 | 13472 | 14048 | 15114 | 15732 | 16014 | 16343 | 16571 | 16815 | 17884 | 19440 | 19899 | 19718 | 18831 | 20339 | 21061 | 21333
6556 | 6556 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 4 | 11600 | 12989 | 13654 | 13737 | 13435 | 14240 | 15239 | 15806 | 15922 | 16260 | 16378 | 16841 | 17659 | 18964 | 19344 | 19145 | 18324 | 19885 | 20487 | 20690
6557 | 6557 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 5 | 12126 | 13490 | 14085 | 14117 | 13503 | 14804 | 15742 | 16174 | 16055 | 16118 | 16259 | 17142 | 17760 | 18850 | 19071 | 18618 | 17819 | 19815 | 20210 | 20378
6558 | 6558 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 6 | 13397 | 14742 | 15172 | 15095 | 13860 | 15992 | 17027 | 17324 | 16816 | 16246 | 16405 | 18021 | 18583 | 19302 | 19298 | 18281 | 17592 | 20485 | 20727 | 20640
6559 | 6559 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 7 | 14786 | 16056 | 16219 | 16210 | 14182 | 17293 | 18222 | 18417 | 17620 | 16382 | 16577 | 19099 | 19315 | 19768 | 19797 | 18039 | 17522 | 21082 | 21371 | 20986
6560 | 6560 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 8 | 15278 | 16473 | 16687 | 16641 | 14577 | 17826 | 18438 | 18690 | 18042 | 16643 | 16763 | 19544 | 19277 | 19941 | 20015 | 18172 | 17655 | 21003 | 21348 | 21094
6561 | 6561 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 9 | 15278 | 16471 | 16769 | 16655 | 14998 | 17794 | 18402 | 18619 | 18067 | 16970 | 17077 | 19375 | 19126 | 19840 | 19876 | 18444 | 17924 | 20808 | 21075 | 20951
6562 | 6562 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 10 | 15292 | 16669 | 16885 | 16806 | 15376 | 17812 | 18654 | 18863 | 18282 | 17417 | 17627 | 19449 | 19356 | 19873 | 20169 | 18769 | 18475 | 21172 | 21230 | 21021
6563 | 6563 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 11 | 15251 | 16705 | 17040 | 16937 | 15477 | 17774 | 18722 | 18949 | 18483 | 17618 | 18014 | 19464 | 19386 | 19749 | 20385 | 18681 | 18838 | 21371 | 21074 | 20957
6564 | 6564 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 12 | 15114 | 16549 | 16950 | 16797 | 15411 | 17609 | 18543 | 18795 | 18449 | 17558 | 18262 | 19305 | 19170 | 19630 | 20129 | 18481 | 19107 | 21206 | 20799 | 20866
6565 | 6565 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 13 | 14941 | 16330 | 16908 | 16667 | 15056 | 17434 | 18295 | 18571 | 18354 | 17226 | 18210 | 19117 | 18851 | 19526 | 19990 | 18087 | 19003 | 20976 | 20513 | 20769
6566 | 6566 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 14 | 14790 | 16225 | 16882 | 16448 | 14859 | 17234 | 18103 | 18441 | 18359 | 16923 | 18186 | 18872 | 18711 | 19645 | 19740 | 17829 | 19024 | 20731 | 20408 | 20866
6567 | 6567 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 15 | 14727 | 16170 | 17043 | 16384 | 14750 | 17056 | 17913 | 18304 | 18391 | 16695 | 18108 | 18608 | 18646 | 19656 | 19589 | 17824 | 18989 | 20426 | 20457 | 20851
6568 | 6568 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 16 | 15094 | 16345 | 17344 | 16555 | 14949 | 17235 | 18258 | 18265 | 18520 | 16663 | 18204 | 18635 | 19246 | 19761 | 19533 | 17997 | 19157 | 20762 | 20549 | 20899
6569 | 6569 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 17 | 15652 | 16642 | 17721 | 16961 | 15364 | 17687 | 18524 | 18367 | 18869 | 17007 | 18456 | 19058 | 19632 | 20201 | 19927 | 18533 | 19579 | 21085 | 20897 | 21335
6570 | 6570 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 18 | 15599 | 16528 | 17773 | 16870 | 15596 | 17667 | 18143 | 18131 | 19147 | 17106 | 18566 | 19175 | 19584 | 20615 | 20038 | 18797 | 19982 | 20761 | 20645 | 21815
6571 | 6571 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 19 | 16007 | 16898 | 18186 | 17269 | 16152 | 18134 | 18700 | 18734 | 19710 | 17824 | 19297 | 19807 | 20453 | 21547 | 20903 | 19870 | 20977 | 21815 | 21793 | 22904
6572 | 6572 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 20 | 16092 | 17029 | 18086 | 17238 | 16148 | 18271 | 18983 | 19111 | 19953 | 18072 | 19530 | 20340 | 21151 | 22202 | 21580 | 20479 | 21528 | 22655 | 22838 | 23758
6573 | 6573 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 21 | 15373 | 16315 | 17442 | 16738 | 15815 | 17682 | 18477 | 18673 | 19632 | 18066 | 19516 | 20113 | 21119 | 22355 | 21922 | 20968 | 21866 | 22872 | 23173 | 24134
6574 | 6574 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 22 | 14292 | 15287 | 16429 | 15861 | 15252 | 16670 | 17522 | 17829 | 18848 | 17730 | 18888 | 19321 | 20458 | 21913 | 21631 | 20977 | 21451 | 22423 | 22858 | 23820
6575 | 6575 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 23 | 13240 | 14204 | 15436 | 15004 | 14622 | 15614 | 16492 | 16775 | 17948 | 17213 | 18024 | 18350 | 19570 | 21391 | 21176 | 20755 | 20690 | 21780 | 22207 | 23376
6576 | 6576 | 274 | 10 | 1 | Autumn | 9 | 30 | Summer | 24 | 12455 | 13472 | 14773 | 14285 | 14056 | 14939 | 15815 | 16192 | 17442 | 16839 | 17508 | 17786 | 18969 | 20870 | 20683 | 20403 | 20160 | 21218 | 21708 | 22917
6577 | 6577 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 1 | 12823 | 13715 | 14220 | 14199 | 14698 | 15361 | 16002 | 16510 | 16925 | 17193 | 17256 | 18590 | 19578 | 20294 | 20160 | 20070 | 19700 | 21694 | 22016 | 22358
6578 | 6578 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 2 | 12608 | 13529 | 13985 | 13980 | 14310 | 15202 | 15877 | 16390 | 16567 | 16916 | 17054 | 18376 | 19357 | 19960 | 19836 | 19677 | 19382 | 21415 | 21734 | 21964
6579 | 6579 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 3 | 12590 | 13440 | 13876 | 13915 | 14148 | 15219 | 15869 | 16352 | 16539 | 16758 | 17014 | 18355 | 19288 | 19789 | 19705 | 19432 | 19244 | 21259 | 21553 | 21722
6580 | 6580 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 4 | 12705 | 13456 | 13841 | 13860 | 14080 | 15239 | 15845 | 16257 | 16493 | 16465 | 16816 | 18122 | 18920 | 19284 | 19165 | 18858 | 18821 | 20698 | 20912 | 21044
6581 | 6581 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 5 | 13296 | 13894 | 14217 | 13996 | 14141 | 15751 | 16237 | 16505 | 16658 | 16374 | 17089 | 18305 | 18880 | 19054 | 18671 | 18433 | 18826 | 20428 | 20598 | 20614
6582 | 6582 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 6 | 14640 | 14980 | 15225 | 14434 | 14508 | 17074 | 17447 | 17403 | 17337 | 16584 | 18068 | 19238 | 19642 | 19330 | 18377 | 18292 | 19496 | 20965 | 20865 | 20699
6583 | 6583 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 7 | 15972 | 16049 | 16396 | 14814 | 14999 | 18317 | 18601 | 18314 | 18182 | 16819 | 19198 | 20067 | 20512 | 19874 | 18181 | 18324 | 20423 | 21645 | 21208 | 21126
6584 | 6584 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 8 | 16341 | 16509 | 16830 | 15171 | 15332 | 18536 | 18879 | 18715 | 18550 | 17021 | 19485 | 20114 | 20577 | 20095 | 18312 | 18385 | 20634 | 21606 | 21299 | 21282
6585 | 6585 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 9 | 16497 | 16750 | 17021 | 15719 | 15885 | 18657 | 18985 | 18851 | 18714 | 17522 | 19742 | 20175 | 20560 | 20126 | 18756 | 18787 | 20807 | 21511 | 21318 | 21265
6586 | 6586 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 10 | 16797 | 16945 | 17252 | 16154 | 16451 | 18971 | 19287 | 19110 | 19025 | 18144 | 20284 | 20571 | 20756 | 20492 | 19157 | 19276 | 21354 | 21738 | 21474 | 21670
6587 | 6587 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 11 | 16736 | 17003 | 17287 | 16184 | 16688 | 18929 | 19267 | 19256 | 19159 | 18433 | 20456 | 20612 | 20460 | 20603 | 18965 | 19257 | 21490 | 21474 | 21319 | 21837
6588 | 6588 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 12 | 16600 | 16944 | 17177 | 16128 | 16951 | 18777 | 19130 | 19216 | 19082 | 18700 | 20429 | 20474 | 20201 | 20376 | 18800 | 19391 | 21430 | 21241 | 21255 | 21637
6589 | 6589 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 13 | 16455 | 16985 | 17139 | 15897 | 16964 | 18631 | 19012 | 19279 | 19002 | 18756 | 20546 | 20325 | 19977 | 20324 | 18479 | 19347 | 21517 | 21031 | 21227 | 21579
6590 | 6590 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 14 | 16283 | 16962 | 16922 | 15645 | 16967 | 18449 | 18889 | 19216 | 18719 | 18744 | 20408 | 20096 | 19872 | 20065 | 18212 | 19365 | 21382 | 20910 | 21318 | 21305
6591 | 6591 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 15 | 16261 | 17171 | 16927 | 15591 | 17061 | 18325 | 18815 | 19306 | 18610 | 18708 | 20141 | 19880 | 20012 | 19983 | 18273 | 19582 | 21193 | 21023 | 21365 | 21197
6592 | 6592 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 16 | 16462 | 17383 | 16987 | 15620 | 17197 | 18543 | 18658 | 19262 | 18442 | 18663 | 19989 | 20087 | 20011 | 19802 | 18315 | 19772 | 21097 | 20974 | 21275 | 20958
6593 | 6593 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 17 | 16582 | 17652 | 17250 | 15821 | 17412 | 18694 | 18641 | 19428 | 18591 | 18785 | 20055 | 20213 | 20170 | 20013 | 18666 | 20105 | 21292 | 21143 | 21535 | 21175
6594 | 6594 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 18 | 16412 | 17584 | 17039 | 15844 | 17441 | 18224 | 18280 | 19397 | 18642 | 18686 | 19912 | 19802 | 19823 | 20100 | 18914 | 20157 | 21502 | 20884 | 22005 | 21323
6595 | 6595 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 19 | 16843 | 17963 | 17405 | 16339 | 17876 | 18748 | 18844 | 19852 | 19193 | 19343 | 20619 | 20605 | 20742 | 20911 | 19940 | 21108 | 22382 | 22007 | 23083 | 22297
6596 | 6596 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 20 | 16946 | 17850 | 17335 | 16293 | 17828 | 18988 | 19165 | 20015 | 19308 | 19493 | 20750 | 21156 | 21541 | 21524 | 20495 | 21625 | 22806 | 23038 | 23933 | 23104
6597 | 6597 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 21 | 16227 | 17152 | 16779 | 15901 | 17446 | 18419 | 18652 | 19582 | 19068 | 19372 | 20529 | 21027 | 21559 | 21778 | 20908 | 21913 | 22909 | 23353 | 24276 | 23583
6598 | 6598 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 22 | 15119 | 16180 | 15927 | 15370 | 16607 | 17491 | 17821 | 18814 | 18409 | 18781 | 19607 | 20396 | 21068 | 21467 | 20909 | 21558 | 22141 | 23045 | 23985 | 23407
6599 | 6599 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 23 | 13981 | 15215 | 15104 | 14797 | 15635 | 16526 | 16835 | 17993 | 17602 | 18014 | 18615 | 19604 | 20287 | 20957 | 20637 | 20920 | 21172 | 22348 | 23505 | 22975
6600 | 6600 | 275 | 10 | 2 | Autumn | 10 | 1 | Autumn | 24 | 13227 | 14506 | 14338 | 14235 | 14980 | 15783 | 16175 | 17451 | 17086 | 17444 | 17904 | 19006 | 19739 | 20469 | 20289 | 20386 | 20462 | 21848 | 23051 | 22544
6601 | 6601 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 1 | 12939 | 13540 | 13818 | 14503 | 14214 | 15452 | 15979 | 16498 | 16565 | 16498 | 17923 | 18927 | 19637 | 19620 | 19668 | 19326 | 20928 | 21803 | 22148 | 21604
6602 | 6602 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 2 | 12757 | 13280 | 13572 | 14162 | 13965 | 15289 | 15824 | 16231 | 16369 | 16268 | 17591 | 18717 | 19404 | 19293 | 19268 | 19009 | 20512 | 21502 | 21745 | 21222
6603 | 6603 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 3 | 12696 | 13188 | 13515 | 13972 | 13912 | 15301 | 15816 | 16189 | 16361 | 16272 | 17540 | 18681 | 19314 | 19200 | 19046 | 18891 | 20352 | 21334 | 21519 | 21059
6604 | 6604 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 4 | 12745 | 13139 | 13444 | 13785 | 13911 | 15278 | 15732 | 16019 | 16169 | 16112 | 17339 | 18359 | 18881 | 18693 | 18491 | 18480 | 19894 | 20698 | 20837 | 20397
6605 | 6605 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 5 | 13266 | 13560 | 13624 | 13882 | 14471 | 15748 | 16073 | 16272 | 16095 | 16490 | 17477 | 18417 | 18851 | 18280 | 18130 | 18541 | 19699 | 20431 | 20444 | 19787
6606 | 6606 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 6 | 14501 | 14559 | 14060 | 14251 | 15647 | 16975 | 17007 | 17011 | 16283 | 17427 | 18377 | 19244 | 19355 | 18025 | 18010 | 19223 | 20298 | 20690 | 20515 | 19340
6607 | 6607 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 7 | 15839 | 15778 | 14494 | 14793 | 16971 | 18197 | 18002 | 17956 | 16495 | 18630 | 19441 | 20181 | 19887 | 17882 | 18084 | 20176 | 21112 | 21067 | 20954 | 19064
6608 | 6608 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 8 | 16309 | 16259 | 14930 | 15184 | 17467 | 18536 | 18472 | 18406 | 16833 | 19066 | 19648 | 20341 | 20128 | 18083 | 18209 | 20449 | 21157 | 21215 | 21160 | 19197
6609 | 6609 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 9 | 16232 | 16201 | 15247 | 15498 | 17573 | 18393 | 18371 | 18343 | 17080 | 19103 | 19698 | 20086 | 19936 | 18276 | 18362 | 20365 | 21029 | 20970 | 20882 | 19347
6610 | 6610 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 10 | 16226 | 16077 | 15308 | 15656 | 17687 | 18262 | 18183 | 18185 | 17308 | 19116 | 19821 | 19983 | 19759 | 18384 | 18560 | 20620 | 21184 | 20839 | 21010 | 19505
6611 | 6611 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 11 | 16161 | 15953 | 15148 | 15653 | 17785 | 17948 | 18004 | 17968 | 17397 | 18917 | 19720 | 19653 | 19521 | 18172 | 18521 | 20730 | 21175 | 20655 | 21160 | 19339
6612 | 6612 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 12 | 16067 | 15812 | 15050 | 15861 | 17861 | 17735 | 17870 | 17781 | 17390 | 18854 | 19648 | 19421 | 19462 | 18039 | 18690 | 20705 | 21328 | 20622 | 20993 | 19218
6613 | 6613 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 13 | 16051 | 15853 | 14883 | 15972 | 18082 | 17661 | 17969 | 17782 | 17282 | 18987 | 19703 | 19334 | 19552 | 17832 | 18759 | 20921 | 21450 | 20718 | 21046 | 19017
6614 | 6614 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 14 | 15943 | 15705 | 14684 | 16054 | 18052 | 17609 | 17983 | 17606 | 17005 | 18994 | 19688 | 19260 | 19676 | 17590 | 18799 | 20816 | 21530 | 20825 | 20788 | 18754
6615 | 6615 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 15 | 15923 | 15809 | 14789 | 16301 | 17976 | 17755 | 18316 | 17727 | 16815 | 19098 | 19796 | 19388 | 19736 | 17648 | 19014 | 20609 | 21320 | 20865 | 20673 | 18795
6616 | 6616 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 16 | 16086 | 16129 | 15108 | 16741 | 18222 | 17965 | 18664 | 17958 | 16771 | 19472 | 20448 | 19508 | 19827 | 17812 | 19322 | 20621 | 21686 | 20891 | 20548 | 18924
6617 | 6617 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 17 | 16515 | 16711 | 15640 | 17330 | 18621 | 18312 | 19194 | 18525 | 17263 | 19924 | 20853 | 19930 | 20348 | 18428 | 19928 | 21069 | 22083 | 21424 | 21030 | 19551
6618 | 6618 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 18 | 16291 | 16454 | 15607 | 17223 | 18492 | 17965 | 19132 | 18369 | 17143 | 19797 | 20473 | 19509 | 20692 | 18612 | 19919 | 21221 | 22002 | 21846 | 21146 | 19792
6619 | 6619 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 19 | 16624 | 16841 | 16086 | 17651 | 18949 | 18514 | 19561 | 18881 | 17787 | 20323 | 21217 | 20375 | 21558 | 19602 | 20843 | 22099 | 22958 | 22927 | 22115 | 20931
6620 | 6620 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 20 | 16714 | 16757 | 16016 | 17577 | 18732 | 18799 | 19679 | 18927 | 17954 | 20375 | 21282 | 21095 | 22152 | 20101 | 21323 | 22498 | 23469 | 23773 | 22920 | 21619
6621 | 6621 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 21 | 15975 | 16154 | 15596 | 17180 | 18175 | 18244 | 19190 | 18616 | 17850 | 20058 | 21113 | 21038 | 22214 | 20458 | 21580 | 22575 | 23720 | 24106 | 23403 | 22184
6622 | 6622 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 22 | 14974 | 15271 | 15034 | 16351 | 16978 | 17364 | 18370 | 17950 | 17538 | 19057 | 20298 | 20487 | 21742 | 20418 | 21190 | 21782 | 23140 | 23809 | 23226 | 22281
6623 | 6623 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 23 | 13911 | 14427 | 14426 | 15456 | 15772 | 16340 | 17502 | 17233 | 17096 | 17955 | 19334 | 19664 | 21156 | 20113 | 20529 | 20797 | 22416 | 23309 | 22781 | 22046
6624 | 6624 | 276 | 10 | 3 | Autumn | 10 | 2 | Autumn | 24 | 13165 | 13667 | 13844 | 14745 | 14908 | 15651 | 16928 | 16615 | 16638 | 17225 | 18669 | 19094 | 20629 | 19752 | 19988 | 20077 | 21712 | 22837 | 22344 | 21738
6625 | 6625 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 1 | 12961 | 13100 | 14074 | 13815 | 14606 | 15354 | 15877 | 15897 | 16496 | 17234 | 18027 | 18900 | 19610 | 19118 | 18854 | 20425 | 21184 | 21827 | 21317 | 20841
6626 | 6626 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 2 | 12761 | 12836 | 13719 | 13529 | 14311 | 15181 | 15595 | 15668 | 16195 | 16911 | 17799 | 18675 | 19280 | 18724 | 18537 | 20007 | 20851 | 21425 | 20926 | 20407
6627 | 6627 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 3 | 12708 | 12762 | 13533 | 13501 | 14267 | 15188 | 15579 | 15708 | 16083 | 16917 | 17745 | 18631 | 19155 | 18536 | 18450 | 19883 | 20658 | 21225 | 20792 | 20167
6628 | 6628 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 4 | 12721 | 12697 | 13359 | 13508 | 14300 | 15143 | 15459 | 15555 | 15811 | 16787 | 17523 | 18270 | 18699 | 18027 | 18083 | 19465 | 20142 | 20569 | 20143 | 19540
6629 | 6629 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 5 | 13186 | 12877 | 13449 | 14078 | 14707 | 15508 | 15753 | 15541 | 15794 | 16981 | 17684 | 18299 | 18542 | 17702 | 18168 | 19291 | 19952 | 20185 | 19533 | 19059
6630 | 6630 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 6 | 14265 | 13305 | 13822 | 15250 | 15980 | 16467 | 16547 | 15775 | 16033 | 17936 | 18575 | 18870 | 18879 | 17610 | 18877 | 19908 | 20469 | 20268 | 19090 | 18816
6631 | 6631 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 7 | 15392 | 13752 | 14386 | 16609 | 17442 | 17488 | 17542 | 16074 | 16362 | 19063 | 19618 | 19481 | 19502 | 17711 | 19846 | 20740 | 21187 | 20709 | 18812 | 18817
6632 | 6632 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 8 | 15851 | 14163 | 14751 | 17031 | 17758 | 17905 | 17962 | 16370 | 16582 | 19256 | 19772 | 19685 | 19755 | 17793 | 20074 | 20747 | 21232 | 20866 | 18894 | 18862
6633 | 6633 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 9 | 16089 | 14746 | 15338 | 17395 | 18089 | 18071 | 18166 | 16908 | 17103 | 19591 | 19742 | 19768 | 19776 | 18209 | 20250 | 20877 | 21117 | 20838 | 19299 | 19238
6634 | 6634 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 10 | 16356 | 15228 | 15930 | 17808 | 18622 | 18285 | 18415 | 17366 | 17688 | 20102 | 19899 | 20012 | 20287 | 18835 | 20935 | 21466 | 21365 | 21395 | 19882 | 19906
6635 | 6635 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 11 | 16318 | 15152 | 16009 | 17731 | 18626 | 18145 | 18231 | 17143 | 17679 | 20003 | 19661 | 19849 | 20449 | 18877 | 21128 | 21538 | 21245 | 21627 | 19801 | 19987
6636 | 6636 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 12 | 15967 | 14824 | 15998 | 17499 | 18333 | 17800 | 17839 | 16800 | 17577 | 19733 | 19307 | 19518 | 19990 | 18783 | 20839 | 21428 | 20846 | 21190 | 19420 | 19900
6637 | 6637 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 13 | 16629 | 15215 | 16657 | 18205 | 18964 | 18446 | 18384 | 17144 | 18207 | 20326 | 19638 | 20150 | 20591 | 19406 | 21600 | 22096 | 21191 | 21789 | 19755 | 20510
6638 | 6638 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 14 | 16612 | 15038 | 16772 | 18273 | 18934 | 18532 | 18296 | 17033 | 18240 | 20431 | 19660 | 20250 | 20320 | 19409 | 21460 | 22146 | 21033 | 21494 | 19451 | 20494
6639 | 6639 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 15 | 16849 | 14956 | 16830 | 18176 | 18981 | 18622 | 18153 | 16838 | 18403 | 20234 | 19548 | 20245 | 20158 | 19546 | 21175 | 21865 | 21125 | 21297 | 19403 | 20619
6640 | 6640 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 16 | 17021 | 14936 | 16920 | 18259 | 19275 | 18600 | 18003 | 16684 | 18488 | 20456 | 19582 | 20064 | 19813 | 19568 | 20902 | 21945 | 21223 | 20883 | 19247 | 20619
6641 | 6641 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 17 | 17158 | 15041 | 17087 | 18322 | 19242 | 18735 | 18174 | 16884 | 18525 | 20470 | 19747 | 20134 | 19834 | 19714 | 20891 | 21893 | 21341 | 20917 | 19423 | 20782
6642 | 6642 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 18 | 16856 | 14941 | 16903 | 18182 | 18708 | 18683 | 18019 | 16788 | 18235 | 20103 | 19489 | 20264 | 19689 | 19534 | 20883 | 21651 | 21094 | 20879 | 19519 | 20659
6643 | 6643 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 19 | 17216 | 15371 | 17298 | 18626 | 19190 | 19082 | 18479 | 17386 | 18840 | 20762 | 20331 | 21072 | 20431 | 20397 | 21716 | 22555 | 22255 | 21817 | 20631 | 21630
6644 | 6644 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 20 | 17101 | 15301 | 17200 | 18390 | 18986 | 19169 | 18476 | 17492 | 18936 | 20743 | 20640 | 21591 | 20989 | 20845 | 22080 | 23033 | 22877 | 22627 | 21316 | 22219
6645 | 6645 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 21 | 16388 | 14850 | 16758 | 17784 | 18401 | 18626 | 18079 | 17288 | 18752 | 20467 | 20565 | 21553 | 21158 | 21035 | 22099 | 23241 | 23262 | 23078 | 21869 | 22575
6646 | 6646 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 22 | 15373 | 14231 | 15884 | 16547 | 17271 | 17740 | 17346 | 16898 | 18093 | 19575 | 19981 | 21001 | 20783 | 20598 | 21265 | 22619 | 22956 | 22880 | 21946 | 22249
6647 | 6647 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 23 | 14404 | 13690 | 15048 | 15417 | 16160 | 16948 | 16707 | 16531 | 17312 | 18715 | 19224 | 20408 | 20263 | 19947 | 20289 | 21902 | 22224 | 22456 | 21739 | 21652
6648 | 6648 | 277 | 10 | 4 | Autumn | 10 | 3 | Autumn | 24 | 13692 | 13071 | 14281 | 14509 | 15342 | 16287 | 15990 | 15980 | 16738 | 17967 | 18648 | 19868 | 19772 | 19404 | 19568 | 21203 | 21822 | 22015 | 21434 | 21153
6649 | 6649 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 1 | 12585 | 13257 | 13305 | 14101 | 14511 | 15148 | 15220 | 15841 | 15658 | 17227 | 17716 | 18776 | 18807 | 18221 | 19808 | 20601 | 20957 | 20926 | 20481 | 19925
6650 | 6650 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 2 | 12353 | 12950 | 13068 | 13829 | 14321 | 14913 | 15039 | 15573 | 15444 | 17077 | 17503 | 18498 | 18509 | 17961 | 19451 | 20313 | 20598 | 20582 | 20094 | 19624
6651 | 6651 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 3 | 12279 | 12689 | 12966 | 13729 | 14244 | 14829 | 15014 | 15414 | 15457 | 16990 | 17447 | 18361 | 18427 | 17840 | 19291 | 20086 | 20452 | 20396 | 19807 | 19449
6652 | 6652 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 4 | 12290 | 12552 | 13026 | 13825 | 14305 | 14787 | 14950 | 15235 | 15390 | 16889 | 17195 | 18007 | 18023 | 17545 | 18946 | 19640 | 19866 | 19798 | 19219 | 19023
6653 | 6653 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 5 | 12689 | 12607 | 13564 | 14220 | 14804 | 15075 | 14943 | 15229 | 15788 | 17076 | 17493 | 17903 | 17643 | 17642 | 18782 | 19467 | 19785 | 19177 | 18711 | 18964
6654 | 6654 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 6 | 13690 | 13036 | 14790 | 15539 | 16048 | 15948 | 15286 | 15558 | 16768 | 18086 | 18467 | 18333 | 17440 | 18411 | 19463 | 20030 | 20315 | 18777 | 18499 | 19592
6655 | 6655 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 7 | 14908 | 13592 | 16154 | 16989 | 17310 | 16947 | 15618 | 15901 | 17984 | 19159 | 19511 | 18994 | 17323 | 19388 | 20311 | 20741 | 21134 | 18490 | 18471 | 20487
6656 | 6656 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 8 | 15363 | 14008 | 16628 | 17360 | 17643 | 17421 | 15982 | 16189 | 18410 | 19397 | 19550 | 19306 | 17516 | 19661 | 20371 | 20830 | 21017 | 18610 | 18548 | 20726
6657 | 6657 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 9 | 15413 | 14527 | 16888 | 17579 | 17558 | 17505 | 16405 | 16615 | 18583 | 19266 | 19222 | 19241 | 17836 | 19743 | 20397 | 20623 | 20603 | 18904 | 18821 | 20774
6658 | 6658 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 10 | 15468 | 14956 | 17148 | 17957 | 17460 | 17648 | 16770 | 17096 | 18742 | 19365 | 19175 | 19469 | 18122 | 20145 | 20710 | 20594 | 20467 | 19205 | 19211 | 21214
6659 | 6659 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 11 | 15445 | 15228 | 17307 | 18190 | 17330 | 17767 | 16878 | 17394 | 18600 | 19502 | 19085 | 19657 | 18027 | 20348 | 20798 | 20507 | 20065 | 19138 | 19310 | 21455
6660 | 6660 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 12 | 15387 | 15483 | 17364 | 18220 | 17306 | 17634 | 16789 | 17605 | 18663 | 19378 | 18811 | 19514 | 17946 | 20381 | 21007 | 20427 | 19716 | 19076 | 19546 | 21500
6661 | 6661 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 13 | 15472 | 15670 | 17601 | 18383 | 17164 | 17727 | 16686 | 17782 | 18836 | 19268 | 18722 | 19609 | 17790 | 20631 | 21170 | 20264 | 19559 | 18905 | 19651 | 21747
6662 | 6662 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 14 | 15315 | 15664 | 17526 | 18300 | 17116 | 17460 | 16383 | 17755 | 18912 | 19078 | 18487 | 19305 | 17473 | 20461 | 21188 | 20062 | 19292 | 18564 | 19598 | 21559
6663 | 6663 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 15 | 15249 | 15792 | 17514 | 18270 | 17114 | 17413 | 16284 | 17797 | 18741 | 19060 | 18372 | 19178 | 17471 | 20217 | 20942 | 20185 | 19297 | 18559 | 19756 | 21300
6664 | 6664 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 16 | 15493 | 16157 | 17863 | 18700 | 17545 | 17527 | 16382 | 18003 | 18974 | 19329 | 18499 | 19120 | 17619 | 20223 | 21296 | 20555 | 19509 | 18664 | 20016 | 21274
6665 | 6665 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 17 | 15876 | 16471 | 18067 | 18849 | 17856 | 17806 | 16669 | 18184 | 19269 | 19549 | 18615 | 19367 | 18006 | 20446 | 21469 | 20897 | 19884 | 19067 | 20400 | 21516
6666 | 6666 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 18 | 15614 | 16268 | 17862 | 18439 | 17761 | 17579 | 16456 | 17950 | 19253 | 19120 | 18719 | 19272 | 18100 | 20497 | 21299 | 20742 | 20309 | 19253 | 20365 | 21615
6667 | 6667 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 19 | 15997 | 16666 | 18289 | 18907 | 18353 | 18015 | 17018 | 18516 | 19732 | 19889 | 19662 | 19962 | 19030 | 21302 | 22175 | 21874 | 21588 | 20365 | 21367 | 22531
6668 | 6668 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 20 | 15885 | 16528 | 18021 | 18655 | 18271 | 17964 | 17062 | 18541 | 19710 | 20096 | 20135 | 20431 | 19459 | 21601 | 22599 | 22455 | 22445 | 21032 | 21937 | 22973
6669 | 6669 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 21 | 15203 | 16007 | 17360 | 17987 | 17724 | 17485 | 16763 | 18250 | 19283 | 19883 | 20055 | 20469 | 19695 | 21546 | 22714 | 22749 | 22810 | 21539 | 22261 | 23076
6670 | 6670 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 22 | 14319 | 15144 | 16129 | 16862 | 16854 | 16744 | 16354 | 17573 | 18253 | 19278 | 19341 | 20064 | 19622 | 20723 | 22100 | 22454 | 22370 | 21640 | 21967 | 22367
6671 | 6671 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 23 | 13536 | 14238 | 14913 | 15733 | 15852 | 15988 | 15862 | 16756 | 17244 | 18383 | 18541 | 19502 | 19315 | 19723 | 21354 | 21699 | 21721 | 21415 | 21358 | 21413
6672 | 6672 | 278 | 10 | 5 | Autumn | 10 | 4 | Autumn | 24 | 12766 | 13497 | 14051 | 14906 | 15168 | 15324 | 15366 | 16158 | 16426 | 17901 | 17986 | 18991 | 18951 | 19004 | 20654 | 21288 | 21202 | 21105 | 20858 | 20731
6673 | 6673 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 1 | 12452 | 12898 | 13959 | 14383 | 14522 | 14912 | 15629 | 15407 | 16621 | 17291 | 17880 | 18388 | 18663 | 19525 | 20371 | 20723 | 21121 | 20509 | 19974 | 21435
6674 | 6674 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 2 | 12213 | 12607 | 13651 | 14171 | 14296 | 14685 | 15315 | 15179 | 16329 | 17064 | 17564 | 18098 | 18303 | 19147 | 20062 | 20378 | 20702 | 20097 | 19641 | 20992
6675 | 6675 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 3 | 12095 | 12509 | 13552 | 14063 | 14277 | 14667 | 15165 | 15167 | 16298 | 17054 | 17421 | 18035 | 18099 | 19023 | 19869 | 20237 | 20430 | 19830 | 19487 | 20813
6676 | 6676 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 4 | 12025 | 12554 | 13604 | 14099 | 14248 | 14574 | 14957 | 15098 | 16234 | 16814 | 17174 | 17655 | 17625 | 18682 | 19424 | 19645 | 19885 | 19208 | 19029 | 20324
6677 | 6677 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 5 | 12208 | 13138 | 14055 | 14652 | 14887 | 14659 | 15047 | 15578 | 16486 | 17251 | 17284 | 17375 | 17357 | 18610 | 19337 | 19635 | 19655 | 18758 | 19014 | 20067
6678 | 6678 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 6 | 12638 | 14367 | 15336 | 15921 | 16178 | 14998 | 15387 | 16624 | 17520 | 18266 | 18018 | 17252 | 17312 | 19309 | 19916 | 20208 | 20071 | 18532 | 19624 | 20592
6679 | 6679 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 7 | 13104 | 15813 | 16866 | 17256 | 17637 | 15418 | 15836 | 17946 | 18709 | 19447 | 19075 | 17248 | 17473 | 20244 | 20716 | 21100 | 20768 | 18563 | 20558 | 21383
6680 | 6680 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 8 | 13596 | 16323 | 17273 | 17618 | 17883 | 15793 | 16145 | 18418 | 19005 | 19520 | 19333 | 17488 | 17627 | 20340 | 20830 | 21013 | 20869 | 18652 | 20811 | 21397
6681 | 6681 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 9 | 14193 | 16691 | 17615 | 17655 | 17761 | 16314 | 16687 | 18726 | 19357 | 19313 | 19374 | 17948 | 18076 | 20477 | 20734 | 20726 | 20853 | 19012 | 20948 | 21481
6682 | 6682 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 10 | 14624 | 17010 | 18049 | 17714 | 17755 | 16677 | 17152 | 19048 | 19938 | 19217 | 19608 | 18347 | 18549 | 20929 | 20848 | 20706 | 21315 | 19545 | 21534 | 21974
6683 | 6683 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 11 | 14810 | 17133 | 18231 | 17728 | 17662 | 16653 | 17297 | 19065 | 20298 | 18912 | 19573 | 18309 | 18683 | 21094 | 20840 | 20364 | 21637 | 19724 | 21857 | 22184
6684 | 6684 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 12 | 14726 | 17186 | 18257 | 17648 | 17379 | 16558 | 17503 | 19048 | 20235 | 18623 | 19473 | 18198 | 18877 | 21270 | 20727 | 19978 | 21550 | 19928 | 21871 | 22373
6685 | 6685 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 13 | 14549 | 17290 | 18309 | 17435 | 17197 | 16332 | 17553 | 19146 | 20299 | 18393 | 19458 | 17952 | 18902 | 21350 | 20480 | 19737 | 21584 | 19950 | 22030 | 22446
6686 | 6686 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 14 | 14324 | 17288 | 18303 | 17349 | 17062 | 16117 | 17613 | 19142 | 20259 | 18254 | 19326 | 17710 | 18938 | 21437 | 20346 | 19541 | 21391 | 19962 | 21906 | 22509
6687 | 6687 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 15 | 14294 | 17359 | 18355 | 17494 | 17011 | 16137 | 17789 | 19185 | 20142 | 18299 | 19321 | 17710 | 19095 | 21178 | 20454 | 19548 | 21176 | 20103 | 21626 | 22227
6688 | 6688 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 16 | 14403 | 17654 | 18700 | 17896 | 17186 | 16266 | 18030 | 19431 | 20463 | 18494 | 19290 | 17748 | 19264 | 21413 | 20703 | 19642 | 20864 | 20233 | 21476 | 22432
6689 | 6689 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 17 | 14557 | 17795 | 18804 | 18058 | 17314 | 16530 | 18188 | 19550 | 20429 | 18595 | 19341 | 18026 | 19527 | 21468 | 20933 | 19905 | 20754 | 20506 | 21597 | 22506
6690 | 6690 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 18 | 14389 | 17548 | 18397 | 17815 | 17300 | 16313 | 17919 | 19278 | 19881 | 18626 | 19443 | 18019 | 19360 | 21234 | 20710 | 20274 | 21018 | 20422 | 21662 | 22325
6691 | 6691 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 19 | 14799 | 17971 | 18853 | 18380 | 17899 | 16861 | 18467 | 19715 | 20485 | 19512 | 20086 | 18891 | 20203 | 22068 | 21803 | 21507 | 22044 | 21424 | 22578 | 23327
6692 | 6692 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 20 | 14688 | 17651 | 18557 | 18239 | 17986 | 16858 | 18441 | 19625 | 20359 | 19874 | 20292 | 19225 | 20551 | 22423 | 22313 | 22319 | 22644 | 21970 | 22999 | 23861
6693 | 6693 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 21 | 14213 | 16990 | 17894 | 17680 | 17511 | 16541 | 18138 | 19168 | 19994 | 19721 | 20224 | 19399 | 20681 | 22505 | 22597 | 22672 | 23030 | 22324 | 23135 | 24143
6694 | 6694 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 22 | 13580 | 15736 | 16719 | 16752 | 16475 | 16071 | 17394 | 18062 | 19054 | 18927 | 19584 | 19250 | 20213 | 21822 | 22230 | 22185 | 22653 | 21991 | 22373 | 23598
6695 | 6695 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 23 | 12975 | 14477 | 15552 | 15651 | 15484 | 15534 | 16531 | 16909 | 18041 | 18075 | 18761 | 18894 | 19521 | 21042 | 21440 | 21504 | 21960 | 21369 | 21411 | 22895
6696 | 6696 | 279 | 10 | 6 | Autumn | 10 | 5 | Autumn | 24 | 12421 | 13596 | 14697 | 15009 | 14760 | 15000 | 15893 | 16146 | 17372 | 17500 | 18210 | 18517 | 18977 | 20338 | 21019 | 20981 | 21499 | 20863 | 20729 | 22239
6697 | 6697 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 1 | 12896 | 13434 | 14112 | 14284 | 14538 | 15259 | 15085 | 16199 | 16866 | 17327 | 17800 | 18240 | 18069 | 19945 | 20375 | 20827 | 20939 | 19880 | 21338 | 21920
6698 | 6698 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 2 | 12577 | 13148 | 13907 | 14052 | 14254 | 14946 | 14860 | 15907 | 16701 | 17046 | 17507 | 17897 | 17804 | 19662 | 20039 | 20427 | 20579 | 19558 | 20929 | 21592
6699 | 6699 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 3 | 12313 | 13012 | 13789 | 14026 | 14116 | 14786 | 14846 | 15880 | 16622 | 16938 | 17382 | 17721 | 17696 | 19497 | 19921 | 20174 | 20282 | 19414 | 20753 | 21361
6700 | 6700 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 4 | 12142 | 13080 | 13844 | 14017 | 14165 | 14606 | 14818 | 15855 | 16536 | 16775 | 17060 | 17311 | 17424 | 19108 | 19383 | 19676 | 19688 | 18979 | 20280 | 20812
6701 | 6701 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 5 | 12228 | 13524 | 14388 | 14675 | 14604 | 14708 | 15323 | 16164 | 16833 | 16950 | 16802 | 17091 | 17596 | 19059 | 19404 | 19470 | 19073 | 18970 | 20018 | 20566
6702 | 6702 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 6 | 12660 | 14826 | 15683 | 16019 | 15766 | 15103 | 16450 | 17274 | 17904 | 17800 | 16753 | 17143 | 18424 | 19717 | 20052 | 19956 | 18681 | 19620 | 20577 | 21028
6703 | 6703 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 7 | 13236 | 16342 | 16980 | 17493 | 17055 | 15545 | 17789 | 18517 | 19053 | 18896 | 16882 | 17332 | 19445 | 20519 | 20943 | 20651 | 18551 | 20519 | 21347 | 21666
6704 | 6704 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 8 | 13712 | 16810 | 17396 | 17778 | 17474 | 15906 | 18319 | 18887 | 19360 | 19234 | 17168 | 17551 | 19787 | 20713 | 20919 | 20790 | 18706 | 20821 | 21407 | 21760
6705 | 6705 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 9 | 14475 | 17298 | 17563 | 17754 | 17757 | 16572 | 18759 | 19374 | 19471 | 19416 | 17709 | 18111 | 20097 | 20759 | 20767 | 20867 | 19086 | 21094 | 21622 | 21735
6706 | 6706 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 10 | 14935 | 17695 | 17601 | 17610 | 17921 | 16997 | 19037 | 19758 | 19491 | 19596 | 18011 | 18554 | 20594 | 20828 | 20699 | 21307 | 19624 | 21633 | 22068 | 21841
6707 | 6707 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 11 | 15099 | 17834 | 17577 | 17280 | 17828 | 17082 | 18991 | 19791 | 19362 | 19477 | 17946 | 18610 | 20801 | 20740 | 20274 | 21547 | 19989 | 21877 | 22198 | 21792
6708 | 6708 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 12 | 15355 | 17913 | 17550 | 17064 | 17776 | 17340 | 19021 | 19800 | 19269 | 19412 | 17909 | 18844 | 20834 | 20662 | 19934 | 21495 | 20115 | 21926 | 22428 | 21726
6709 | 6709 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 13 | 15471 | 18009 | 17374 | 16887 | 17821 | 17427 | 19159 | 19853 | 19064 | 19428 | 17841 | 18909 | 21040 | 20451 | 19721 | 21576 | 20148 | 22117 | 22533 | 21504
6710 | 6710 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 14 | 15453 | 17896 | 17202 | 16680 | 17633 | 17401 | 19068 | 19748 | 18882 | 19215 | 17706 | 18861 | 20844 | 20236 | 19439 | 21297 | 19913 | 21900 | 22510 | 21268
6711 | 6711 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 15 | 15724 | 18052 | 17428 | 16821 | 17741 | 17657 | 19192 | 19876 | 19098 | 19297 | 17688 | 19103 | 20672 | 20425 | 19531 | 21166 | 19574 | 21706 | 22315 | 21443
6712 | 6712 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 16 | 16142 | 18448 | 17929 | 17220 | 17923 | 18007 | 19543 | 20426 | 19516 | 19378 | 17756 | 19374 | 20646 | 20776 | 19726 | 20957 | 19249 | 21640 | 22611 | 21764
6713 | 6713 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 17 | 16309 | 18459 | 18008 | 17330 | 17904 | 18082 | 19571 | 20400 | 19642 | 19334 | 17974 | 19545 | 20678 | 20910 | 19896 | 20758 | 19385 | 21677 | 22591 | 21929
6714 | 6714 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 18 | 15970 | 17966 | 17699 | 17227 | 17852 | 17732 | 19189 | 19784 | 19106 | 19281 | 18103 | 19229 | 20586 | 20560 | 20143 | 20891 | 19693 | 21637 | 22301 | 21655
6715 | 6715 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 19 | 16351 | 18380 | 18228 | 17788 | 18290 | 18244 | 19577 | 20332 | 19816 | 19832 | 18713 | 19998 | 21330 | 21595 | 21326 | 21879 | 20525 | 22527 | 23271 | 22860
6716 | 6716 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 20 | 16162 | 18062 | 18054 | 17841 | 18035 | 18185 | 19447 | 20141 | 19909 | 19937 | 18805 | 20280 | 21554 | 22042 | 22084 | 22437 | 21078 | 22941 | 23796 | 23513
6717 | 6717 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 21 | 15643 | 17356 | 17459 | 17331 | 17522 | 17847 | 18945 | 19703 | 19631 | 19764 | 18842 | 20345 | 21467 | 22242 | 22385 | 22783 | 21547 | 23074 | 24075 | 23947
6718 | 6718 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 22 | 14728 | 16158 | 16493 | 16260 | 16564 | 17054 | 17788 | 18701 | 18941 | 19046 | 18597 | 19818 | 20563 | 21821 | 21838 | 22365 | 21566 | 22291 | 23513 | 23679
6719 | 6719 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 23 | 13818 | 15012 | 15392 | 15274 | 15575 | 16195 | 16638 | 17671 | 18013 | 18219 | 18228 | 19124 | 19553 | 21034 | 21156 | 21680 | 21324 | 21352 | 22830 | 22968
6720 | 6720 | 280 | 10 | 7 | Autumn | 10 | 6 | Autumn | 24 | 13055 | 14138 | 14719 | 14516 | 14836 | 15519 | 15830 | 16946 | 17481 | 17645 | 17886 | 18547 | 18811 | 20596 | 20618 | 21195 | 21041 | 20648 | 22163 | 22577
6721 | 6721 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 1 | 12032 | 13171 | 13651 | 13912 | 14102 | 13682 | 15436 | 16026 | 16406 | 16886 | 16366 | 16659 | 18810 | 19562 | 20079 | 20267 | 19066 | 20852 | 21458 | 21601
6722 | 6722 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 2 | 11757 | 12958 | 13414 | 13608 | 13853 | 13452 | 15129 | 15845 | 16200 | 16606 | 16110 | 16401 | 18458 | 19242 | 19697 | 19909 | 18713 | 20440 | 21123 | 21226
6723 | 6723 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 3 | 11682 | 12836 | 13386 | 13499 | 13748 | 13437 | 15114 | 15811 | 16217 | 16530 | 16031 | 16375 | 18369 | 19156 | 19463 | 19657 | 18517 | 20276 | 20903 | 21058
6724 | 6724 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 4 | 11744 | 12890 | 13380 | 13548 | 13662 | 13424 | 15113 | 15755 | 16040 | 16262 | 15764 | 16140 | 18078 | 18655 | 18996 | 19077 | 18012 | 19804 | 20351 | 20389
6725 | 6725 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 5 | 12291 | 13408 | 14032 | 13988 | 13696 | 13561 | 15447 | 16088 | 16512 | 16055 | 15523 | 16044 | 18028 | 18710 | 18816 | 18473 | 17488 | 19539 | 20093 | 20244
6726 | 6726 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 6 | 13571 | 14712 | 15420 | 15187 | 14073 | 13964 | 16626 | 17225 | 17649 | 16097 | 15574 | 16179 | 18830 | 19423 | 19362 | 18122 | 17209 | 20130 | 20577 | 20761
6727 | 6727 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 7 | 14997 | 16022 | 16946 | 16513 | 14574 | 14294 | 17938 | 18431 | 18864 | 16303 | 15716 | 16184 | 19778 | 20354 | 20104 | 18026 | 17070 | 20918 | 21232 | 21571
6728 | 6728 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 8 | 15535 | 16406 | 17221 | 16919 | 14942 | 14596 | 18322 | 18751 | 18984 | 16604 | 15821 | 16315 | 19924 | 20324 | 20232 | 18174 | 17111 | 20965 | 21307 | 21478
6729 | 6729 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 9 | 15995 | 16554 | 17165 | 17169 | 15472 | 15439 | 18781 | 18849 | 18877 | 17134 | 16336 | 17071 | 20173 | 20138 | 20280 | 18529 | 17591 | 21141 | 21242 | 21253
6730 | 6730 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 10 | 16268 | 16600 | 17040 | 17341 | 15769 | 16131 | 19163 | 18877 | 18738 | 17429 | 16721 | 17773 | 20577 | 20059 | 20712 | 19062 | 18025 | 21581 | 21347 | 21213
6731 | 6731 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 11 | 16425 | 16664 | 16792 | 17311 | 15847 | 16296 | 19221 | 18775 | 18467 | 17349 | 16767 | 17862 | 20760 | 19729 | 21048 | 19521 | 18230 | 21809 | 21401 | 20943
6732 | 6732 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 12 | 16514 | 16599 | 16506 | 17185 | 15832 | 16307 | 19114 | 18565 | 18219 | 17157 | 16737 | 17805 | 20972 | 19367 | 20974 | 19640 | 18361 | 22019 | 21321 | 20592
6733 | 6733 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 13 | 16683 | 16450 | 16366 | 17260 | 15829 | 16262 | 19202 | 18384 | 18067 | 17115 | 16729 | 17738 | 21129 | 19197 | 21093 | 19711 | 18377 | 22168 | 21146 | 20439
6734 | 6734 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 14 | 16765 | 16445 | 16324 | 17236 | 15892 | 16162 | 19260 | 18362 | 18020 | 17141 | 16770 | 17607 | 21306 | 19095 | 20993 | 19654 | 18411 | 22313 | 21087 | 20315
6735 | 6735 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 15 | 16826 | 16570 | 16364 | 17240 | 15803 | 16333 | 19285 | 18477 | 18044 | 17030 | 16915 | 17760 | 21028 | 19089 | 20763 | 19219 | 18530 | 22018 | 21159 | 20285
6736 | 6736 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 16 | 17039 | 16893 | 16597 | 17264 | 15804 | 16574 | 19636 | 18741 | 18171 | 16943 | 17034 | 17924 | 21177 | 19128 | 20393 | 18732 | 18586 | 22141 | 21302 | 20270
6737 | 6737 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 17 | 16988 | 16893 | 16620 | 17166 | 15927 | 16665 | 19555 | 18808 | 18072 | 17112 | 17264 | 17971 | 21034 | 19191 | 20076 | 18749 | 18756 | 22006 | 21351 | 20340
6738 | 6738 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 18 | 16692 | 16804 | 16679 | 17300 | 15985 | 16751 | 19219 | 18532 | 18054 | 17479 | 17471 | 18221 | 20739 | 19501 | 20298 | 19114 | 18980 | 21813 | 21163 | 20719
6739 | 6739 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 19 | 17089 | 17328 | 17238 | 17725 | 16341 | 17309 | 19756 | 19205 | 18864 | 18036 | 18156 | 19110 | 21514 | 20655 | 21250 | 19917 | 19901 | 22793 | 22371 | 22019
6740 | 6740 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 20 | 16760 | 17122 | 17263 | 17450 | 16171 | 17329 | 19516 | 19246 | 19157 | 18036 | 18338 | 19450 | 21808 | 21357 | 21761 | 20434 | 20334 | 23306 | 23019 | 22914
6741 | 6741 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 21 | 16059 | 16461 | 16694 | 16878 | 15772 | 16967 | 18994 | 18866 | 18901 | 17952 | 18404 | 19468 | 21787 | 21570 | 22024 | 20848 | 20755 | 23555 | 23418 | 23340
6742 | 6742 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 22 | 14796 | 15503 | 15602 | 15896 | 15232 | 16139 | 17950 | 18122 | 18047 | 17655 | 18053 | 18883 | 21072 | 20996 | 21588 | 20845 | 20618 | 22993 | 23156 | 22902
6743 | 6743 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 23 | 13569 | 14413 | 14610 | 14922 | 14713 | 15347 | 16916 | 17179 | 17202 | 17284 | 17555 | 18211 | 20315 | 20316 | 20904 | 20612 | 20218 | 22324 | 22458 | 22318
6744 | 6744 | 281 | 10 | 8 | Autumn | 10 | 7 | Autumn | 24 | 12710 | 13742 | 13847 | 14193 | 14220 | 14853 | 16181 | 16638 | 16616 | 16956 | 17208 | 17823 | 19617 | 19789 | 20434 | 20349 | 19943 | 21662 | 22095 | 21837
6745 | 6745 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 1 | 12616 | 13142 | 13696 | 13912 | 13646 | 15076 | 15677 | 15985 | 16490 | 15987 | 16226 | 18368 | 19262 | 19688 | 19962 | 18870 | 18915 | 21392 | 21552 | 21754
6746 | 6746 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 2 | 12364 | 12923 | 13419 | 13668 | 13418 | 14786 | 15516 | 15794 | 16231 | 15777 | 16010 | 18052 | 19013 | 19338 | 19636 | 18544 | 18607 | 21077 | 21202 | 21345
6747 | 6747 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 3 | 12236 | 12873 | 13281 | 13533 | 13316 | 14737 | 15454 | 15801 | 16154 | 15699 | 15983 | 17970 | 18876 | 19110 | 19387 | 18343 | 18504 | 20846 | 21029 | 21036
6748 | 6748 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 4 | 12296 | 12913 | 13361 | 13477 | 13243 | 14779 | 15456 | 15697 | 16045 | 15510 | 15822 | 17740 | 18530 | 18699 | 18852 | 17868 | 18093 | 20313 | 20372 | 20451
6749 | 6749 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 5 | 12727 | 13548 | 13829 | 13533 | 13307 | 15151 | 15842 | 16229 | 16282 | 15328 | 15783 | 17767 | 18533 | 18589 | 18310 | 17392 | 17799 | 20091 | 20250 | 20137
6750 | 6750 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 6 | 14016 | 14938 | 15055 | 13934 | 13636 | 16371 | 17040 | 17451 | 17207 | 15446 | 15981 | 18622 | 19250 | 19176 | 17990 | 17122 | 17701 | 20580 | 20761 | 20527
6751 | 6751 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 7 | 15563 | 16496 | 16422 | 14466 | 13996 | 17725 | 18293 | 18733 | 18386 | 15636 | 16027 | 19646 | 20124 | 19964 | 17939 | 17010 | 17561 | 21266 | 21583 | 21197
6752 | 6752 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 8 | 16015 | 16781 | 16849 | 14855 | 14215 | 18136 | 18646 | 18900 | 18725 | 15783 | 16195 | 19840 | 20321 | 20116 | 18103 | 17064 | 17631 | 21349 | 21488 | 21279
6753 | 6753 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 9 | 16147 | 16397 | 16785 | 15066 | 14482 | 18268 | 18431 | 18478 | 18560 | 15997 | 16639 | 19795 | 20034 | 19857 | 18149 | 17231 | 18008 | 20985 | 20939 | 20975
6754 | 6754 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 10 | 16428 | 16162 | 16851 | 15248 | 14739 | 18517 | 18321 | 18208 | 18621 | 16238 | 17195 | 20072 | 19977 | 20166 | 18561 | 17545 | 18634 | 20968 | 20786 | 21323
6755 | 6755 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 11 | 16535 | 15918 | 16839 | 15276 | 14770 | 18604 | 18253 | 17890 | 18408 | 16323 | 17322 | 20153 | 19879 | 20400 | 18922 | 17654 | 18655 | 20924 | 20428 | 21616
6756 | 6756 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 12 | 16433 | 15716 | 16804 | 15277 | 14709 | 18667 | 18234 | 17713 | 18091 | 16527 | 17500 | 20246 | 19681 | 20221 | 18940 | 17668 | 18501 | 20742 | 19979 | 21465
6757 | 6757 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 13 | 16507 | 15550 | 16880 | 15269 | 14671 | 18777 | 18082 | 17576 | 18076 | 16557 | 17465 | 20353 | 19444 | 20285 | 18955 | 17620 | 18360 | 20517 | 19762 | 21545
6758 | 6758 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 14 | 16460 | 15482 | 16837 | 15312 | 14635 | 18855 | 18091 | 17556 | 17932 | 16659 | 17397 | 20440 | 19311 | 20094 | 18805 | 17559 | 18107 | 20363 | 19544 | 21331
6759 | 6759 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 15 | 16535 | 15400 | 16703 | 15067 | 14794 | 18676 | 17982 | 17340 | 17920 | 16530 | 17278 | 20172 | 19407 | 19872 | 18377 | 17684 | 18239 | 20439 | 19514 | 21084
6760 | 6760 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 16 | 16931 | 15678 | 16782 | 15111 | 15181 | 19007 | 18224 | 17434 | 18041 | 16567 | 17363 | 20497 | 19789 | 19703 | 18088 | 17938 | 18539 | 20772 | 19687 | 20857
6761 | 6761 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 17 | 17253 | 16074 | 17025 | 15620 | 15707 | 19262 | 18615 | 17711 | 18338 | 17096 | 17714 | 20747 | 20189 | 19787 | 18505 | 18516 | 18994 | 21211 | 20157 | 20950
6762 | 6762 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 18 | 17126 | 16273 | 17282 | 15984 | 16072 | 19113 | 18503 | 18020 | 18734 | 17411 | 18085 | 20636 | 20091 | 20172 | 19036 | 18938 | 19552 | 21205 | 20725 | 21403
6763 | 6763 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 19 | 17582 | 16846 | 17695 | 16342 | 16589 | 19635 | 19144 | 18800 | 19283 | 18042 | 18929 | 21381 | 21124 | 21101 | 19821 | 19866 | 20672 | 22412 | 22036 | 22486
6764 | 6764 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 20 | 17252 | 16846 | 17393 | 16133 | 16498 | 19362 | 19133 | 19016 | 19313 | 18151 | 19206 | 21594 | 21507 | 21558 | 20300 | 20258 | 21251 | 23050 | 22930 | 23135
6765 | 6765 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 21 | 16507 | 16283 | 16800 | 15700 | 16246 | 18809 | 18716 | 18682 | 19037 | 18149 | 19167 | 21509 | 21626 | 21761 | 20663 | 20656 | 21551 | 23453 | 23358 | 23564
6766 | 6766 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 22 | 15320 | 15206 | 15809 | 15147 | 15668 | 17742 | 17929 | 17788 | 18280 | 17775 | 18558 | 20751 | 21181 | 21301 | 20645 | 20519 | 21131 | 23192 | 22943 | 23240
6767 | 6767 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 23 | 14152 | 14169 | 14818 | 14634 | 14967 | 16705 | 16992 | 16951 | 17401 | 17309 | 17920 | 19923 | 20354 | 20553 | 20360 | 20061 | 20486 | 22448 | 22295 | 22565
6768 | 6768 | 282 | 10 | 9 | Autumn | 10 | 8 | Autumn | 24 | 13302 | 13371 | 14026 | 14075 | 14494 | 15879 | 16348 | 16250 | 16820 | 16874 | 17441 | 19203 | 19924 | 20069 | 20092 | 19780 | 20134 | 22078 | 21829 | 22145
6769 | 6769 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 1 | 12705 | 13104 | 13616 | 13438 | 13381 | 15228 | 15551 | 15991 | 16425 | 15777 | 17673 | 18722 | 19210 | 19516 | 18563 | 18645 | 20630 | 21415 | 21643 | 21525
6770 | 6770 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 2 | 12513 | 12826 | 13368 | 13197 | 13167 | 15055 | 15353 | 15735 | 16180 | 15579 | 17418 | 18485 | 18931 | 19200 | 18241 | 18339 | 20300 | 21058 | 21231 | 21152
6771 | 6771 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 3 | 12353 | 12666 | 13191 | 13029 | 13096 | 14955 | 15331 | 15609 | 16070 | 15547 | 17381 | 18336 | 18831 | 18949 | 18030 | 18211 | 20125 | 20875 | 20911 | 20833
6772 | 6772 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 4 | 12420 | 12741 | 13140 | 12974 | 13101 | 14974 | 15256 | 15561 | 15879 | 15425 | 17230 | 18060 | 18389 | 18467 | 17594 | 17835 | 19704 | 20239 | 20341 | 20187
6773 | 6773 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 5 | 12958 | 13253 | 13231 | 13071 | 13269 | 15429 | 15875 | 15883 | 15753 | 15476 | 17486 | 18151 | 18538 | 17995 | 17172 | 17588 | 19664 | 20154 | 20054 | 19518
6774 | 6774 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 6 | 14252 | 14498 | 13641 | 13422 | 13684 | 16656 | 17152 | 16894 | 15876 | 15715 | 18465 | 18941 | 19306 | 17727 | 16935 | 17516 | 20395 | 20681 | 20450 | 19050
6775 | 6775 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 7 | 15558 | 15884 | 14220 | 13811 | 14011 | 17977 | 18513 | 18147 | 16132 | 15837 | 19545 | 19875 | 20291 | 17721 | 16857 | 17390 | 21134 | 21510 | 21124 | 18911
6776 | 6776 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 8 | 15940 | 16318 | 14634 | 14038 | 14309 | 18338 | 18697 | 18521 | 16472 | 16024 | 19517 | 20106 | 20284 | 17905 | 16921 | 17466 | 20892 | 21419 | 21211 | 19038
6777 | 6777 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 9 | 15730 | 16227 | 14811 | 14259 | 14760 | 18077 | 18241 | 18319 | 16638 | 16443 | 19152 | 19785 | 19735 | 17906 | 17046 | 17788 | 20397 | 20818 | 20851 | 19016
6778 | 6778 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 10 | 15334 | 15994 | 14713 | 14208 | 15012 | 17668 | 17674 | 18066 | 16482 | 16703 | 18774 | 19406 | 19222 | 17996 | 17037 | 18099 | 20258 | 20348 | 20883 | 19146
6779 | 6779 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 11 | 15207 | 15817 | 14590 | 14175 | 15045 | 17422 | 17167 | 17811 | 16291 | 16630 | 18294 | 19141 | 18630 | 18179 | 16970 | 17963 | 20204 | 19804 | 21003 | 19381
6780 | 6780 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 12 | 15304 | 15782 | 14597 | 14340 | 15314 | 17356 | 16925 | 17751 | 16442 | 16712 | 18121 | 19057 | 18273 | 18305 | 17099 | 17923 | 20204 | 19473 | 20964 | 19523
6781 | 6781 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 13 | 15290 | 15984 | 14707 | 14485 | 15443 | 17308 | 16886 | 17923 | 16592 | 16763 | 18104 | 18992 | 18209 | 18477 | 17208 | 17949 | 20274 | 19411 | 21185 | 19692
6782 | 6782 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 14 | 15361 | 16002 | 14787 | 14573 | 15466 | 17324 | 16866 | 17913 | 16787 | 16682 | 17981 | 18980 | 18132 | 18449 | 17264 | 17814 | 20052 | 19311 | 21089 | 19642
6783 | 6783 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 15 | 15394 | 15984 | 14711 | 14734 | 15465 | 17445 | 16899 | 17905 | 16423 | 16845 | 17947 | 19084 | 18138 | 18029 | 17398 | 17947 | 19716 | 19286 | 20846 | 19198
6784 | 6784 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 16 | 15875 | 16316 | 15016 | 15211 | 15808 | 18028 | 17360 | 18141 | 16360 | 17320 | 18536 | 19575 | 18461 | 17845 | 17749 | 18356 | 19979 | 19554 | 20713 | 18963
6785 | 6785 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 17 | 16325 | 16646 | 15609 | 15779 | 16316 | 18518 | 17729 | 18455 | 16912 | 17757 | 18951 | 20061 | 18990 | 18334 | 18399 | 18893 | 20234 | 20095 | 20877 | 19455
6786 | 6786 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 18 | 16395 | 16780 | 15826 | 15995 | 16556 | 18281 | 17854 | 18614 | 17383 | 17894 | 18925 | 19914 | 19440 | 18822 | 18786 | 19423 | 20303 | 20643 | 21306 | 20005
6787 | 6787 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 19 | 16883 | 17161 | 16135 | 16442 | 17088 | 18876 | 18572 | 19057 | 17856 | 18660 | 19589 | 20835 | 20517 | 19538 | 19651 | 20472 | 21337 | 21921 | 22353 | 20867
6788 | 6788 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 20 | 16676 | 16851 | 15917 | 16346 | 17134 | 18843 | 18759 | 19039 | 17806 | 18890 | 19887 | 21156 | 21184 | 19978 | 20018 | 21047 | 22006 | 22816 | 23017 | 21485
6789 | 6789 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 21 | 15973 | 16192 | 15403 | 16023 | 16730 | 18323 | 18315 | 18634 | 17611 | 18715 | 19815 | 21139 | 21293 | 20240 | 20335 | 21264 | 22361 | 23190 | 23401 | 21962
6790 | 6790 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 22 | 15001 | 15167 | 14808 | 15411 | 15879 | 17476 | 17362 | 17810 | 17257 | 18054 | 19126 | 20630 | 20671 | 20168 | 20155 | 20818 | 21919 | 22754 | 23057 | 22034
6791 | 6791 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 23 | 13926 | 14142 | 14234 | 14717 | 15114 | 16450 | 16422 | 16905 | 16923 | 17312 | 18264 | 19791 | 19952 | 19875 | 19706 | 20184 | 21177 | 22115 | 22409 | 21810
6792 | 6792 | 283 | 10 | 10 | Autumn | 10 | 9 | Autumn | 24 | 13219 | 13350 | 13698 | 14231 | 14534 | 15828 | 15744 | 16271 | 16485 | 16899 | 17715 | 19323 | 19403 | 19587 | 19407 | 19804 | 20695 | 21624 | 21979 | 21577
6793 | 6793 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 1 | 12428 | 12830 | 12967 | 12945 | 14385 | 14873 | 15330 | 15734 | 15334 | 16945 | 17714 | 18446 | 19037 | 17973 | 18117 | 20120 | 20808 | 21281 | 21199 | 19700
6794 | 6794 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 2 | 12214 | 12567 | 12729 | 12720 | 14126 | 14670 | 15073 | 15488 | 15129 | 16711 | 17424 | 18187 | 18703 | 17674 | 17831 | 19811 | 20448 | 20882 | 20838 | 19357
6795 | 6795 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 3 | 12173 | 12411 | 12574 | 12657 | 14113 | 14674 | 14984 | 15408 | 15054 | 16741 | 17370 | 18137 | 18506 | 17506 | 17743 | 19674 | 20247 | 20596 | 20549 | 19134
6796 | 6796 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 4 | 12243 | 12377 | 12537 | 12681 | 14210 | 14642 | 14992 | 15271 | 14909 | 16666 | 17164 | 17782 | 18170 | 17121 | 17410 | 19308 | 19760 | 20055 | 19925 | 18618
6797 | 6797 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 5 | 12888 | 12455 | 12624 | 12856 | 14756 | 15283 | 15350 | 15206 | 14802 | 16974 | 17320 | 17991 | 18131 | 16726 | 17182 | 19289 | 19565 | 19771 | 19251 | 18063
6798 | 6798 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 6 | 14271 | 12856 | 12979 | 13262 | 16054 | 16593 | 16419 | 15377 | 14950 | 18011 | 18275 | 18832 | 18777 | 16519 | 17133 | 20037 | 20201 | 20174 | 18781 | 17705
6799 | 6799 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 7 | 15873 | 13501 | 13399 | 13636 | 17424 | 17991 | 17732 | 15735 | 15216 | 19162 | 19507 | 19910 | 19623 | 16476 | 17035 | 20803 | 21163 | 20857 | 18648 | 17565
6800 | 6800 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 8 | 16149 | 13930 | 13652 | 13941 | 17580 | 18193 | 18142 | 16101 | 15373 | 19186 | 19672 | 19947 | 19792 | 16551 | 17129 | 20585 | 21164 | 20948 | 18773 | 17601
6801 | 6801 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 9 | 15668 | 14064 | 13841 | 14354 | 17311 | 17698 | 17900 | 16250 | 15519 | 18805 | 19461 | 19370 | 19440 | 16640 | 17412 | 20051 | 20764 | 20540 | 18699 | 17653
6802 | 6802 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 10 | 15030 | 13860 | 13689 | 14520 | 16812 | 17014 | 17535 | 16006 | 15356 | 18304 | 19105 | 18725 | 19332 | 16507 | 17600 | 19791 | 20663 | 20456 | 18711 | 17558
6803 | 6803 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 11 | 14670 | 13801 | 13704 | 14564 | 16417 | 16501 | 17269 | 15769 | 15311 | 17773 | 18779 | 18187 | 19453 | 16499 | 17527 | 19800 | 20858 | 20637 | 19009 | 17591
6804 | 6804 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 12 | 14464 | 13730 | 13785 | 14607 | 16229 | 16138 | 17070 | 15583 | 15387 | 17429 | 18553 | 17782 | 19340 | 16594 | 17454 | 19767 | 20927 | 20558 | 19117 | 17693
6805 | 6805 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 13 | 14300 | 13712 | 13813 | 14572 | 16123 | 15974 | 17117 | 15540 | 15392 | 17281 | 18544 | 17602 | 19447 | 16589 | 17368 | 19722 | 21024 | 20663 | 19170 | 17681
6806 | 6806 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 14 | 14245 | 13720 | 13836 | 14446 | 15976 | 15890 | 17046 | 15544 | 15430 | 17094 | 18565 | 17482 | 19335 | 16597 | 17186 | 19455 | 20975 | 20518 | 19069 | 17675
6807 | 6807 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 15 | 14368 | 13729 | 14075 | 14703 | 16034 | 16008 | 17119 | 15523 | 15667 | 17144 | 18734 | 17571 | 19200 | 16813 | 17402 | 19195 | 20837 | 20353 | 18706 | 17879
6808 | 6808 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 16 | 14935 | 14125 | 14644 | 15327 | 16633 | 16556 | 17441 | 15830 | 16171 | 17796 | 19120 | 18001 | 19225 | 17252 | 17882 | 19551 | 20857 | 20304 | 18554 | 18297
6809 | 6809 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 17 | 15475 | 14818 | 15311 | 15950 | 17121 | 17048 | 17875 | 16524 | 16851 | 18337 | 19742 | 18586 | 19431 | 17962 | 18470 | 19871 | 21336 | 20526 | 19107 | 19018
6810 | 6810 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 18 | 15646 | 15203 | 15682 | 16281 | 17267 | 17416 | 18266 | 17069 | 17056 | 18547 | 19743 | 19071 | 19856 | 18418 | 19074 | 20013 | 21266 | 21040 | 19740 | 19511
6811 | 6811 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 19 | 16188 | 15516 | 16120 | 16813 | 17778 | 18122 | 18684 | 17515 | 17624 | 19163 | 20458 | 20103 | 20708 | 19257 | 20110 | 21031 | 22206 | 22091 | 20610 | 20467
6812 | 6812 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 20 | 16154 | 15243 | 15980 | 16814 | 17621 | 18250 | 18596 | 17376 | 17662 | 19354 | 20648 | 20664 | 21094 | 19563 | 20628 | 21639 | 22863 | 22730 | 21202 | 20920
6813 | 6813 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 21 | 15550 | 14723 | 15645 | 16391 | 17155 | 17783 | 18138 | 17109 | 17555 | 19205 | 20519 | 20694 | 21180 | 19845 | 20820 | 21950 | 23175 | 23114 | 21692 | 21369
6814 | 6814 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 22 | 14457 | 14106 | 15011 | 15529 | 16187 | 16789 | 17268 | 16706 | 17137 | 18466 | 19751 | 20024 | 20671 | 19632 | 20346 | 21497 | 22692 | 22766 | 21758 | 21263
6815 | 6815 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 23 | 13385 | 13523 | 14313 | 14703 | 15157 | 15842 | 16347 | 16252 | 16576 | 17596 | 18826 | 19280 | 19935 | 19181 | 19712 | 20748 | 21884 | 22121 | 21546 | 20864
6816 | 6816 | 284 | 10 | 11 | Autumn | 10 | 10 | Autumn | 24 | 12590 | 12965 | 13794 | 14144 | 14445 | 15125 | 15666 | 15848 | 16193 | 17030 | 18203 | 18694 | 19407 | 18865 | 19317 | 20233 | 21342 | 21670 | 21301 | 20591
6817 | 6817 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 1 | 12165 | 12276 | 12503 | 13987 | 14290 | 14693 | 15133 | 14784 | 14943 | 17003 | 17766 | 18305 | 18710 | 17568 | 19588 | 20320 | 21019 | 20884 | 19436 | 19296
6818 | 6818 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 2 | 11913 | 12038 | 12286 | 13728 | 14037 | 14443 | 14897 | 14588 | 14752 | 16750 | 17505 | 17999 | 18424 | 17296 | 19295 | 19978 | 20644 | 20526 | 19095 | 18995
6819 | 6819 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 3 | 11794 | 11851 | 12182 | 13685 | 13977 | 14320 | 14786 | 14490 | 14750 | 16697 | 17435 | 17815 | 18209 | 17207 | 19161 | 19766 | 20424 | 20228 | 18862 | 18856
6820 | 6820 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 4 | 11890 | 11801 | 12203 | 13794 | 14022 | 14356 | 14687 | 14387 | 14681 | 16560 | 17217 | 17529 | 17791 | 16894 | 18816 | 19297 | 19912 | 19604 | 18336 | 18419
6821 | 6821 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 5 | 12399 | 11894 | 12363 | 14336 | 14490 | 14732 | 14650 | 14300 | 14758 | 16763 | 17353 | 17552 | 17357 | 16698 | 18828 | 19126 | 19700 | 18940 | 17779 | 18069
6822 | 6822 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 6 | 13692 | 12306 | 12840 | 15717 | 15874 | 15903 | 14951 | 14575 | 15078 | 17861 | 18275 | 18330 | 17180 | 16736 | 19666 | 19843 | 20198 | 18538 | 17474 | 17964
6823 | 6823 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 7 | 15071 | 12704 | 13210 | 17090 | 17430 | 17208 | 15332 | 14868 | 15226 | 19114 | 19362 | 19224 | 17206 | 16642 | 20444 | 20832 | 20956 | 18390 | 17309 | 17783
6824 | 6824 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 8 | 15532 | 13001 | 13551 | 17303 | 17715 | 17647 | 15748 | 15082 | 15457 | 19343 | 19479 | 19454 | 17427 | 16761 | 20258 | 20885 | 20970 | 18528 | 17354 | 17863
6825 | 6825 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 9 | 15431 | 13220 | 14017 | 17062 | 17562 | 17436 | 15934 | 15273 | 15885 | 19183 | 19260 | 19155 | 17426 | 17095 | 19769 | 20532 | 20717 | 18488 | 17444 | 18160
6826 | 6826 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 10 | 15243 | 13323 | 14454 | 16816 | 17344 | 17361 | 15996 | 15426 | 16188 | 19156 | 19226 | 19170 | 17551 | 17431 | 19664 | 20566 | 20742 | 18653 | 17505 | 18529
6827 | 6827 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 11 | 15075 | 13523 | 14717 | 16593 | 17076 | 17379 | 16073 | 15635 | 16071 | 19193 | 19204 | 19263 | 17772 | 17329 | 19641 | 20743 | 20861 | 18923 | 17514 | 18461
6828 | 6828 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 12 | 14878 | 13606 | 14765 | 16337 | 16859 | 17202 | 15916 | 15634 | 15934 | 18996 | 19013 | 19076 | 17794 | 17179 | 19531 | 20744 | 20873 | 18952 | 17539 | 18315
6829 | 6829 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 13 | 14939 | 13674 | 14753 | 16248 | 16860 | 17288 | 15918 | 15671 | 15838 | 19040 | 19073 | 19163 | 17830 | 17074 | 19468 | 20821 | 20966 | 18986 | 17510 | 18215
6830 | 6830 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 14 | 15025 | 13791 | 14744 | 16203 | 17025 | 17338 | 16041 | 15804 | 15808 | 19180 | 19175 | 19173 | 17873 | 17017 | 19328 | 20890 | 20984 | 19008 | 17625 | 18138
6831 | 6831 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 15 | 15150 | 14015 | 15000 | 16231 | 17274 | 17366 | 15961 | 15966 | 16128 | 19260 | 19217 | 19121 | 17611 | 17318 | 19147 | 20830 | 20868 | 18725 | 17907 | 18423
6832 | 6832 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 16 | 15449 | 14410 | 15440 | 16588 | 17637 | 17470 | 16032 | 16210 | 16578 | 19372 | 19301 | 19054 | 17415 | 17706 | 19403 | 20746 | 20730 | 18471 | 18218 | 18785
6833 | 6833 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 17 | 15795 | 14942 | 15888 | 16952 | 18182 | 17703 | 16506 | 16729 | 17073 | 19746 | 19608 | 19183 | 17893 | 18226 | 19641 | 21149 | 21054 | 18946 | 18859 | 19305
6834 | 6834 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 18 | 15958 | 15086 | 15951 | 17006 | 17991 | 17828 | 16741 | 16775 | 17356 | 19383 | 19706 | 19442 | 18326 | 18700 | 19668 | 20949 | 21415 | 19471 | 19257 | 19836
6835 | 6835 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 19 | 16345 | 15501 | 16455 | 17496 | 18439 | 18213 | 17142 | 17297 | 18089 | 20014 | 20425 | 20235 | 19001 | 19694 | 20644 | 21859 | 22458 | 20334 | 20210 | 20945
6836 | 6836 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 20 | 15969 | 15300 | 16407 | 17289 | 18309 | 18066 | 16928 | 17264 | 18213 | 20092 | 20688 | 20525 | 19331 | 20142 | 21186 | 22459 | 23038 | 20909 | 20638 | 21526
6837 | 6837 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 21 | 15340 | 14980 | 15996 | 16820 | 17783 | 17593 | 16633 | 17136 | 18027 | 19896 | 20697 | 20558 | 19571 | 20320 | 21484 | 22767 | 23499 | 21416 | 21112 | 21860
6838 | 6838 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 22 | 14290 | 14315 | 15104 | 15806 | 16683 | 16676 | 16171 | 16646 | 17304 | 19064 | 20030 | 19975 | 19442 | 19811 | 20987 | 22239 | 23101 | 21460 | 20999 | 21447
6839 | 6839 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 23 | 13294 | 13619 | 14275 | 14781 | 15578 | 15745 | 15705 | 16074 | 16568 | 18124 | 19147 | 19221 | 19153 | 19185 | 20232 | 21432 | 22336 | 21258 | 20619 | 20871
6840 | 6840 | 285 | 10 | 12 | Autumn | 10 | 11 | Autumn | 24 | 12501 | 13100 | 13715 | 14070 | 14782 | 15052 | 15287 | 15678 | 16137 | 17516 | 18509 | 18683 | 18853 | 18795 | 19720 | 20881 | 21784 | 21011 | 20354 | 20529
6841 | 6841 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 1 | 12316 | 12180 | 13931 | 14265 | 14606 | 14890 | 14653 | 14783 | 16493 | 17417 | 17679 | 18383 | 17690 | 19389 | 20164 | 20914 | 20993 | 19537 | 19428 | 21261
6842 | 6842 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 2 | 12045 | 11929 | 13645 | 13985 | 14338 | 14627 | 14429 | 14579 | 16260 | 17159 | 17361 | 18087 | 17383 | 19069 | 19811 | 20515 | 20550 | 19167 | 19084 | 20906
6843 | 6843 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 3 | 11876 | 11808 | 13575 | 13889 | 14282 | 14492 | 14307 | 14539 | 16270 | 17099 | 17236 | 17899 | 17217 | 18955 | 19617 | 20316 | 20306 | 18939 | 18949 | 20734
6844 | 6844 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 4 | 11838 | 11824 | 13689 | 13949 | 14316 | 14418 | 14231 | 14510 | 16255 | 16948 | 17029 | 17530 | 16861 | 18655 | 19188 | 19826 | 19791 | 18425 | 18519 | 20280
6845 | 6845 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 5 | 11924 | 12016 | 14270 | 14454 | 14852 | 14447 | 14214 | 14645 | 16629 | 17192 | 17229 | 17192 | 16535 | 18746 | 19089 | 19676 | 19586 | 17912 | 18204 | 20183
6846 | 6846 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 6 | 12340 | 12457 | 15615 | 15851 | 16116 | 14753 | 14508 | 15021 | 17763 | 18166 | 18170 | 17077 | 16390 | 19595 | 19815 | 20187 | 20148 | 17587 | 18068 | 20850
6847 | 6847 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 7 | 13000 | 12854 | 17048 | 17448 | 17487 | 15192 | 14880 | 15243 | 18963 | 19349 | 19261 | 17196 | 16387 | 20445 | 20861 | 20993 | 21007 | 17453 | 17911 | 21555
6848 | 6848 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 8 | 13455 | 13192 | 17267 | 17724 | 17728 | 15592 | 15087 | 15485 | 19039 | 19473 | 19422 | 17424 | 16484 | 20258 | 20912 | 21000 | 21031 | 17476 | 17963 | 21269
6849 | 6849 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 9 | 13578 | 13629 | 17000 | 17521 | 17556 | 15726 | 15241 | 15875 | 18650 | 19225 | 19020 | 17397 | 16577 | 19740 | 20531 | 20713 | 20540 | 17521 | 18223 | 20701
6850 | 6850 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 10 | 13477 | 13951 | 16625 | 17286 | 17319 | 15648 | 15251 | 16213 | 18342 | 19048 | 18817 | 17382 | 16456 | 19496 | 20428 | 20601 | 20221 | 17446 | 18465 | 20497
6851 | 6851 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 11 | 13564 | 14250 | 16435 | 17304 | 17221 | 15760 | 15498 | 16520 | 18160 | 19080 | 18747 | 17576 | 16406 | 19447 | 20582 | 20694 | 19962 | 17434 | 18378 | 20489
6852 | 6852 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 12 | 13522 | 14458 | 16340 | 17333 | 17123 | 15803 | 15709 | 16708 | 17913 | 19121 | 18625 | 17648 | 16480 | 19394 | 20646 | 20761 | 19848 | 17523 | 18298 | 20467
6853 | 6853 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 13 | 13554 | 14509 | 16326 | 17462 | 17234 | 15889 | 15833 | 16771 | 17865 | 19280 | 18684 | 17744 | 16506 | 19389 | 20780 | 20912 | 19871 | 17551 | 18242 | 20458
6854 | 6854 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 14 | 13590 | 14414 | 16172 | 17520 | 17284 | 15905 | 15854 | 16624 | 17711 | 19264 | 18586 | 17715 | 16551 | 19169 | 20768 | 20853 | 19775 | 17582 | 18081 | 20218
6855 | 6855 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 15 | 13593 | 14584 | 16128 | 17576 | 17385 | 15724 | 15905 | 16669 | 17643 | 19169 | 18441 | 17429 | 16818 | 18958 | 20677 | 20713 | 19820 | 17831 | 18332 | 19990
6856 | 6856 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 16 | 13924 | 15085 | 16484 | 17874 | 17752 | 15838 | 16175 | 16970 | 18117 | 19252 | 18461 | 17353 | 17261 | 19324 | 20701 | 20690 | 19896 | 18241 | 18793 | 20331
6857 | 6857 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 17 | 14568 | 15623 | 16960 | 18412 | 18115 | 16426 | 16799 | 17399 | 18505 | 19653 | 18722 | 17918 | 17982 | 19659 | 21201 | 21113 | 20261 | 18980 | 19426 | 20684
6858 | 6858 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 18 | 14777 | 15709 | 17083 | 18145 | 18261 | 16720 | 16871 | 17484 | 18434 | 19734 | 18927 | 18341 | 18344 | 19703 | 21018 | 21491 | 20590 | 19416 | 19978 | 20790
6859 | 6859 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 19 | 15061 | 16181 | 17554 | 18557 | 18708 | 17096 | 17363 | 18159 | 18974 | 20375 | 19615 | 18952 | 19128 | 20637 | 21881 | 22501 | 21583 | 20364 | 21082 | 21869
6860 | 6860 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 20 | 14746 | 16122 | 17314 | 18386 | 18606 | 16846 | 17288 | 18224 | 19073 | 20538 | 19940 | 19202 | 19361 | 21117 | 22428 | 23037 | 22321 | 20782 | 21659 | 22525
6861 | 6861 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 21 | 14233 | 15705 | 16818 | 17818 | 18183 | 16502 | 17116 | 17978 | 18872 | 20449 | 19962 | 19348 | 19619 | 21361 | 22683 | 23453 | 22791 | 21256 | 21999 | 22970
6862 | 6862 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 22 | 13588 | 14790 | 15772 | 16692 | 17197 | 15998 | 16583 | 17217 | 18063 | 19718 | 19328 | 19166 | 19357 | 20816 | 22111 | 23022 | 22442 | 21124 | 21575 | 22560
6863 | 6863 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 23 | 12987 | 13914 | 14689 | 15540 | 16076 | 15470 | 15948 | 16416 | 17146 | 18763 | 18423 | 18817 | 18880 | 20008 | 21254 | 22218 | 21686 | 20705 | 20960 | 21834
6864 | 6864 | 286 | 10 | 13 | Autumn | 10 | 12 | Autumn | 24 | 12437 | 13326 | 13937 | 14715 | 15271 | 14997 | 15497 | 15939 | 16566 | 18087 | 17795 | 18487 | 18552 | 19478 | 20675 | 21636 | 21126 | 20418 | 20606 | 21373
6865 | 6865 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 1 | 11790 | 13234 | 13799 | 14143 | 14036 | 14071 | 14232 | 15862 | 16498 | 16896 | 17483 | 17045 | 17261 | 19532 | 20332 | 20455 | 20630 | 19117 | 20978 | 21502
6866 | 6866 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 2 | 11537 | 12950 | 13521 | 13864 | 13745 | 13835 | 14018 | 15625 | 16237 | 16599 | 17152 | 16760 | 16974 | 19201 | 19964 | 20028 | 20202 | 18786 | 20625 | 21122
6867 | 6867 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 3 | 11357 | 12877 | 13434 | 13805 | 13657 | 13726 | 13996 | 15644 | 16187 | 16534 | 17064 | 16629 | 16914 | 19038 | 19787 | 19812 | 19973 | 18664 | 20462 | 20894
6868 | 6868 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 4 | 11297 | 12959 | 13486 | 13831 | 13702 | 13645 | 13969 | 15645 | 16100 | 16371 | 16754 | 16312 | 16638 | 18648 | 19329 | 19321 | 19375 | 18237 | 20008 | 20341
6869 | 6869 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 5 | 11410 | 13527 | 13998 | 14387 | 14174 | 13656 | 14143 | 16079 | 16385 | 16652 | 16551 | 16031 | 16501 | 18588 | 19213 | 19136 | 18872 | 17925 | 19908 | 20086
6870 | 6870 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 6 | 11793 | 14876 | 15395 | 15679 | 15456 | 13972 | 14563 | 17266 | 17530 | 17671 | 16577 | 15964 | 16563 | 19377 | 19777 | 19735 | 18598 | 17811 | 20594 | 20676
6871 | 6871 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 7 | 12236 | 16356 | 17015 | 17104 | 16938 | 14392 | 14857 | 18563 | 18888 | 18868 | 16833 | 16032 | 16552 | 20474 | 20628 | 20633 | 18526 | 17672 | 21323 | 21610
6872 | 6872 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 8 | 12564 | 16706 | 17408 | 17444 | 17330 | 14646 | 15221 | 18775 | 19159 | 19171 | 17149 | 16190 | 16699 | 20666 | 20773 | 20770 | 18636 | 17840 | 21152 | 21692
6873 | 6873 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 9 | 12861 | 16581 | 17336 | 17404 | 17143 | 14928 | 15751 | 18551 | 19088 | 18919 | 17343 | 16423 | 17122 | 20418 | 20608 | 20419 | 18723 | 18218 | 20706 | 21371
6874 | 6874 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 10 | 12946 | 16253 | 17136 | 17177 | 16983 | 14901 | 16042 | 18190 | 19038 | 18633 | 17445 | 16415 | 17432 | 20425 | 20604 | 20220 | 19050 | 18569 | 20619 | 21417
6875 | 6875 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 11 | 13201 | 15963 | 17008 | 16943 | 16857 | 14898 | 16074 | 17776 | 19162 | 18222 | 17317 | 16384 | 17342 | 20602 | 20720 | 19983 | 19243 | 18507 | 20637 | 21644
6876 | 6876 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 12 | 13469 | 15754 | 16932 | 16850 | 16753 | 15034 | 16110 | 17535 | 19240 | 17918 | 17247 | 16499 | 17301 | 20633 | 20754 | 19843 | 19209 | 18398 | 20575 | 21684
6877 | 6877 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 13 | 13672 | 15751 | 17066 | 16992 | 16847 | 15142 | 16152 | 17501 | 19431 | 17929 | 17126 | 16588 | 17310 | 20819 | 20957 | 19927 | 19092 | 18395 | 20618 | 21867
6878 | 6878 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 14 | 13734 | 15678 | 17222 | 17126 | 16859 | 15277 | 16125 | 17438 | 19518 | 17964 | 17132 | 16705 | 17234 | 20876 | 20966 | 19901 | 19018 | 18298 | 20440 | 21906
6879 | 6879 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 15 | 13866 | 15734 | 17417 | 17322 | 16827 | 15539 | 16402 | 17515 | 19451 | 18090 | 17219 | 16956 | 17491 | 20770 | 20814 | 19930 | 18848 | 18533 | 20200 | 21787
6880 | 6880 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 16 | 14276 | 16165 | 17851 | 17778 | 17017 | 16021 | 16935 | 18082 | 19521 | 18385 | 17516 | 17369 | 17936 | 20763 | 20762 | 19973 | 18907 | 18952 | 20499 | 21749
6881 | 6881 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 17 | 14685 | 16449 | 18204 | 17975 | 17169 | 16493 | 17207 | 18330 | 19758 | 18500 | 17907 | 17852 | 18313 | 21016 | 20942 | 20102 | 19241 | 19340 | 20608 | 22024
6882 | 6882 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 18 | 14688 | 16435 | 17829 | 17974 | 17154 | 16453 | 17149 | 18132 | 19270 | 18530 | 18273 | 18001 | 18640 | 20651 | 21141 | 20253 | 19803 | 19740 | 20549 | 21735
6883 | 6883 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 19 | 15076 | 16879 | 18212 | 18391 | 17476 | 16920 | 17786 | 18623 | 19831 | 19135 | 18736 | 18724 | 19582 | 21450 | 22090 | 21213 | 20664 | 20814 | 21600 | 22702
6884 | 6884 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 20 | 14833 | 16604 | 18014 | 18247 | 17410 | 16822 | 17818 | 18648 | 19812 | 19365 | 18848 | 18884 | 19962 | 21935 | 22576 | 21901 | 21149 | 21388 | 22261 | 23393
6885 | 6885 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 21 | 14496 | 16077 | 17399 | 17773 | 16976 | 16608 | 17518 | 18366 | 19518 | 19270 | 18888 | 19063 | 20080 | 22109 | 22929 | 22331 | 21620 | 21715 | 22696 | 23803
6886 | 6886 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 22 | 13811 | 15010 | 16246 | 16760 | 16031 | 16040 | 16717 | 17506 | 18633 | 18574 | 18592 | 18754 | 19533 | 21497 | 22462 | 21943 | 21588 | 21282 | 22280 | 23345
6887 | 6887 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 23 | 13064 | 13896 | 15055 | 15603 | 14938 | 15374 | 15882 | 16528 | 17604 | 17621 | 18121 | 18234 | 18845 | 20617 | 21630 | 21156 | 21233 | 20665 | 21539 | 22530
6888 | 6888 | 287 | 10 | 14 | Autumn | 10 | 13 | Autumn | 24 | 12523 | 13141 | 14209 | 14780 | 14145 | 14903 | 15383 | 15908 | 16945 | 16991 | 17757 | 17896 | 18435 | 20030 | 21042 | 20579 | 20930 | 20305 | 21069 | 22012
6889 | 6889 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 1 | 11431 | 13193 | 13843 | 13741 | 14200 | 14478 | 15450 | 16011 | 16647 | 16917 | 16644 | 17402 | 18809 | 19856 | 20042 | 20277 | 19347 | 20844 | 21379 | 21905
6890 | 6890 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 2 | 11198 | 12923 | 13567 | 13443 | 13874 | 14249 | 15214 | 15747 | 16395 | 16616 | 16380 | 17146 | 18519 | 19498 | 19630 | 19875 | 18994 | 20493 | 21010 | 21503
6891 | 6891 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 3 | 11122 | 12824 | 13496 | 13357 | 13807 | 14217 | 15230 | 15718 | 16393 | 16555 | 16316 | 17090 | 18452 | 19350 | 19440 | 19668 | 18863 | 20343 | 20794 | 21282
6892 | 6892 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 4 | 11121 | 12903 | 13553 | 13423 | 13742 | 14222 | 15291 | 15685 | 16276 | 16337 | 16085 | 16860 | 18194 | 18948 | 18999 | 19112 | 18371 | 19911 | 20258 | 20715
6893 | 6893 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 5 | 11296 | 13411 | 14109 | 13913 | 13846 | 14778 | 15755 | 16025 | 16583 | 16186 | 15830 | 17078 | 18322 | 18880 | 18860 | 18643 | 17854 | 19825 | 20007 | 20451
6894 | 6894 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 6 | 11729 | 14814 | 15444 | 15223 | 14232 | 16008 | 17017 | 17229 | 17621 | 16311 | 15873 | 17968 | 19237 | 19499 | 19516 | 18401 | 17589 | 20532 | 20608 | 20883
6895 | 6895 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 7 | 12139 | 16441 | 16907 | 16734 | 14777 | 17357 | 18368 | 18634 | 18900 | 16626 | 16111 | 19088 | 20152 | 20391 | 20446 | 18353 | 17665 | 21280 | 21562 | 21659
6896 | 6896 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 8 | 12508 | 16770 | 17176 | 17117 | 15209 | 17835 | 18531 | 18918 | 19067 | 16962 | 16356 | 19458 | 20020 | 20461 | 20514 | 18461 | 17806 | 21030 | 21559 | 21654
6897 | 6897 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 9 | 13007 | 16613 | 17064 | 16854 | 15476 | 17817 | 18230 | 18786 | 18890 | 17099 | 16597 | 19357 | 19569 | 20234 | 20083 | 18482 | 17918 | 20501 | 21165 | 21379
6898 | 6898 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 10 | 13358 | 16506 | 16937 | 16677 | 15534 | 17815 | 18001 | 18715 | 18620 | 17361 | 16783 | 19436 | 19408 | 20205 | 19858 | 18787 | 17957 | 20385 | 21193 | 21385
6899 | 6899 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 11 | 13536 | 16506 | 16854 | 16470 | 15434 | 17875 | 17794 | 18721 | 18312 | 17469 | 16899 | 19538 | 19364 | 20304 | 19605 | 18956 | 17750 | 20391 | 21390 | 21536
6900 | 6900 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 12 | 13701 | 16477 | 16820 | 16253 | 15377 | 17890 | 17610 | 18643 | 18223 | 17383 | 16924 | 19534 | 19323 | 20371 | 19503 | 18885 | 17642 | 20359 | 21471 | 21624
6901 | 6901 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 13 | 13680 | 16567 | 16929 | 16257 | 15197 | 18133 | 17566 | 18739 | 18258 | 17259 | 16937 | 19780 | 19290 | 20499 | 19511 | 18690 | 17550 | 20327 | 21579 | 21742
6902 | 6902 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 14 | 13614 | 16625 | 16969 | 16210 | 15161 | 18167 | 17383 | 18762 | 18311 | 17133 | 16917 | 19770 | 19073 | 20457 | 19440 | 18563 | 17555 | 20094 | 21562 | 21676
6903 | 6903 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 15 | 13978 | 16770 | 17097 | 16275 | 15356 | 18164 | 17305 | 18788 | 18573 | 17021 | 17036 | 19675 | 18940 | 20384 | 19547 | 18469 | 17949 | 19927 | 21515 | 21576
6904 | 6904 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 16 | 14615 | 17121 | 17449 | 16551 | 15786 | 18477 | 17641 | 18943 | 18976 | 17072 | 17294 | 19833 | 19309 | 20384 | 19633 | 18583 | 18460 | 20262 | 21513 | 21519
6905 | 6905 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 17 | 15070 | 17568 | 17737 | 16866 | 16298 | 18731 | 17983 | 19363 | 19356 | 17541 | 17952 | 20167 | 19512 | 20676 | 19874 | 19026 | 19258 | 20477 | 21898 | 21820
6906 | 6906 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 18 | 15019 | 17364 | 17842 | 17019 | 16630 | 18673 | 18001 | 19116 | 19327 | 18076 | 18463 | 20171 | 19409 | 20913 | 20057 | 19612 | 19955 | 20474 | 21663 | 22135
6907 | 6907 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 19 | 15453 | 17735 | 18234 | 17309 | 16900 | 19130 | 18454 | 19623 | 19900 | 18460 | 19039 | 20873 | 20264 | 21813 | 20976 | 20432 | 20707 | 21528 | 22614 | 23189
6908 | 6908 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 20 | 15391 | 17486 | 18050 | 17214 | 16584 | 18966 | 18422 | 19544 | 19989 | 18469 | 18995 | 21033 | 20684 | 22233 | 21608 | 20879 | 21065 | 22160 | 23288 | 23802
6909 | 6909 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 21 | 14928 | 16833 | 17521 | 16713 | 16184 | 18416 | 18062 | 19146 | 19774 | 18397 | 18933 | 20867 | 20824 | 22496 | 21953 | 21306 | 21353 | 22561 | 23662 | 24286
6910 | 6910 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 22 | 13999 | 15665 | 16466 | 15723 | 15574 | 17218 | 17141 | 18188 | 18968 | 18027 | 18464 | 19913 | 20224 | 21980 | 21530 | 21222 | 21086 | 22130 | 23196 | 23906
6911 | 6911 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 23 | 13103 | 14458 | 15293 | 14625 | 14925 | 16020 | 16142 | 17129 | 17964 | 17534 | 17913 | 18869 | 19382 | 21128 | 20726 | 20860 | 20627 | 21383 | 22380 | 23129
6912 | 6912 | 288 | 10 | 15 | Autumn | 10 | 14 | Autumn | 24 | 12536 | 13607 | 14458 | 13832 | 14410 | 15188 | 15498 | 16451 | 17280 | 17173 | 17448 | 18126 | 18850 | 20544 | 20154 | 20567 | 20205 | 20917 | 21874 | 22611
6913 | 6913 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 1 | 12553 | 13103 | 13306 | 13794 | 13597 | 14878 | 15445 | 16006 | 16143 | 16038 | 16802 | 18146 | 18942 | 19418 | 19754 | 18911 | 19491 | 21093 | 21637 | 21504
6914 | 6914 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 2 | 12267 | 12821 | 12996 | 13450 | 13337 | 14623 | 15166 | 15751 | 15852 | 15786 | 16672 | 17857 | 18615 | 19006 | 19342 | 18550 | 19253 | 20696 | 21210 | 21032
6915 | 6915 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 3 | 12197 | 12733 | 12893 | 13351 | 13252 | 14625 | 15129 | 15729 | 15798 | 15739 | 16706 | 17813 | 18480 | 18844 | 19163 | 18427 | 19201 | 20490 | 21013 | 20795
6916 | 6916 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 4 | 12299 | 12800 | 12975 | 13322 | 13206 | 14713 | 15136 | 15691 | 15731 | 15564 | 16614 | 17624 | 18160 | 18456 | 18645 | 17979 | 18889 | 19974 | 20459 | 20238
6917 | 6917 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 5 | 12854 | 13367 | 13484 | 13439 | 13195 | 15219 | 15532 | 16051 | 16064 | 15371 | 16826 | 17822 | 18159 | 18368 | 18225 | 17494 | 18833 | 19744 | 20206 | 19956
6918 | 6918 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 6 | 14219 | 14716 | 14840 | 13883 | 13570 | 16537 | 16807 | 17207 | 17195 | 15493 | 17755 | 18825 | 19020 | 19094 | 18046 | 17275 | 19443 | 20381 | 20659 | 20483
6919 | 6919 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 7 | 15691 | 16180 | 16372 | 14430 | 14092 | 17908 | 18242 | 18519 | 18430 | 15765 | 18922 | 19783 | 20163 | 20041 | 18009 | 17346 | 20366 | 21332 | 21410 | 21309
6920 | 6920 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 8 | 16026 | 16526 | 16838 | 14941 | 14461 | 18154 | 18615 | 18793 | 18739 | 16106 | 19241 | 19758 | 20353 | 20198 | 18195 | 17556 | 20617 | 21402 | 21467 | 21390
6921 | 6921 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 9 | 16041 | 16656 | 16823 | 15439 | 14951 | 18085 | 18730 | 18850 | 18632 | 16606 | 19318 | 19564 | 20274 | 20011 | 18462 | 17907 | 20642 | 21252 | 21421 | 21151
6922 | 6922 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 10 | 16127 | 16875 | 16979 | 15947 | 15425 | 18165 | 18965 | 19082 | 18851 | 17112 | 19520 | 19725 | 20600 | 20105 | 19086 | 18274 | 20899 | 21599 | 21756 | 21278
6923 | 6923 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 11 | 16046 | 16934 | 16928 | 16179 | 15619 | 18118 | 19141 | 19209 | 18775 | 17422 | 19651 | 19767 | 20851 | 19936 | 19342 | 18160 | 20993 | 21893 | 21998 | 21166
6924 | 6924 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 12 | 15799 | 16908 | 16727 | 16152 | 15615 | 17977 | 19117 | 19187 | 18459 | 17514 | 19643 | 19652 | 20847 | 19763 | 19207 | 17982 | 20820 | 21912 | 22016 | 21025
6925 | 6925 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 13 | 15777 | 17031 | 16763 | 16056 | 15662 | 17968 | 19248 | 19335 | 18493 | 17567 | 19802 | 19647 | 20988 | 19801 | 19037 | 17919 | 20940 | 22043 | 22161 | 21056
6926 | 6926 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 14 | 15767 | 17246 | 16887 | 16144 | 15846 | 17960 | 19446 | 19499 | 18560 | 17722 | 19902 | 19597 | 21151 | 19889 | 19068 | 18087 | 21054 | 22178 | 22255 | 21117
6927 | 6927 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 15 | 15788 | 17405 | 16995 | 16183 | 16073 | 17926 | 19516 | 19524 | 18503 | 17867 | 19943 | 19477 | 21128 | 20025 | 19001 | 18491 | 21156 | 22158 | 22178 | 21215
6928 | 6928 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 16 | 15817 | 17468 | 16987 | 16141 | 16191 | 17966 | 19386 | 19361 | 18266 | 17830 | 19950 | 19507 | 20862 | 19816 | 18820 | 18697 | 21233 | 21853 | 21820 | 20973
6929 | 6929 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 17 | 15846 | 17374 | 16900 | 16230 | 16476 | 17908 | 19395 | 19284 | 18108 | 18047 | 20120 | 19346 | 20857 | 19696 | 18901 | 19125 | 21428 | 21876 | 21759 | 20863
6930 | 6930 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 18 | 15769 | 17187 | 16728 | 16381 | 16609 | 17627 | 18816 | 19039 | 18153 | 18132 | 20218 | 19054 | 20340 | 19676 | 19297 | 19648 | 21780 | 21453 | 21891 | 20917
6931 | 6931 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 19 | 16184 | 17551 | 16977 | 16614 | 16941 | 18041 | 19269 | 19547 | 18673 | 18627 | 20679 | 19845 | 21061 | 20532 | 20059 | 20366 | 22490 | 22389 | 22936 | 21936
6932 | 6932 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 20 | 15875 | 17326 | 16843 | 16246 | 16703 | 17965 | 19128 | 19548 | 18809 | 18501 | 20593 | 20174 | 21468 | 21097 | 20454 | 20676 | 22622 | 23042 | 23539 | 22694
6933 | 6933 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 21 | 15299 | 16764 | 16297 | 15806 | 16309 | 17552 | 18666 | 19242 | 18598 | 18352 | 20254 | 20229 | 21546 | 21371 | 20816 | 20934 | 22628 | 23402 | 24006 | 23197
6934 | 6934 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 22 | 14211 | 15699 | 15285 | 15173 | 15615 | 16597 | 17660 | 18384 | 17828 | 17851 | 19452 | 19586 | 20888 | 20899 | 20708 | 20651 | 22016 | 22913 | 23630 | 22865
6935 | 6935 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 23 | 13115 | 14534 | 14182 | 14538 | 14942 | 15587 | 16587 | 17366 | 16876 | 17288 | 18561 | 18740 | 20013 | 20101 | 20340 | 20215 | 21224 | 22112 | 22879 | 22158
6936 | 6936 | 289 | 10 | 16 | Autumn | 10 | 15 | Autumn | 24 | 12371 | 13701 | 13370 | 14000 | 14330 | 14915 | 15878 | 16646 | 16224 | 16811 | 17936 | 18197 | 19425 | 19519 | 20032 | 19782 | 20676 | 21585 | 22340 | 21631
6937 | 6937 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 1 | 12287 | 12477 | 13263 | 13154 | 13693 | 14749 | 15315 | 15414 | 15990 | 16100 | 17446 | 18183 | 19030 | 19070 | 18354 | 18996 | 20460 | 21248 | 21149 | 21068
6938 | 6938 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 2 | 12051 | 12205 | 12951 | 12914 | 13590 | 14495 | 15089 | 15160 | 15721 | 16024 | 17227 | 17904 | 18705 | 18708 | 18036 | 18795 | 20140 | 20863 | 20715 | 20653
6939 | 6939 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 3 | 11956 | 12093 | 12839 | 12806 | 13601 | 14445 | 15063 | 15100 | 15660 | 16078 | 17146 | 17801 | 18584 | 18540 | 17923 | 18761 | 19952 | 20659 | 20480 | 20410
6940 | 6940 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 4 | 12052 | 12172 | 12822 | 12763 | 13684 | 14481 | 15064 | 15081 | 15505 | 16041 | 16950 | 17539 | 18247 | 18069 | 17502 | 18472 | 19485 | 20121 | 19934 | 19780
6941 | 6941 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 5 | 12580 | 12687 | 12960 | 12773 | 14187 | 14923 | 15482 | 15485 | 15430 | 16316 | 17163 | 17613 | 18250 | 17706 | 17060 | 18449 | 19334 | 19894 | 19668 | 19233
6942 | 6942 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 6 | 13980 | 14025 | 13407 | 13151 | 15378 | 16220 | 16684 | 16681 | 15620 | 17286 | 18191 | 18529 | 18929 | 17554 | 16854 | 19067 | 20036 | 20343 | 20187 | 18895
6943 | 6943 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 7 | 15561 | 15564 | 13965 | 13662 | 16703 | 17665 | 18022 | 17953 | 15945 | 18479 | 19303 | 19692 | 19814 | 17525 | 16920 | 19966 | 20911 | 21067 | 20973 | 18732
6944 | 6944 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 8 | 15944 | 15976 | 14486 | 14017 | 17077 | 18020 | 18286 | 18267 | 16351 | 18794 | 19336 | 19884 | 19949 | 17709 | 17121 | 20201 | 20763 | 21109 | 21029 | 18861
6945 | 6945 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 9 | 16036 | 15985 | 15006 | 14531 | 17226 | 18137 | 18360 | 18193 | 16756 | 18892 | 19207 | 19839 | 19976 | 17990 | 17488 | 20242 | 20535 | 21069 | 20795 | 19094
6946 | 6946 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 10 | 16165 | 16066 | 15433 | 14901 | 17274 | 18275 | 18500 | 18301 | 17249 | 19010 | 19344 | 20056 | 20174 | 18524 | 17765 | 20399 | 20730 | 21321 | 20840 | 19674
6947 | 6947 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 11 | 16326 | 16045 | 15697 | 15193 | 17384 | 18467 | 18642 | 18346 | 17573 | 19170 | 19411 | 20327 | 20385 | 18802 | 17675 | 20523 | 20860 | 21585 | 20751 | 19996
6948 | 6948 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 12 | 16311 | 15892 | 15697 | 15313 | 17400 | 18466 | 18641 | 18184 | 17578 | 19184 | 19244 | 20349 | 20408 | 18691 | 17523 | 20379 | 20712 | 21629 | 20624 | 19895
6949 | 6949 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 13 | 16388 | 15857 | 15553 | 15315 | 17524 | 18550 | 18742 | 18179 | 17451 | 19298 | 19196 | 20439 | 20518 | 18476 | 17416 | 20448 | 20660 | 21734 | 20610 | 19671
6950 | 6950 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 14 | 16548 | 15935 | 15591 | 15455 | 17608 | 18701 | 18860 | 18211 | 17444 | 19351 | 19152 | 20548 | 20579 | 18459 | 17533 | 20507 | 20573 | 21773 | 20630 | 19633
6951 | 6951 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 15 | 16637 | 15983 | 15572 | 15643 | 17683 | 18711 | 18826 | 18115 | 17289 | 19312 | 19060 | 20470 | 20452 | 18316 | 17861 | 20546 | 20447 | 21618 | 20660 | 19473
6952 | 6952 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 16 | 16818 | 16151 | 15688 | 15924 | 18007 | 18763 | 18847 | 18054 | 17190 | 19474 | 19379 | 20355 | 20289 | 18275 | 18202 | 20759 | 20738 | 21393 | 20538 | 19400
6953 | 6953 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 17 | 16959 | 16167 | 15868 | 16262 | 18214 | 18876 | 18866 | 17930 | 17318 | 19723 | 19494 | 20442 | 20303 | 18442 | 18717 | 21047 | 20950 | 21419 | 20516 | 19581
6954 | 6954 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 18 | 16564 | 16047 | 16054 | 16327 | 18419 | 18396 | 18670 | 17824 | 17528 | 19839 | 19436 | 19962 | 20402 | 18881 | 19283 | 21449 | 20951 | 21611 | 20622 | 20085
6955 | 6955 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 19 | 16899 | 16273 | 16249 | 16622 | 18676 | 18811 | 19128 | 18279 | 17833 | 20228 | 19969 | 20613 | 21230 | 19584 | 19967 | 22129 | 21794 | 22626 | 21620 | 20933
6956 | 6956 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 20 | 16632 | 16114 | 15872 | 16376 | 18356 | 18649 | 19099 | 18361 | 17783 | 20094 | 20210 | 20959 | 21603 | 19943 | 20255 | 22255 | 22405 | 23242 | 22394 | 21477
6957 | 6957 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 21 | 15974 | 15550 | 15405 | 15965 | 17702 | 18146 | 18738 | 18071 | 17628 | 19675 | 20080 | 20957 | 21796 | 20247 | 20478 | 22231 | 22696 | 23707 | 22909 | 21992
6958 | 6958 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 22 | 14816 | 14532 | 14762 | 15271 | 16694 | 17109 | 17847 | 17261 | 17231 | 18852 | 19395 | 20254 | 21257 | 20125 | 20189 | 21616 | 22262 | 23341 | 22597 | 22012
6959 | 6959 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 23 | 13589 | 13418 | 14091 | 14563 | 15633 | 15996 | 16780 | 16243 | 16701 | 17920 | 18554 | 19323 | 20380 | 19722 | 19719 | 20791 | 21566 | 22565 | 21852 | 21677
6960 | 6960 | 290 | 10 | 17 | Autumn | 10 | 16 | Autumn | 24 | 12708 | 12570 | 13510 | 13912 | 14880 | 15235 | 16004 | 15537 | 16284 | 17271 | 17961 | 18699 | 19757 | 19377 | 19259 | 20214 | 21014 | 21994 | 21301 | 21389
6961 | 6961 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 1 | 12315 | 12662 | 12854 | 13435 | 14238 | 14812 | 14923 | 15481 | 15321 | 16892 | 17843 | 18437 | 18704 | 17939 | 18648 | 20119 | 20996 | 20963 | 20913 | 19693
6962 | 6962 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 2 | 12057 | 12338 | 12591 | 13300 | 14005 | 14557 | 14648 | 15194 | 15089 | 16675 | 17611 | 18115 | 18328 | 17616 | 18438 | 19792 | 20646 | 20512 | 20481 | 19327
6963 | 6963 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 3 | 11970 | 12202 | 12474 | 13303 | 13932 | 14531 | 14597 | 15142 | 15047 | 16630 | 17558 | 18029 | 18192 | 17528 | 18425 | 19616 | 20486 | 20294 | 20261 | 19187
6964 | 6964 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 4 | 12045 | 12187 | 12439 | 13393 | 13955 | 14560 | 14620 | 15035 | 14915 | 16499 | 17407 | 17754 | 17861 | 17147 | 18170 | 19181 | 20021 | 19764 | 19649 | 18679
6965 | 6965 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 5 | 12628 | 12323 | 12436 | 13896 | 14417 | 15002 | 15064 | 15007 | 14781 | 16765 | 17591 | 17817 | 17849 | 16733 | 18169 | 19050 | 19937 | 19501 | 19093 | 18110
6966 | 6966 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 6 | 13977 | 12777 | 12825 | 15106 | 15718 | 16236 | 16324 | 15273 | 14951 | 17859 | 18527 | 18577 | 18633 | 16565 | 18816 | 19781 | 20576 | 20034 | 18758 | 17794
6967 | 6967 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 7 | 15431 | 13361 | 13363 | 16459 | 17206 | 17607 | 17656 | 15675 | 15240 | 19039 | 19783 | 19537 | 19602 | 16663 | 19729 | 20696 | 21511 | 20834 | 18600 | 17797
6968 | 6968 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 8 | 15750 | 13901 | 13734 | 16812 | 17491 | 17867 | 17985 | 16109 | 15583 | 19104 | 20084 | 19683 | 19744 | 16866 | 19970 | 20558 | 21598 | 20885 | 18716 | 17963
6969 | 6969 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 9 | 15803 | 14367 | 14187 | 16874 | 17351 | 17876 | 17844 | 16451 | 16020 | 18926 | 19869 | 19645 | 19479 | 17166 | 19944 | 20250 | 21259 | 20573 | 18873 | 18220
6970 | 6970 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 10 | 15993 | 14842 | 14633 | 17008 | 17434 | 18076 | 18018 | 17009 | 16476 | 19126 | 19942 | 19917 | 19529 | 17511 | 20170 | 20513 | 21165 | 20693 | 19523 | 18600
6971 | 6971 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 11 | 16017 | 15016 | 14838 | 17030 | 17338 | 18107 | 17957 | 17236 | 16743 | 19091 | 19920 | 20028 | 19321 | 17323 | 20199 | 20555 | 20866 | 20506 | 19751 | 18446
6972 | 6972 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 12 | 16018 | 15018 | 14959 | 17053 | 17165 | 18103 | 17788 | 17240 | 16858 | 18921 | 19768 | 20050 | 19164 | 17170 | 20055 | 20402 | 20581 | 20374 | 19649 | 18297
6973 | 6973 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 13 | 16139 | 14944 | 15017 | 17231 | 17169 | 18259 | 17838 | 17162 | 16914 | 18931 | 19822 | 20212 | 19207 | 17121 | 20192 | 20403 | 20526 | 20427 | 19484 | 18243
6974 | 6974 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 14 | 16261 | 14930 | 15111 | 17276 | 17138 | 18333 | 17830 | 17118 | 16980 | 18844 | 19811 | 20235 | 19203 | 17192 | 20205 | 20276 | 20554 | 20388 | 19396 | 18296
6975 | 6975 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 15 | 16321 | 14904 | 15305 | 17356 | 17141 | 18311 | 17735 | 16965 | 17038 | 18737 | 19761 | 20101 | 19240 | 17505 | 20229 | 20135 | 20754 | 20399 | 19219 | 18598
6976 | 6976 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 16 | 16571 | 15055 | 15646 | 17746 | 17544 | 18401 | 17737 | 16936 | 17191 | 19079 | 19918 | 19990 | 19224 | 17883 | 20477 | 20470 | 21143 | 20310 | 19173 | 18957
6977 | 6977 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 17 | 16618 | 15296 | 16042 | 18016 | 17850 | 18490 | 17671 | 17122 | 17551 | 19240 | 20242 | 20056 | 19242 | 18446 | 20811 | 20735 | 21521 | 20326 | 19405 | 19541
6978 | 6978 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 18 | 16496 | 15519 | 16118 | 18254 | 17914 | 18348 | 17591 | 17336 | 17719 | 19181 | 20327 | 20130 | 19290 | 19031 | 21230 | 20748 | 21785 | 20479 | 19946 | 20176
6979 | 6979 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 19 | 16852 | 15720 | 16408 | 18503 | 18141 | 18801 | 18029 | 17604 | 18169 | 19666 | 20827 | 20905 | 20092 | 19697 | 21900 | 21568 | 22694 | 21502 | 20807 | 20961
6980 | 6980 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 20 | 16610 | 15311 | 16137 | 18156 | 18024 | 18732 | 18059 | 17481 | 17992 | 19820 | 21128 | 21192 | 20604 | 19940 | 21988 | 22140 | 23388 | 22269 | 21345 | 21345
6981 | 6981 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 21 | 16040 | 14809 | 15697 | 17467 | 17489 | 18327 | 17695 | 17242 | 17785 | 19593 | 21119 | 21289 | 20801 | 20109 | 21920 | 22384 | 23833 | 22747 | 21859 | 21682
6982 | 6982 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 22 | 14971 | 14124 | 14973 | 16434 | 16508 | 17387 | 16833 | 16781 | 17251 | 18852 | 20400 | 20688 | 20303 | 19777 | 21272 | 21914 | 23386 | 22424 | 21860 | 21457
6983 | 6983 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 23 | 13802 | 13473 | 14265 | 15386 | 15521 | 16313 | 15797 | 16233 | 16661 | 18000 | 19464 | 19801 | 19481 | 19310 | 20460 | 21230 | 22553 | 21687 | 21547 | 21044
6984 | 6984 | 291 | 10 | 18 | Autumn | 10 | 17 | Autumn | 24 | 12969 | 12894 | 13614 | 14636 | 14797 | 15521 | 15070 | 15792 | 16157 | 17416 | 18817 | 19172 | 18877 | 18857 | 19886 | 20684 | 21971 | 21139 | 21266 | 20644
6985 | 6985 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 1 | 12310 | 12669 | 13544 | 14360 | 14915 | 14824 | 15434 | 15303 | 16007 | 17675 | 18265 | 18502 | 19006 | 18649 | 20139 | 21045 | 21466 | 21150 | 19964 | 20397
6986 | 6986 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 2 | 12040 | 12402 | 13408 | 14112 | 14686 | 14540 | 15137 | 15060 | 15924 | 17461 | 17963 | 18156 | 18650 | 18462 | 19835 | 20717 | 21087 | 20736 | 19610 | 20169
6987 | 6987 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 3 | 11924 | 12237 | 13370 | 14010 | 14617 | 14465 | 15066 | 15001 | 15968 | 17422 | 17905 | 18023 | 18492 | 18434 | 19647 | 20550 | 20909 | 20492 | 19455 | 20093
6988 | 6988 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 4 | 11997 | 12186 | 13449 | 14039 | 14691 | 14501 | 14982 | 14899 | 15962 | 17324 | 17722 | 17748 | 18062 | 18202 | 19236 | 20110 | 20418 | 19881 | 18941 | 19738
6989 | 6989 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 5 | 12509 | 12224 | 13961 | 14510 | 15195 | 14986 | 15010 | 14805 | 16279 | 17583 | 17823 | 17802 | 17751 | 18245 | 19150 | 20054 | 20161 | 19343 | 18383 | 19631
6990 | 6990 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 6 | 13847 | 12571 | 15167 | 15799 | 16461 | 16265 | 15320 | 15005 | 17292 | 18574 | 18579 | 18636 | 17650 | 18910 | 19903 | 20694 | 20558 | 19006 | 18052 | 20151
6991 | 6991 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 7 | 15448 | 13154 | 16582 | 17361 | 17998 | 17658 | 15817 | 15393 | 18567 | 19923 | 19723 | 19707 | 17706 | 19889 | 20881 | 21685 | 21459 | 18891 | 18087 | 21047
6992 | 6992 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 8 | 15842 | 13548 | 16953 | 17659 | 18448 | 17999 | 16280 | 15758 | 18891 | 20270 | 20049 | 19882 | 17904 | 20146 | 20767 | 21787 | 21653 | 19013 | 18251 | 21265
6993 | 6993 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 9 | 15675 | 13909 | 16931 | 17421 | 18275 | 17760 | 16528 | 16121 | 18831 | 19978 | 19825 | 19541 | 18024 | 20031 | 20360 | 21366 | 21299 | 19064 | 18403 | 21108
6994 | 6994 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 10 | 15547 | 13995 | 16687 | 17132 | 17977 | 17501 | 16638 | 16157 | 18720 | 19576 | 19577 | 19312 | 18331 | 19950 | 20322 | 21000 | 21294 | 19409 | 18482 | 21061
6995 | 6995 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 11 | 15401 | 14058 | 16556 | 16818 | 17842 | 17207 | 16615 | 16138 | 18744 | 19260 | 19386 | 19034 | 18472 | 19942 | 20330 | 20636 | 21310 | 19601 | 18297 | 21083
6996 | 6996 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 12 | 15369 | 14300 | 16680 | 16748 | 17793 | 17128 | 16710 | 16348 | 18875 | 19195 | 19321 | 18979 | 18475 | 19901 | 20276 | 20467 | 21162 | 19602 | 18252 | 21049
6997 | 6997 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 13 | 15419 | 14436 | 16933 | 16832 | 17881 | 17249 | 16701 | 16479 | 19082 | 19315 | 19349 | 19109 | 18353 | 20107 | 20358 | 20499 | 21139 | 19515 | 18274 | 21248
6998 | 6998 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 14 | 15546 | 14661 | 17105 | 16929 | 18008 | 17381 | 16799 | 16682 | 19186 | 19454 | 19433 | 19203 | 18387 | 20224 | 20337 | 20620 | 21117 | 19530 | 18429 | 21346
6999 | 6999 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 15 | 15709 | 15042 | 17433 | 17195 | 18197 | 17587 | 16959 | 17071 | 19277 | 19744 | 19605 | 19358 | 18359 | 20361 | 20304 | 20932 | 21044 | 19459 | 18837 | 21468
7000 | 7000 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 16 | 15927 | 15501 | 17956 | 17707 | 18557 | 17767 | 17111 | 17407 | 19509 | 20090 | 19760 | 19376 | 18376 | 20640 | 20666 | 21345 | 20944 | 19435 | 19215 | 21723
7001 | 7001 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 17 | 16008 | 15911 | 18236 | 18032 | 18942 | 17725 | 17312 | 17777 | 19827 | 20417 | 20102 | 19385 | 18604 | 20978 | 20925 | 21718 | 21374 | 19669 | 19794 | 22071
7002 | 7002 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 18 | 15904 | 15972 | 18443 | 18141 | 19092 | 17666 | 17516 | 17923 | 19966 | 20465 | 20426 | 19386 | 19047 | 21379 | 20923 | 21961 | 22079 | 20196 | 20436 | 22538
7003 | 7003 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 19 | 16133 | 16221 | 18667 | 18349 | 19408 | 18075 | 17744 | 18330 | 20326 | 20895 | 21003 | 20128 | 19717 | 22007 | 21708 | 22842 | 22897 | 21061 | 21216 | 23278
7004 | 7004 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 20 | 15921 | 15931 | 18273 | 18185 | 19234 | 18047 | 17553 | 18087 | 20105 | 21086 | 21212 | 20545 | 19988 | 22028 | 22216 | 23482 | 23580 | 21571 | 21578 | 23429
7005 | 7005 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 21 | 15344 | 15492 | 17582 | 17623 | 18809 | 17650 | 17270 | 17833 | 19639 | 20993 | 21295 | 20666 | 20231 | 21932 | 22420 | 23892 | 24114 | 22091 | 21929 | 23495
7006 | 7006 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 22 | 14311 | 14753 | 16529 | 16615 | 17780 | 16751 | 16762 | 17253 | 18767 | 20220 | 20661 | 20109 | 20061 | 21254 | 21931 | 23410 | 23743 | 22086 | 21704 | 22918
7007 | 7007 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 23 | 13199 | 14008 | 15438 | 15595 | 16646 | 15666 | 16160 | 16609 | 17807 | 19230 | 19806 | 19230 | 19633 | 20406 | 21198 | 22544 | 23024 | 21739 | 21268 | 22109
7008 | 7008 | 292 | 10 | 19 | Autumn | 10 | 18 | Autumn | 24 | 12377 | 13369 | 14684 | 14870 | 15857 | 14921 | 15698 | 16086 | 17163 | 18589 | 19219 | 18621 | 19301 | 19838 | 20657 | 21967 | 22497 | 21460 | 20866 | 21577
7009 | 7009 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 1 | 12398 | 12849 | 13928 | 14513 | 14773 | 14841 | 14808 | 15478 | 16642 | 17557 | 18358 | 18329 | 17863 | 19581 | 20541 | 21005 | 21683 | 19729 | 20164 | 21496
7010 | 7010 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 2 | 12115 | 12718 | 13701 | 14287 | 14530 | 14564 | 14585 | 15405 | 16447 | 17311 | 17979 | 18011 | 17584 | 19306 | 20238 | 20643 | 21158 | 19390 | 19958 | 21175
7011 | 7011 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 3 | 11973 | 12661 | 13586 | 14209 | 14501 | 14484 | 14519 | 15451 | 16410 | 17280 | 17861 | 17881 | 17496 | 19146 | 20093 | 20488 | 20930 | 19237 | 19893 | 20956
7012 | 7012 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 4 | 11934 | 12722 | 13590 | 14264 | 14554 | 14388 | 14404 | 15443 | 16304 | 17125 | 17606 | 17493 | 17130 | 18755 | 19670 | 20010 | 20368 | 18712 | 19522 | 20424
7013 | 7013 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 5 | 12077 | 13253 | 14069 | 14793 | 14977 | 14458 | 14356 | 15816 | 16631 | 17312 | 17745 | 17247 | 16764 | 18714 | 19653 | 19787 | 20146 | 18165 | 19418 | 20199
7014 | 7014 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 6 | 12509 | 14480 | 15359 | 16074 | 16141 | 14803 | 14606 | 16878 | 17761 | 18147 | 18597 | 17230 | 16617 | 19528 | 20350 | 20220 | 20553 | 17861 | 19965 | 20835
7015 | 7015 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 7 | 13166 | 15941 | 16979 | 17669 | 17674 | 15364 | 15075 | 18245 | 19050 | 19398 | 19695 | 17376 | 16804 | 20564 | 21405 | 21168 | 21299 | 17922 | 20867 | 21736
7016 | 7016 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 8 | 13757 | 16343 | 17329 | 18148 | 18114 | 15850 | 15471 | 18612 | 19179 | 19770 | 19828 | 17632 | 17052 | 20496 | 21550 | 21393 | 21333 | 18111 | 21108 | 21578
7017 | 7017 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 9 | 14239 | 16432 | 17221 | 18086 | 18042 | 16205 | 15959 | 18682 | 19022 | 19677 | 19644 | 17864 | 17375 | 20204 | 21247 | 21143 | 21124 | 18367 | 21053 | 21233
7018 | 7018 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 10 | 14517 | 16442 | 17180 | 17926 | 17942 | 16585 | 16277 | 18703 | 18930 | 19726 | 19636 | 18318 | 17587 | 20319 | 21038 | 21286 | 21029 | 18603 | 21163 | 21390
7019 | 7019 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 11 | 14628 | 16472 | 17040 | 17810 | 17808 | 16760 | 16466 | 18713 | 18683 | 19755 | 19604 | 18539 | 17434 | 20393 | 20750 | 21383 | 20802 | 18495 | 21265 | 21513
7020 | 7020 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 12 | 14550 | 16371 | 16736 | 17495 | 17541 | 16585 | 16397 | 18534 | 18423 | 19384 | 19327 | 18348 | 17203 | 20168 | 20402 | 21050 | 20532 | 18274 | 21061 | 21302
7021 | 7021 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 13 | 14440 | 16413 | 16620 | 17413 | 17439 | 16357 | 16304 | 18546 | 18381 | 19174 | 19141 | 18106 | 17112 | 20086 | 20270 | 20904 | 20375 | 18132 | 21102 | 21214
7022 | 7022 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 14 | 14374 | 16397 | 16538 | 17393 | 17385 | 16273 | 16321 | 18509 | 18274 | 19071 | 19016 | 17985 | 17118 | 19901 | 20226 | 20722 | 20267 | 18118 | 21031 | 21007
7023 | 7023 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 15 | 14497 | 16631 | 16704 | 17592 | 17553 | 16286 | 16551 | 18626 | 18452 | 19055 | 18920 | 17919 | 17486 | 19855 | 20523 | 20611 | 20322 | 18508 | 21135 | 20941
7024 | 7024 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 16 | 14840 | 17280 | 17282 | 18187 | 17992 | 16570 | 17013 | 19138 | 19090 | 19333 | 19099 | 18070 | 18007 | 20344 | 21059 | 20640 | 20554 | 19000 | 21499 | 21389
7025 | 7025 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 17 | 15139 | 17662 | 17728 | 18698 | 18435 | 16917 | 17526 | 19600 | 19319 | 19825 | 19385 | 18352 | 18623 | 20676 | 21499 | 21129 | 20850 | 19651 | 21915 | 21734
7026 | 7026 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 18 | 15272 | 17796 | 17816 | 18825 | 18547 | 17097 | 17616 | 19672 | 19190 | 20064 | 19577 | 18674 | 19107 | 20591 | 21656 | 21760 | 21292 | 20223 | 22308 | 21711
7027 | 7027 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 19 | 15448 | 17993 | 18001 | 19112 | 18846 | 17299 | 17989 | 19988 | 19614 | 20563 | 20127 | 19275 | 19719 | 21311 | 22477 | 22522 | 22184 | 20987 | 23033 | 22590
7028 | 7028 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 20 | 15031 | 17616 | 17841 | 18935 | 18799 | 17109 | 17740 | 19749 | 19710 | 20710 | 20257 | 19503 | 19924 | 21794 | 23097 | 23200 | 22640 | 21371 | 23212 | 23256
7029 | 7029 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 21 | 14474 | 16862 | 17204 | 18426 | 18406 | 16731 | 17397 | 19178 | 19369 | 20646 | 20251 | 19614 | 20009 | 21897 | 23411 | 23647 | 23091 | 21677 | 23233 | 23563
7030 | 7030 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 22 | 13786 | 15821 | 16184 | 17381 | 17481 | 16196 | 16790 | 18275 | 18592 | 19965 | 19671 | 19395 | 19658 | 21378 | 22908 | 23263 | 22792 | 21456 | 22667 | 23171
7031 | 7031 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 23 | 13123 | 14733 | 15157 | 16243 | 16441 | 15582 | 16133 | 17293 | 17690 | 19092 | 18893 | 18945 | 19159 | 20641 | 22043 | 22546 | 22140 | 21033 | 21877 | 22508
7032 | 7032 | 293 | 10 | 20 | Autumn | 10 | 19 | Autumn | 24 | 12552 | 13959 | 14407 | 15437 | 15653 | 15084 | 15575 | 16617 | 17090 | 18488 | 18264 | 18587 | 18703 | 20080 | 21447 | 22004 | 21605 | 20611 | 21340 | 21999
7033 | 7033 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 1 | 11949 | 13288 | 14146 | 14440 | 14853 | 14356 | 15066 | 16122 | 16942 | 17719 | 17815 | 17343 | 18138 | 20037 | 20568 | 21283 | 20968 | 19995 | 21342 | 22030
7034 | 7034 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 2 | 11682 | 13034 | 13883 | 14152 | 14475 | 14078 | 14939 | 15885 | 16737 | 17315 | 17487 | 17051 | 17948 | 19726 | 20196 | 20745 | 20527 | 19760 | 20996 | 21670
7035 | 7035 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 3 | 11505 | 12914 | 13783 | 14092 | 14365 | 13998 | 14980 | 15837 | 16693 | 17234 | 17369 | 16961 | 17930 | 19581 | 20032 | 20508 | 20288 | 19678 | 20756 | 21462
7036 | 7036 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 4 | 11455 | 12966 | 13878 | 14171 | 14409 | 13930 | 15027 | 15779 | 16639 | 17080 | 17019 | 16665 | 17747 | 19233 | 19623 | 20003 | 19648 | 19346 | 20253 | 20954
7037 | 7037 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 5 | 11508 | 13483 | 14436 | 14650 | 14940 | 13932 | 15461 | 16199 | 16987 | 17321 | 16937 | 16381 | 17845 | 19292 | 19470 | 19844 | 19172 | 19281 | 20063 | 20819
7038 | 7038 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 6 | 11844 | 14780 | 15719 | 15858 | 16188 | 14215 | 16582 | 17396 | 18044 | 18265 | 17170 | 16329 | 18571 | 20048 | 19955 | 20314 | 19035 | 19844 | 20710 | 21374
7039 | 7039 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 7 | 12439 | 16417 | 17295 | 17421 | 17544 | 14689 | 17981 | 18756 | 19471 | 19421 | 17518 | 16558 | 19596 | 21133 | 20918 | 21075 | 19154 | 20741 | 21600 | 22294
7040 | 7040 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 8 | 12859 | 16777 | 17775 | 17852 | 17822 | 15081 | 18355 | 18913 | 19854 | 19583 | 17706 | 16823 | 19887 | 21292 | 21158 | 21107 | 19204 | 20975 | 21439 | 22358
7041 | 7041 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 9 | 13429 | 16791 | 17824 | 17885 | 17822 | 15672 | 18537 | 18893 | 19786 | 19521 | 17945 | 17256 | 19980 | 21108 | 21016 | 20999 | 19321 | 21023 | 21206 | 22105
7042 | 7042 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 10 | 13938 | 16871 | 17780 | 17961 | 17937 | 16054 | 18608 | 18965 | 19878 | 19535 | 18197 | 17644 | 20245 | 21089 | 21346 | 21081 | 19630 | 21323 | 21552 | 22122
7043 | 7043 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 11 | 14176 | 16597 | 17517 | 17747 | 17869 | 15995 | 18341 | 18563 | 19815 | 19153 | 18098 | 17514 | 20341 | 20815 | 21454 | 20875 | 19604 | 21440 | 21698 | 21889
7044 | 7044 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 12 | 14362 | 16424 | 17319 | 17506 | 17768 | 16008 | 18230 | 18247 | 19616 | 18899 | 17916 | 17461 | 20289 | 20633 | 21287 | 20788 | 19433 | 21405 | 21653 | 21726
7045 | 7045 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 13 | 14384 | 16390 | 17307 | 17378 | 17679 | 15977 | 18304 | 18151 | 19581 | 18762 | 17767 | 17405 | 20414 | 20578 | 21223 | 20663 | 19278 | 21528 | 21641 | 21665
7046 | 7046 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 14 | 14516 | 16403 | 17385 | 17413 | 17681 | 16101 | 18377 | 18135 | 19617 | 18754 | 17674 | 17502 | 20448 | 20624 | 21129 | 20626 | 19151 | 21541 | 21516 | 21692
7047 | 7047 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 15 | 14693 | 16556 | 17592 | 17530 | 17588 | 16395 | 18575 | 18280 | 19613 | 18772 | 17762 | 17788 | 20463 | 20800 | 20901 | 20599 | 19222 | 21524 | 21333 | 21855
7048 | 7048 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 16 | 15014 | 16924 | 18016 | 17809 | 17683 | 16723 | 18964 | 18753 | 19825 | 18855 | 17912 | 18052 | 20605 | 21075 | 20672 | 20565 | 19311 | 21621 | 21522 | 22090
7049 | 7049 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 17 | 15317 | 17176 | 18358 | 18155 | 17692 | 17079 | 19272 | 18934 | 20093 | 18995 | 18233 | 18456 | 20793 | 21292 | 20941 | 20656 | 19746 | 21819 | 21648 | 22332
7050 | 7050 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 18 | 15298 | 17364 | 18622 | 18404 | 17882 | 17336 | 19494 | 19021 | 20096 | 19335 | 18704 | 18895 | 21103 | 21435 | 21556 | 21111 | 20320 | 22211 | 21611 | 22557
7051 | 7051 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 19 | 15508 | 17509 | 18892 | 18676 | 18153 | 17687 | 19782 | 19398 | 20461 | 19815 | 19078 | 19443 | 21669 | 22203 | 22282 | 21958 | 21001 | 22930 | 22478 | 23498
7052 | 7052 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 20 | 15224 | 17286 | 18669 | 18573 | 17893 | 17396 | 19489 | 19406 | 20588 | 19829 | 19228 | 19562 | 21651 | 22745 | 22881 | 22348 | 21529 | 23090 | 23115 | 24232
7053 | 7053 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 21 | 14760 | 16663 | 18154 | 18170 | 17476 | 17052 | 18903 | 19026 | 20387 | 19750 | 19324 | 19610 | 21490 | 23015 | 23307 | 22786 | 22064 | 23139 | 23453 | 24740
7054 | 7054 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 22 | 13999 | 15607 | 17061 | 17193 | 16565 | 16388 | 17936 | 18167 | 19552 | 19080 | 18975 | 19194 | 20770 | 22453 | 22873 | 22434 | 21972 | 22544 | 23039 | 24328
7055 | 7055 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 23 | 13263 | 14552 | 15906 | 16147 | 15577 | 15717 | 16937 | 17240 | 18537 | 18276 | 18438 | 18674 | 19915 | 21569 | 22134 | 21775 | 21575 | 21750 | 22381 | 23525
7056 | 7056 | 294 | 10 | 21 | Autumn | 10 | 20 | Autumn | 24 | 12637 | 13799 | 15086 | 15349 | 14801 | 15136 | 16237 | 16611 | 17872 | 17641 | 18029 | 18205 | 19334 | 20968 | 21590 | 21233 | 21216 | 21206 | 21872 | 22975
7057 | 7057 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 1 | 12219 | 13543 | 14125 | 14540 | 14474 | 14629 | 15677 | 16427 | 16913 | 17227 | 17050 | 17643 | 19108 | 20065 | 20852 | 20610 | 19768 | 21178 | 21891 | 22118
7058 | 7058 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 2 | 12077 | 13305 | 13860 | 14168 | 14189 | 14520 | 15463 | 16231 | 16646 | 16953 | 16824 | 17490 | 18843 | 19724 | 20340 | 20201 | 19443 | 20849 | 21546 | 21722
7059 | 7059 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 3 | 12022 | 13195 | 13792 | 14061 | 14087 | 14548 | 15411 | 16210 | 16646 | 16864 | 16786 | 17504 | 18695 | 19596 | 20136 | 19987 | 19323 | 20629 | 21356 | 21516
7060 | 7060 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 4 | 12100 | 13281 | 13879 | 14119 | 13972 | 14612 | 15390 | 16208 | 16565 | 16585 | 16588 | 17353 | 18367 | 19221 | 19658 | 19357 | 18870 | 20125 | 20843 | 20975
7061 | 7061 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 5 | 12648 | 13834 | 14356 | 14663 | 14157 | 15053 | 15835 | 16602 | 16837 | 16552 | 16473 | 17509 | 18399 | 19114 | 19536 | 18915 | 18540 | 19944 | 20709 | 20670
7062 | 7062 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 6 | 13873 | 15121 | 15582 | 15936 | 14690 | 16193 | 17082 | 17718 | 17745 | 16859 | 16564 | 18279 | 19264 | 19629 | 20031 | 18793 | 18393 | 20587 | 21251 | 20996
7063 | 7063 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 7 | 15307 | 16705 | 17167 | 17299 | 15390 | 17589 | 18480 | 19164 | 19027 | 17250 | 16857 | 19341 | 20320 | 20617 | 20811 | 18919 | 18435 | 21475 | 22166 | 21868
7064 | 7064 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 8 | 15737 | 17243 | 17661 | 17631 | 15799 | 18008 | 18721 | 19624 | 19450 | 17527 | 17029 | 19693 | 20306 | 20911 | 20903 | 19019 | 18439 | 21359 | 22264 | 22093
7065 | 7065 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 9 | 16048 | 17411 | 17810 | 17748 | 16236 | 18280 | 18806 | 19685 | 19586 | 17894 | 17418 | 19927 | 20252 | 20892 | 20911 | 19271 | 18758 | 21236 | 22115 | 22026
7066 | 7066 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 10 | 16277 | 17553 | 18075 | 17950 | 16543 | 18568 | 19103 | 19869 | 19744 | 18398 | 17956 | 20272 | 20633 | 21294 | 21068 | 19657 | 19161 | 21657 | 22213 | 22467
7067 | 7067 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 11 | 16245 | 17549 | 18174 | 17973 | 16579 | 18698 | 19115 | 19905 | 19503 | 18760 | 18177 | 20435 | 20775 | 21474 | 20936 | 19694 | 19044 | 21867 | 22058 | 22702
7068 | 7068 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 12 | 16198 | 17345 | 17930 | 17791 | 16412 | 18611 | 18825 | 19612 | 19112 | 18603 | 18106 | 20306 | 20656 | 21221 | 20756 | 19448 | 18850 | 21738 | 21800 | 22470
7069 | 7069 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 13 | 16303 | 17358 | 17843 | 17730 | 16293 | 18744 | 18793 | 19618 | 18955 | 18524 | 18092 | 20426 | 20652 | 21149 | 20631 | 19291 | 18737 | 21725 | 21749 | 22413
7070 | 7070 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 14 | 16367 | 17439 | 17885 | 17755 | 16215 | 18824 | 18785 | 19686 | 18957 | 18436 | 18120 | 20475 | 20543 | 21070 | 20612 | 19173 | 18783 | 21610 | 21786 | 22309
7071 | 7071 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 15 | 16487 | 17477 | 17822 | 17613 | 16221 | 18808 | 18700 | 19647 | 18957 | 18270 | 18084 | 20392 | 20285 | 20759 | 20501 | 19147 | 18995 | 21339 | 21859 | 21971
7072 | 7072 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 16 | 16863 | 17753 | 17949 | 17639 | 16386 | 19006 | 18932 | 19781 | 19062 | 18182 | 18245 | 20467 | 20428 | 20474 | 20415 | 19162 | 19394 | 21457 | 22035 | 21630
7073 | 7073 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 17 | 17023 | 17972 | 18165 | 17561 | 16726 | 19156 | 18940 | 19933 | 19379 | 18293 | 18623 | 20611 | 20504 | 20711 | 20471 | 19557 | 19827 | 21549 | 22240 | 21872
7074 | 7074 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 18 | 17174 | 18118 | 18221 | 17703 | 17022 | 19188 | 18824 | 19893 | 19753 | 18453 | 19136 | 20836 | 20359 | 21268 | 20870 | 20090 | 20549 | 21486 | 22423 | 22503
7075 | 7075 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 19 | 17371 | 18407 | 18495 | 17975 | 17067 | 19484 | 19191 | 20236 | 20210 | 18773 | 19475 | 21385 | 21046 | 21981 | 21701 | 20764 | 21228 | 22377 | 23377 | 23365
7076 | 7076 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 20 | 16952 | 18131 | 18353 | 17677 | 16860 | 19164 | 19145 | 20289 | 20248 | 18819 | 19468 | 21305 | 21437 | 22524 | 22037 | 21246 | 21532 | 22995 | 24110 | 24102
7077 | 7077 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 21 | 16196 | 17562 | 17892 | 17196 | 16524 | 18523 | 18683 | 19986 | 20107 | 18796 | 19396 | 21048 | 21486 | 22853 | 22393 | 21719 | 21810 | 23298 | 24579 | 24653
7078 | 7078 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 22 | 15119 | 16470 | 16878 | 16244 | 15873 | 17517 | 17766 | 19082 | 19331 | 18382 | 18856 | 20282 | 20890 | 22362 | 22001 | 21590 | 21465 | 22866 | 24156 | 24295
7079 | 7079 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 23 | 14032 | 15289 | 15801 | 15248 | 15188 | 16501 | 16808 | 18036 | 18432 | 17817 | 18211 | 19401 | 20132 | 21602 | 21316 | 21181 | 20915 | 22196 | 23332 | 23620
7080 | 7080 | 295 | 10 | 22 | Autumn | 10 | 21 | Autumn | 24 | 13262 | 14455 | 14964 | 14455 | 14619 | 15775 | 16147 | 17337 | 17799 | 17408 | 17806 | 18799 | 19560 | 21041 | 20761 | 20806 | 20549 | 21667 | 22771 | 23106
7081 | 7081 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 1 | 12345 | 13276 | 13917 | 13902 | 13859 | 14920 | 15683 | 16107 | 16773 | 16277 | 17334 | 18270 | 19245 | 20060 | 19915 | 19168 | 19986 | 21432 | 21682 | 22152
7082 | 7082 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 2 | 12113 | 13009 | 13542 | 13603 | 13608 | 14691 | 15475 | 15846 | 16398 | 16068 | 17186 | 18005 | 18952 | 19550 | 19506 | 18833 | 19746 | 21073 | 21274 | 21586
7083 | 7083 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 3 | 12019 | 12913 | 13417 | 13470 | 13551 | 14616 | 15436 | 15822 | 16334 | 16038 | 17214 | 17888 | 18849 | 19371 | 19312 | 18730 | 19714 | 20891 | 21084 | 21335
7084 | 7084 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 4 | 12071 | 12995 | 13484 | 13377 | 13527 | 14610 | 15463 | 15804 | 16242 | 15885 | 17169 | 17613 | 18534 | 18938 | 18719 | 18301 | 19425 | 20387 | 20548 | 20732
7085 | 7085 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 5 | 12567 | 13475 | 14044 | 13567 | 13656 | 15089 | 15905 | 16120 | 16523 | 15826 | 17354 | 17703 | 18639 | 18866 | 18315 | 17992 | 19352 | 20268 | 20247 | 20460
7086 | 7086 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 6 | 13874 | 14755 | 15387 | 14165 | 14056 | 16416 | 17120 | 17154 | 17570 | 16021 | 18231 | 18663 | 19461 | 19455 | 18278 | 17898 | 19933 | 20871 | 20620 | 20856
7087 | 7087 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 7 | 15495 | 16339 | 16792 | 14884 | 14548 | 17850 | 18615 | 18491 | 18757 | 16365 | 19484 | 19780 | 20579 | 20271 | 18433 | 17952 | 21030 | 21801 | 21483 | 21544
7088 | 7088 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 8 | 15912 | 16821 | 17140 | 15312 | 14800 | 18104 | 19092 | 18958 | 18996 | 16560 | 19998 | 19810 | 20805 | 20378 | 18543 | 17964 | 21450 | 21910 | 21702 | 21582
7089 | 7089 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 9 | 15951 | 16889 | 17192 | 15663 | 15232 | 18104 | 19085 | 19011 | 18962 | 16892 | 20068 | 19697 | 20675 | 20317 | 18726 | 18207 | 21388 | 21692 | 21550 | 21467
7090 | 7090 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 10 | 16106 | 17057 | 17300 | 15988 | 15631 | 18287 | 19157 | 19238 | 19147 | 17332 | 20166 | 19970 | 20647 | 20370 | 19010 | 18508 | 21357 | 21686 | 21897 | 21555
7091 | 7091 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 11 | 16100 | 17213 | 17381 | 16361 | 15842 | 18356 | 19258 | 19469 | 19250 | 17638 | 20239 | 20135 | 20462 | 20243 | 19054 | 18421 | 21002 | 21538 | 22144 | 21483
7092 | 7092 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 12 | 15923 | 17081 | 17331 | 16393 | 15857 | 18238 | 19146 | 19351 | 19058 | 17766 | 20138 | 20024 | 20220 | 20090 | 18838 | 18238 | 20629 | 21310 | 21941 | 21355
7093 | 7093 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 13 | 15816 | 16897 | 17177 | 16230 | 15745 | 18122 | 19072 | 19181 | 18885 | 17677 | 20093 | 19908 | 20057 | 19853 | 18570 | 18012 | 20485 | 21143 | 21765 | 21117
7094 | 7094 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 14 | 15772 | 16853 | 17114 | 16074 | 15732 | 18020 | 19039 | 19097 | 18821 | 17598 | 19973 | 19754 | 20051 | 19769 | 18384 | 18007 | 20388 | 21107 | 21592 | 21017
7095 | 7095 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 15 | 15785 | 16733 | 16925 | 15914 | 15766 | 17862 | 18917 | 18849 | 18602 | 17448 | 19826 | 19501 | 20156 | 19654 | 18353 | 18221 | 20514 | 21174 | 21245 | 20877
7096 | 7096 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 16 | 16153 | 16985 | 17074 | 16082 | 16201 | 18182 | 19139 | 18878 | 18610 | 17660 | 19897 | 19797 | 20520 | 19744 | 18536 | 18792 | 20812 | 21509 | 21066 | 20908
7097 | 7097 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 17 | 16405 | 17312 | 17096 | 16417 | 16693 | 18308 | 19401 | 19138 | 18655 | 18126 | 20342 | 19972 | 20800 | 19896 | 19029 | 19323 | 21450 | 21812 | 21406 | 21073
7098 | 7098 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 18 | 16500 | 17392 | 17234 | 16597 | 17184 | 18259 | 19406 | 19303 | 18755 | 18614 | 20698 | 19832 | 20911 | 20299 | 19571 | 20061 | 22211 | 22018 | 22065 | 21550
7099 | 7099 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 19 | 16618 | 17628 | 17440 | 16578 | 17348 | 18559 | 19666 | 19666 | 19164 | 18844 | 21039 | 20432 | 21622 | 21046 | 20168 | 20686 | 22745 | 22925 | 22887 | 22457
7100 | 7100 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 20 | 16366 | 17465 | 17118 | 16349 | 17009 | 18480 | 19672 | 19645 | 19096 | 18775 | 20962 | 20759 | 22096 | 21329 | 20615 | 20972 | 23034 | 23650 | 23629 | 22931
7101 | 7101 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 21 | 15693 | 16960 | 16598 | 15964 | 16601 | 17971 | 19309 | 19409 | 18894 | 18616 | 20726 | 20715 | 22270 | 21613 | 21027 | 21216 | 23136 | 24108 | 24166 | 23442
7102 | 7102 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 22 | 14631 | 15939 | 15631 | 15305 | 15847 | 17028 | 18367 | 18597 | 18165 | 18053 | 20019 | 20080 | 21664 | 21187 | 20875 | 20866 | 22616 | 23676 | 23824 | 23157
7103 | 7103 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 23 | 13579 | 14884 | 14640 | 14632 | 15081 | 16068 | 17316 | 17678 | 17347 | 17408 | 19188 | 19318 | 20772 | 20511 | 20483 | 20321 | 21875 | 22877 | 23163 | 22552
7104 | 7104 | 296 | 10 | 23 | Autumn | 10 | 22 | Autumn | 24 | 12835 | 14044 | 13829 | 14057 | 14546 | 15376 | 16582 | 17014 | 16694 | 16992 | 18640 | 18738 | 20157 | 19950 | 20106 | 19960 | 21372 | 22316 | 22659 | 22054
7105 | 7105 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 1 | 12502 | 13150 | 13417 | 13489 | 14274 | 15040 | 15486 | 16117 | 16208 | 16696 | 18434 | 18547 | 19150 | 19287 | 18673 | 19553 | 21489 | 21357 | 21858 | 21288
7106 | 7106 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 2 | 12283 | 12803 | 13131 | 13239 | 14164 | 14831 | 15226 | 15756 | 15956 | 16572 | 18190 | 18292 | 18831 | 18913 | 18369 | 19340 | 21137 | 20971 | 21312 | 20860
7107 | 7107 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 3 | 12167 | 12659 | 12991 | 13157 | 14176 | 14792 | 15213 | 15686 | 15859 | 16641 | 18182 | 18209 | 18728 | 18735 | 18274 | 19316 | 21006 | 20784 | 21060 | 20616
7108 | 7108 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 4 | 12266 | 12738 | 12920 | 13145 | 14324 | 14850 | 15237 | 15646 | 15650 | 16649 | 18011 | 17973 | 18425 | 18208 | 17895 | 19071 | 20584 | 20282 | 20486 | 19931
7109 | 7109 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 5 | 12813 | 13290 | 13126 | 13293 | 14752 | 15335 | 15610 | 16002 | 15678 | 16899 | 18163 | 18141 | 18372 | 17851 | 17617 | 19020 | 20401 | 19993 | 20217 | 19378
7110 | 7110 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 6 | 14137 | 14629 | 13725 | 13702 | 15939 | 16569 | 16683 | 17115 | 16087 | 17808 | 19110 | 19036 | 18982 | 17854 | 17546 | 19626 | 21000 | 20371 | 20608 | 19191
7111 | 7111 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 7 | 15723 | 16071 | 14483 | 14226 | 17476 | 18116 | 18089 | 18389 | 16531 | 19125 | 20238 | 20211 | 20009 | 18048 | 17626 | 20747 | 21777 | 21239 | 21300 | 19253
7112 | 7112 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 8 | 16200 | 16377 | 14867 | 14414 | 17945 | 18544 | 18514 | 18592 | 16768 | 19598 | 20349 | 20410 | 20260 | 18118 | 17590 | 21112 | 21757 | 21411 | 21278 | 19265
7113 | 7113 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 9 | 16173 | 16331 | 15123 | 14742 | 17893 | 18429 | 18476 | 18469 | 16948 | 19582 | 20188 | 20180 | 20043 | 18192 | 17725 | 20931 | 21527 | 21142 | 21042 | 19291
7114 | 7114 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 10 | 15983 | 16102 | 15116 | 14774 | 17696 | 18110 | 18297 | 18225 | 17103 | 19253 | 20108 | 19888 | 20101 | 18226 | 17777 | 20645 | 21700 | 21245 | 20888 | 19371
7115 | 7115 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 11 | 15980 | 15992 | 15276 | 14784 | 17683 | 17897 | 18182 | 18032 | 17510 | 18927 | 20003 | 19654 | 20251 | 18228 | 17649 | 20252 | 21926 | 21450 | 20778 | 19419
7116 | 7116 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 12 | 15995 | 16003 | 15367 | 14964 | 17701 | 17807 | 18071 | 17999 | 17665 | 18806 | 19820 | 19542 | 20138 | 18141 | 17599 | 20010 | 21756 | 21375 | 20780 | 19348
7117 | 7117 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 13 | 15983 | 15906 | 15236 | 14898 | 17732 | 17746 | 17905 | 17854 | 17585 | 18750 | 19712 | 19456 | 20031 | 17955 | 17455 | 19931 | 21706 | 21272 | 20622 | 19153
7118 | 7118 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 14 | 16078 | 15971 | 15221 | 14990 | 17766 | 17867 | 17980 | 17908 | 17502 | 18800 | 19704 | 19549 | 19996 | 17875 | 17552 | 19930 | 21581 | 21202 | 20618 | 19052
7119 | 7119 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 15 | 16214 | 16067 | 15365 | 15272 | 17868 | 18122 | 18131 | 17985 | 17375 | 19084 | 19801 | 19789 | 19821 | 17998 | 17920 | 20185 | 21352 | 21006 | 20629 | 19158
7120 | 7120 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 16 | 16566 | 16322 | 15673 | 15802 | 18074 | 18555 | 18398 | 18154 | 17316 | 19419 | 20381 | 20136 | 19670 | 18148 | 18454 | 20455 | 21618 | 20787 | 20620 | 19277
7121 | 7121 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 17 | 16908 | 16400 | 16057 | 16353 | 18563 | 18902 | 18746 | 18288 | 17545 | 19952 | 20780 | 20410 | 20020 | 18635 | 18981 | 21098 | 22030 | 21125 | 20781 | 19782
7122 | 7122 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 18 | 17125 | 16578 | 16263 | 16886 | 18840 | 18999 | 18958 | 18416 | 17753 | 20328 | 20801 | 20525 | 20615 | 19192 | 19736 | 21878 | 22447 | 21817 | 21289 | 20411
7123 | 7123 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 19 | 17379 | 16787 | 16244 | 17036 | 19006 | 19259 | 19310 | 18784 | 17991 | 20639 | 21299 | 21188 | 21253 | 19765 | 20345 | 22400 | 23230 | 22648 | 22213 | 21119
7124 | 7124 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 20 | 17090 | 16453 | 16008 | 16697 | 18769 | 19246 | 19260 | 18670 | 17987 | 20516 | 21469 | 21607 | 21754 | 20177 | 20612 | 22694 | 23661 | 23403 | 22705 | 21713
7125 | 7125 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 21 | 16508 | 15919 | 15591 | 16270 | 18215 | 18833 | 18961 | 18389 | 17878 | 20193 | 21515 | 21692 | 22004 | 20528 | 20822 | 22764 | 24128 | 23929 | 23213 | 22281
7126 | 7126 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 22 | 15430 | 14952 | 14919 | 15510 | 17291 | 17859 | 18115 | 17623 | 17434 | 19462 | 20881 | 21044 | 21490 | 20352 | 20457 | 22237 | 23725 | 23593 | 22936 | 22233
7127 | 7127 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 23 | 14278 | 13934 | 14216 | 14728 | 16332 | 16774 | 17152 | 16755 | 16863 | 18600 | 20013 | 20120 | 20741 | 19928 | 19890 | 21482 | 23006 | 22916 | 22329 | 21875
7128 | 7128 | 297 | 10 | 24 | Autumn | 10 | 23 | Autumn | 24 | 13471 | 13128 | 13627 | 14187 | 15653 | 16020 | 16464 | 16066 | 16436 | 18062 | 19345 | 19498 | 20187 | 19546 | 19528 | 20981 | 22410 | 22409 | 21827 | 21544
7129 | 7129 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 1 | 12910 | 13118 | 13493 | 14318 | 15522 | 15301 | 15943 | 16002 | 15945 | 18188 | 18980 | 18863 | 19735 | 18570 | 19517 | 21453 | 22134 | 21977 | 21452 | 20314
7130 | 7130 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 2 | 12662 | 12830 | 13240 | 14183 | 15292 | 15032 | 15578 | 15733 | 15737 | 17969 | 18756 | 18558 | 19259 | 18272 | 19307 | 21102 | 21817 | 21433 | 21027 | 19980
7131 | 7131 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 3 | 12552 | 12657 | 13120 | 14168 | 15260 | 14987 | 15485 | 15631 | 15710 | 17962 | 18732 | 18464 | 19082 | 18178 | 19280 | 20967 | 21656 | 21174 | 20771 | 19835
7132 | 7132 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 4 | 12639 | 12609 | 13108 | 14305 | 15303 | 15034 | 15484 | 15452 | 15589 | 17855 | 18518 | 18205 | 18713 | 17819 | 19049 | 20558 | 21150 | 20599 | 20073 | 19349
7133 | 7133 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 5 | 13148 | 12819 | 13279 | 14766 | 15818 | 15454 | 15901 | 15558 | 15611 | 18081 | 18659 | 18244 | 18719 | 17605 | 19055 | 20428 | 20903 | 20370 | 19552 | 18977
7134 | 7134 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 6 | 14411 | 13411 | 13706 | 15962 | 17087 | 16568 | 17090 | 16033 | 15822 | 19104 | 19603 | 18927 | 19354 | 17565 | 19683 | 21047 | 21494 | 20770 | 19363 | 18789
7135 | 7135 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 7 | 16036 | 14200 | 14264 | 17543 | 18516 | 18010 | 18426 | 16571 | 16247 | 20302 | 20871 | 20047 | 20238 | 17690 | 20843 | 21873 | 22540 | 21482 | 19442 | 18821
7136 | 7136 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 8 | 16541 | 14698 | 14557 | 18099 | 18905 | 18536 | 18748 | 16932 | 16483 | 20543 | 21223 | 20419 | 20399 | 17751 | 21304 | 21953 | 22732 | 21551 | 19540 | 18848
7137 | 7137 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 9 | 16643 | 15138 | 15059 | 18216 | 18946 | 18660 | 18788 | 17305 | 16871 | 20562 | 21038 | 20393 | 20365 | 18060 | 21298 | 21901 | 22393 | 21481 | 19732 | 19120
7138 | 7138 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 10 | 16817 | 15562 | 15534 | 18354 | 19141 | 18950 | 19032 | 17787 | 17208 | 20994 | 21169 | 20770 | 20497 | 18437 | 21339 | 22405 | 22567 | 21659 | 20142 | 19536
7139 | 7139 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 11 | 16704 | 15732 | 15607 | 18198 | 18956 | 18947 | 18971 | 17996 | 17045 | 21047 | 21099 | 20826 | 20246 | 18207 | 20859 | 22534 | 22662 | 21447 | 20090 | 19340
7140 | 7140 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 12 | 16557 | 15744 | 15710 | 18061 | 18731 | 18755 | 18853 | 17948 | 17068 | 20776 | 20946 | 20626 | 20124 | 18054 | 20514 | 22277 | 22671 | 21340 | 19912 | 19191
7141 | 7141 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 13 | 16369 | 15604 | 15643 | 18040 | 18623 | 18600 | 18725 | 17808 | 16929 | 20698 | 20832 | 20475 | 19927 | 17864 | 20388 | 22188 | 22584 | 21134 | 19671 | 18992
7142 | 7142 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 14 | 16296 | 15413 | 15550 | 17920 | 18518 | 18474 | 18576 | 17567 | 16868 | 20478 | 20724 | 20295 | 19803 | 17823 | 20248 | 21919 | 22460 | 20991 | 19428 | 18934
7143 | 7143 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 15 | 16408 | 15406 | 15660 | 18028 | 18619 | 18401 | 18401 | 17443 | 17122 | 20277 | 20656 | 20112 | 19812 | 18168 | 20479 | 21679 | 22360 | 20974 | 19508 | 19267
7144 | 7144 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 16 | 16768 | 15600 | 16063 | 18282 | 19180 | 18486 | 18362 | 17436 | 17622 | 20575 | 20782 | 19996 | 19896 | 18726 | 20773 | 21967 | 22421 | 20984 | 19642 | 19804
7145 | 7145 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 17 | 17045 | 15877 | 16512 | 18718 | 19432 | 18742 | 18393 | 17632 | 18090 | 20858 | 21008 | 20242 | 19952 | 19167 | 21331 | 22276 | 22671 | 21062 | 20064 | 20267
7146 | 7146 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 18 | 17083 | 16094 | 17040 | 19046 | 19554 | 19031 | 18580 | 17919 | 18562 | 20946 | 21159 | 20719 | 20299 | 19842 | 22034 | 22613 | 22715 | 21509 | 20629 | 21006
7147 | 7147 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 19 | 17313 | 16054 | 17151 | 19176 | 19790 | 19336 | 18888 | 18091 | 18752 | 21346 | 21488 | 21274 | 20990 | 20398 | 22510 | 23350 | 23346 | 22409 | 21327 | 21683
7148 | 7148 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 20 | 17126 | 15746 | 16756 | 18891 | 19590 | 19214 | 18692 | 17995 | 18624 | 21390 | 21697 | 21667 | 21212 | 20587 | 22736 | 23708 | 23941 | 22864 | 21885 | 22012
7149 | 7149 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 21 | 16615 | 15313 | 16326 | 18328 | 19257 | 18896 | 18363 | 17825 | 18410 | 21373 | 21676 | 21852 | 21425 | 20764 | 22785 | 24160 | 24356 | 23374 | 22468 | 22349
7150 | 7150 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 22 | 15558 | 14588 | 15509 | 17357 | 18307 | 17970 | 17511 | 17295 | 17788 | 20651 | 21020 | 21252 | 20942 | 20337 | 22206 | 23710 | 23979 | 23061 | 22388 | 22026
7151 | 7151 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 23 | 14464 | 13878 | 14698 | 16365 | 17231 | 16974 | 16602 | 16664 | 17090 | 19748 | 20025 | 20445 | 20218 | 19741 | 21426 | 22954 | 23118 | 22427 | 22016 | 21492
7152 | 7152 | 298 | 10 | 25 | Autumn | 10 | 24 | Autumn | 24 | 13603 | 13271 | 14117 | 15640 | 16422 | 16225 | 15845 | 16178 | 16659 | 19042 | 19410 | 19838 | 19641 | 19360 | 20887 | 22317 | 22577 | 21900 | 21673 | 21150
7153 | 7153 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 1 | 12777 | 12851 | 13934 | 15149 | 15603 | 15363 | 15471 | 15436 | 16441 | 18329 | 18619 | 19045 | 19059 | 19038 | 20990 | 21699 | 21869 | 21216 | 20124 | 20781
7154 | 7154 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 2 | 12443 | 12561 | 13788 | 14897 | 15373 | 14976 | 15181 | 15212 | 16308 | 18111 | 18345 | 18579 | 18682 | 18830 | 20642 | 21382 | 21504 | 20775 | 19774 | 20533
7155 | 7155 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 3 | 12305 | 12428 | 13771 | 14863 | 15370 | 14893 | 15093 | 15193 | 16372 | 18135 | 18232 | 18442 | 18525 | 18830 | 20536 | 21248 | 21242 | 20536 | 19643 | 20484
7156 | 7156 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 4 | 12393 | 12419 | 13915 | 14926 | 15409 | 14914 | 14944 | 15116 | 16432 | 17978 | 17981 | 18144 | 18042 | 18643 | 20173 | 20782 | 20699 | 19862 | 19174 | 20175
7157 | 7157 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 5 | 12985 | 12629 | 14411 | 15479 | 15843 | 15398 | 15135 | 15205 | 16755 | 18226 | 18054 | 18244 | 17784 | 18709 | 20103 | 20592 | 20442 | 19379 | 18828 | 20089
7158 | 7158 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 6 | 14336 | 13063 | 15616 | 16776 | 17068 | 16612 | 15662 | 15485 | 17727 | 19225 | 18663 | 18967 | 17840 | 19375 | 20764 | 21221 | 20748 | 19209 | 18646 | 20622
7159 | 7159 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 7 | 15814 | 13630 | 17239 | 18240 | 18673 | 17992 | 16276 | 15971 | 19096 | 20570 | 19766 | 19923 | 18103 | 20565 | 21624 | 22292 | 21525 | 19302 | 18680 | 21732
7160 | 7160 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 8 | 16228 | 13934 | 17799 | 18656 | 19225 | 18324 | 16646 | 16226 | 19691 | 20955 | 20074 | 20123 | 18278 | 21044 | 21731 | 22503 | 21659 | 19395 | 18697 | 22164
7161 | 7161 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 9 | 16417 | 14507 | 17993 | 18763 | 19201 | 18436 | 17094 | 16711 | 19917 | 20865 | 20057 | 20186 | 18605 | 21108 | 21740 | 22254 | 21579 | 19640 | 19022 | 22182
7162 | 7162 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 10 | 16678 | 14974 | 18114 | 19040 | 19333 | 18603 | 17482 | 17136 | 20178 | 20876 | 20122 | 20387 | 19043 | 21215 | 22313 | 22504 | 21896 | 20117 | 19509 | 22320
7163 | 7163 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 11 | 16670 | 15034 | 17898 | 18928 | 19298 | 18403 | 17549 | 17050 | 20099 | 20600 | 19967 | 20182 | 19029 | 20787 | 22497 | 22651 | 22186 | 20131 | 19383 | 21921
7164 | 7164 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 12 | 16609 | 15209 | 17807 | 18749 | 19203 | 18313 | 17527 | 17111 | 19926 | 20460 | 19773 | 20083 | 18864 | 20477 | 22272 | 22695 | 22156 | 19988 | 19271 | 21618
7165 | 7165 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 13 | 16523 | 15165 | 17797 | 18693 | 19107 | 18177 | 17375 | 17021 | 19919 | 20319 | 19636 | 19929 | 18652 | 20401 | 22234 | 22642 | 22079 | 19796 | 19121 | 21536
7166 | 7166 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 14 | 16429 | 15075 | 17729 | 18610 | 19055 | 18103 | 17215 | 16974 | 19763 | 20305 | 19470 | 19825 | 18446 | 20272 | 21979 | 22532 | 21814 | 19562 | 19071 | 21388
7167 | 7167 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 15 | 16278 | 15208 | 17888 | 18605 | 18981 | 18049 | 17227 | 17119 | 19651 | 20410 | 19404 | 19734 | 18437 | 20400 | 21629 | 22327 | 21422 | 19532 | 19293 | 21500
7168 | 7168 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 16 | 16295 | 15624 | 18191 | 19008 | 19158 | 18138 | 17360 | 17490 | 19599 | 20712 | 19465 | 19697 | 18482 | 20569 | 21790 | 22254 | 21087 | 19532 | 19695 | 21643
7169 | 7169 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 17 | 16227 | 16051 | 18603 | 19241 | 19437 | 18164 | 17542 | 17927 | 19971 | 20923 | 19670 | 19724 | 18832 | 21088 | 22058 | 22469 | 21120 | 19915 | 20118 | 22183
7170 | 7170 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 18 | 16349 | 16425 | 18751 | 19351 | 19561 | 18179 | 17616 | 18319 | 20390 | 20817 | 20156 | 19966 | 19256 | 21716 | 22323 | 22441 | 21806 | 20423 | 20799 | 22872
7171 | 7171 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 19 | 16519 | 16512 | 18876 | 19579 | 19552 | 18474 | 17765 | 18476 | 20624 | 21089 | 20436 | 20602 | 19755 | 22159 | 23030 | 23056 | 22460 | 21123 | 21479 | 23422
7172 | 7172 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 20 | 16118 | 16099 | 18561 | 19326 | 19388 | 18236 | 17616 | 18274 | 20394 | 21204 | 20588 | 20723 | 20060 | 22332 | 23346 | 23594 | 22978 | 21665 | 21799 | 23723
7173 | 7173 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 21 | 15567 | 15604 | 17943 | 18925 | 18919 | 17821 | 17347 | 17973 | 20012 | 21044 | 20578 | 20819 | 20339 | 22300 | 23708 | 23939 | 23423 | 22200 | 22107 | 23855
7174 | 7174 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 22 | 14587 | 14817 | 16977 | 17968 | 17986 | 16960 | 16798 | 17324 | 19229 | 20366 | 19997 | 20296 | 20118 | 21714 | 23253 | 23552 | 23107 | 22137 | 21807 | 23376
7175 | 7175 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 23 | 13521 | 13986 | 15930 | 16851 | 16801 | 15987 | 16101 | 16565 | 18302 | 19304 | 19196 | 19512 | 19625 | 20891 | 22443 | 22651 | 22413 | 21730 | 21234 | 22599
7176 | 7176 | 299 | 10 | 26 | Autumn | 10 | 25 | Autumn | 24 | 12717 | 13429 | 15221 | 16045 | 16054 | 15239 | 15622 | 16130 | 17736 | 18724 | 18672 | 18931 | 19242 | 20381 | 21831 | 22117 | 21945 | 21407 | 20923 | 22136
7177 | 7177 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 1 | 12373 | 13310 | 14757 | 15249 | 15212 | 14928 | 14990 | 15954 | 17500 | 17961 | 18121 | 18418 | 18063 | 20473 | 21238 | 21439 | 21419 | 19920 | 20598 | 22411
7178 | 7178 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 2 | 12092 | 13132 | 14504 | 15002 | 14945 | 14624 | 14753 | 15803 | 17273 | 17704 | 17772 | 18065 | 17770 | 20141 | 20936 | 21088 | 21003 | 19571 | 20351 | 22029
7179 | 7179 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 3 | 11962 | 13123 | 14476 | 15008 | 14859 | 14552 | 14752 | 15894 | 17312 | 17650 | 17623 | 17950 | 17723 | 20069 | 20833 | 20856 | 20688 | 19461 | 20321 | 21898
7180 | 7180 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 4 | 11939 | 13260 | 14549 | 15055 | 14874 | 14432 | 14704 | 15976 | 17251 | 17469 | 17345 | 17532 | 17419 | 19750 | 20408 | 20350 | 20109 | 19004 | 20019 | 21431
7181 | 7181 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 5 | 12177 | 13776 | 15110 | 15519 | 15273 | 14656 | 14829 | 16361 | 17573 | 17617 | 17391 | 17346 | 17272 | 19727 | 20261 | 20132 | 19778 | 18672 | 19938 | 21223
7182 | 7182 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 6 | 12754 | 14986 | 16414 | 16761 | 16264 | 15227 | 15166 | 17386 | 18644 | 18316 | 18092 | 17491 | 17283 | 20442 | 20935 | 20480 | 20112 | 18507 | 20478 | 21757
7183 | 7183 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 7 | 13576 | 16629 | 17928 | 18419 | 17611 | 15888 | 15718 | 18845 | 19932 | 19504 | 19307 | 17840 | 17464 | 21358 | 22068 | 21297 | 21069 | 18565 | 21602 | 22536
7184 | 7184 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 8 | 14057 | 17177 | 18354 | 18949 | 18010 | 16252 | 15974 | 19437 | 20197 | 19827 | 19750 | 18028 | 17523 | 21474 | 22282 | 21436 | 21386 | 18566 | 22016 | 22548
7185 | 7185 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 9 | 14430 | 17238 | 18335 | 18780 | 17972 | 16552 | 16326 | 19533 | 20162 | 19679 | 19819 | 18210 | 17766 | 21352 | 21911 | 21199 | 21317 | 18749 | 21893 | 22376
7186 | 7186 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 10 | 14397 | 16939 | 18168 | 18340 | 17569 | 16490 | 16302 | 19165 | 20016 | 19282 | 19672 | 18180 | 17749 | 21464 | 21705 | 21050 | 21413 | 18778 | 21577 | 22534
7187 | 7187 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 11 | 14415 | 16616 | 17936 | 17989 | 17333 | 16405 | 16054 | 18663 | 19768 | 18925 | 19363 | 18050 | 17473 | 21548 | 21754 | 21227 | 21619 | 18558 | 21087 | 22669
7188 | 7188 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 12 | 14383 | 16418 | 17631 | 17749 | 17091 | 16215 | 15937 | 18297 | 19444 | 18515 | 19128 | 17809 | 17281 | 21242 | 21706 | 21123 | 21701 | 18365 | 20705 | 22372
7189 | 7189 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 13 | 14273 | 16389 | 17572 | 17625 | 16994 | 16052 | 15834 | 18232 | 19361 | 18357 | 18972 | 17622 | 17156 | 21201 | 21651 | 21069 | 21668 | 18211 | 20618 | 22321
7190 | 7190 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 14 | 14049 | 16224 | 17400 | 17527 | 16781 | 15796 | 15688 | 18051 | 19157 | 18095 | 18720 | 17335 | 17046 | 20867 | 21461 | 20717 | 21337 | 18076 | 20385 | 21960
7191 | 7191 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 15 | 14070 | 16411 | 17422 | 17667 | 16782 | 15835 | 15864 | 18234 | 19156 | 18066 | 18696 | 17357 | 17312 | 20552 | 21289 | 20358 | 20990 | 18327 | 20526 | 21622
7192 | 7192 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 16 | 14559 | 17026 | 18071 | 18354 | 17264 | 16285 | 16549 | 18781 | 19911 | 18449 | 18981 | 17719 | 18038 | 21028 | 21529 | 20335 | 20867 | 19031 | 20972 | 22066
7193 | 7193 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 17 | 15180 | 17819 | 18713 | 19085 | 17861 | 16896 | 17412 | 19625 | 20564 | 19092 | 19625 | 18448 | 18814 | 21666 | 22118 | 20753 | 21373 | 19823 | 21881 | 22720
7194 | 7194 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 18 | 15395 | 18192 | 19115 | 19382 | 18403 | 17288 | 18103 | 20168 | 20562 | 19871 | 20223 | 18958 | 19537 | 22060 | 22220 | 21556 | 21947 | 20654 | 22719 | 23195
7195 | 7195 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 19 | 15365 | 18321 | 19347 | 19376 | 18500 | 17426 | 18240 | 20393 | 20931 | 20088 | 20621 | 19419 | 20062 | 22731 | 22800 | 22202 | 22572 | 21342 | 23285 | 24010
7196 | 7196 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 20 | 15049 | 18005 | 19083 | 19191 | 18239 | 17268 | 18024 | 20139 | 20922 | 20169 | 20693 | 19674 | 20216 | 23015 | 23300 | 22710 | 23101 | 21680 | 23607 | 24457
7197 | 7197 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 21 | 14571 | 17386 | 18673 | 18696 | 17816 | 16969 | 17698 | 19698 | 20799 | 20081 | 20790 | 19865 | 20319 | 23336 | 23620 | 23117 | 23650 | 22005 | 23756 | 24980
7198 | 7198 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 22 | 13853 | 16408 | 17682 | 17723 | 16934 | 16373 | 16999 | 18860 | 20047 | 19431 | 20239 | 19580 | 19872 | 22838 | 23197 | 22767 | 23372 | 21691 | 23264 | 24619
7199 | 7199 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 23 | 13127 | 15361 | 16560 | 16535 | 15968 | 15668 | 16229 | 17912 | 19087 | 18622 | 19504 | 19068 | 19244 | 22017 | 22287 | 22071 | 22769 | 21121 | 22497 | 23874
7200 | 7200 | 300 | 10 | 27 | Autumn | 10 | 26 | Autumn | 24 | 12550 | 14605 | 15716 | 15774 | 15265 | 15145 | 15751 | 17317 | 18388 | 18074 | 18882 | 18663 | 18877 | 21384 | 21724 | 21582 | 22233 | 20788 | 22020 | 23307
7201 | 7201 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 1 | 12247 | 14185 | 14982 | 14964 | 14690 | 14623 | 15625 | 17062 | 17735 | 17567 | 18866 | 17622 | 18653 | 20817 | 21081 | 21095 | 22410 | 20509 | 22331 | 22812
7202 | 7202 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 2 | 11971 | 13949 | 14747 | 14693 | 14408 | 14391 | 15484 | 16837 | 17528 | 17258 | 18561 | 17361 | 18468 | 20547 | 20760 | 20703 | 21966 | 20280 | 21967 | 22491
7203 | 7203 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 3 | 11841 | 13882 | 14730 | 14593 | 14270 | 14369 | 15559 | 16879 | 17576 | 17137 | 18451 | 17326 | 18486 | 20457 | 20536 | 20394 | 21711 | 20244 | 21828 | 22335
7204 | 7204 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 4 | 11835 | 13960 | 14784 | 14620 | 14263 | 14334 | 15664 | 16859 | 17474 | 16927 | 18135 | 17064 | 18339 | 20073 | 20066 | 19845 | 21062 | 19948 | 21363 | 21790
7205 | 7205 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 5 | 12030 | 14513 | 15236 | 15017 | 14627 | 14463 | 16066 | 17211 | 17764 | 17030 | 17914 | 16951 | 18429 | 19956 | 19872 | 19529 | 20447 | 19861 | 21144 | 21476
7206 | 7206 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 6 | 12461 | 15820 | 16468 | 16038 | 15761 | 14821 | 17137 | 18340 | 18825 | 17813 | 18002 | 17027 | 19136 | 20677 | 20259 | 19897 | 20074 | 20405 | 21678 | 21999
7207 | 7207 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 7 | 13020 | 17351 | 18100 | 17386 | 17319 | 15371 | 18619 | 19677 | 20225 | 19076 | 18361 | 17243 | 20359 | 21827 | 21083 | 20858 | 20062 | 21510 | 22437 | 22990
7208 | 7208 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 8 | 13305 | 17802 | 18622 | 17771 | 17844 | 15625 | 19220 | 19979 | 20613 | 19547 | 18464 | 17315 | 20833 | 22058 | 21228 | 21187 | 20059 | 21916 | 22445 | 23107
7209 | 7209 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 9 | 13665 | 17707 | 18381 | 17641 | 17861 | 15897 | 19247 | 19887 | 20326 | 19554 | 18667 | 17488 | 20694 | 21624 | 20921 | 21038 | 20204 | 21718 | 22203 | 22597
7210 | 7210 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 10 | 13927 | 17780 | 18201 | 17502 | 17933 | 16117 | 19122 | 19991 | 20132 | 19635 | 18831 | 17717 | 20586 | 21660 | 21010 | 21381 | 20426 | 21643 | 22599 | 22669
7211 | 7211 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 11 | 13857 | 17568 | 17885 | 17249 | 17669 | 15898 | 18646 | 19687 | 19661 | 19328 | 18602 | 17436 | 20053 | 21684 | 21159 | 21582 | 20232 | 21129 | 22708 | 22734
7212 | 7212 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 12 | 14018 | 17371 | 17752 | 17019 | 17597 | 15875 | 18367 | 19320 | 19419 | 19149 | 18378 | 17336 | 19764 | 21730 | 21151 | 21754 | 20060 | 20845 | 22512 | 22801
7213 | 7213 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 13 | 13995 | 17338 | 17662 | 16918 | 17502 | 15797 | 18325 | 19222 | 19295 | 19005 | 18257 | 17224 | 19716 | 21707 | 21129 | 21733 | 19943 | 20790 | 22493 | 22773
7214 | 7214 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 14 | 13972 | 17378 | 17783 | 16912 | 17466 | 15882 | 18381 | 19239 | 19364 | 19004 | 18212 | 17302 | 19685 | 21711 | 20971 | 21588 | 19790 | 20746 | 22320 | 22761
7215 | 7215 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 15 | 14204 | 17531 | 18051 | 17063 | 17553 | 16220 | 18736 | 19420 | 19577 | 19178 | 18355 | 17657 | 19921 | 21624 | 20700 | 21327 | 19782 | 20971 | 22070 | 22661
7216 | 7216 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 16 | 14767 | 18030 | 18638 | 17473 | 17800 | 16837 | 19226 | 20094 | 20038 | 19434 | 18601 | 18240 | 20241 | 21710 | 20526 | 21061 | 19833 | 21253 | 22351 | 22710
7217 | 7217 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 17 | 15340 | 18393 | 19088 | 17827 | 18171 | 17405 | 19765 | 20502 | 20437 | 19759 | 19026 | 18762 | 20874 | 22052 | 20699 | 21316 | 20356 | 21916 | 22761 | 23075
7218 | 7218 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 18 | 15810 | 18603 | 19210 | 18276 | 18422 | 17843 | 20014 | 20423 | 20545 | 19996 | 19493 | 19336 | 21507 | 22011 | 21363 | 21766 | 21328 | 22636 | 23111 | 23127
7219 | 7219 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 19 | 15911 | 18811 | 19181 | 18336 | 18549 | 17948 | 20199 | 20737 | 20783 | 20302 | 19894 | 19797 | 21934 | 22531 | 21956 | 22356 | 22111 | 23186 | 23908 | 23812
7220 | 7220 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 20 | 15480 | 18519 | 18943 | 18017 | 18310 | 17685 | 19884 | 20636 | 20811 | 20255 | 19935 | 19862 | 22054 | 22950 | 22393 | 22824 | 22480 | 23482 | 24325 | 24416
7221 | 7221 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 21 | 14994 | 18065 | 18406 | 17554 | 17962 | 17322 | 19395 | 20442 | 20591 | 20247 | 20062 | 19892 | 21989 | 23191 | 22742 | 23323 | 23103 | 23622 | 24845 | 24888
7222 | 7222 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 22 | 14169 | 17053 | 17411 | 16648 | 17085 | 16591 | 18518 | 19632 | 19820 | 19635 | 19822 | 19409 | 21337 | 22729 | 22360 | 23025 | 23124 | 23124 | 24481 | 24576
7223 | 7223 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 23 | 13376 | 15953 | 16233 | 15700 | 16177 | 15834 | 17577 | 18667 | 18760 | 18904 | 19414 | 18781 | 20528 | 21837 | 21679 | 22435 | 22853 | 22383 | 23768 | 23744
7224 | 7224 | 301 | 10 | 28 | Autumn | 10 | 27 | Autumn | 24 | 12804 | 15119 | 15457 | 14992 | 15358 | 15344 | 16970 | 17948 | 18138 | 18289 | 19115 | 18400 | 19994 | 21264 | 21180 | 21879 | 22634 | 21897 | 23191 | 23244
7225 | 7225 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 1 | 12458 | 14088 | 14387 | 14119 | 14833 | 14927 | 16353 | 16961 | 17110 | 17933 | 17410 | 17900 | 19790 | 20315 | 20400 | 21744 | 20387 | 21894 | 22399 | 22361
7226 | 7226 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 2 | 12298 | 13841 | 14104 | 13823 | 14544 | 14763 | 16111 | 16745 | 16870 | 17635 | 17143 | 17724 | 19481 | 19997 | 20008 | 21299 | 20032 | 21517 | 22065 | 21988
7227 | 7227 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 3 | 12278 | 13773 | 13968 | 13662 | 14442 | 14804 | 16128 | 16784 | 16812 | 17543 | 17039 | 17756 | 19409 | 19780 | 19704 | 21051 | 19815 | 21370 | 21901 | 21707
7228 | 7228 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 4 | 12413 | 13842 | 14010 | 13673 | 14413 | 14924 | 16141 | 16731 | 16690 | 17299 | 16720 | 17655 | 19134 | 19360 | 19198 | 20438 | 19222 | 20920 | 21366 | 21119
7229 | 7229 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 5 | 12930 | 14335 | 14436 | 14073 | 14617 | 15366 | 16554 | 17090 | 16897 | 17174 | 16511 | 17813 | 19160 | 19234 | 18943 | 19875 | 18642 | 20733 | 21076 | 20795
7230 | 7230 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 6 | 14163 | 15594 | 15515 | 15273 | 15165 | 16495 | 17770 | 18245 | 17695 | 17379 | 16525 | 18615 | 19955 | 19701 | 19387 | 19571 | 18314 | 21314 | 21636 | 21071
7231 | 7231 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 7 | 15808 | 17242 | 16924 | 16878 | 15828 | 18020 | 19193 | 19713 | 18944 | 17829 | 16744 | 19909 | 20921 | 20586 | 20405 | 19600 | 18322 | 22109 | 22656 | 21849
7232 | 7232 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 8 | 16356 | 17758 | 17312 | 17405 | 16104 | 18615 | 19529 | 20127 | 19303 | 17985 | 16863 | 20404 | 21081 | 20741 | 20750 | 19622 | 18346 | 22126 | 22783 | 21933
7233 | 7233 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 9 | 16563 | 17755 | 17405 | 17632 | 16605 | 18847 | 19657 | 20072 | 19314 | 18432 | 17123 | 20497 | 21126 | 20658 | 20821 | 19989 | 18528 | 22099 | 22492 | 21811
7234 | 7234 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 10 | 16777 | 17859 | 17550 | 17978 | 17016 | 18994 | 20023 | 20149 | 19411 | 18852 | 17417 | 20652 | 21724 | 21007 | 21423 | 20469 | 18822 | 22756 | 22828 | 22196
7235 | 7235 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 11 | 16592 | 17701 | 17465 | 17887 | 17017 | 18670 | 19853 | 19845 | 19213 | 18737 | 17341 | 20254 | 21916 | 21294 | 21766 | 20412 | 18854 | 23007 | 23040 | 22540
7236 | 7236 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 12 | 16460 | 17581 | 17257 | 17809 | 16870 | 18421 | 19513 | 19593 | 18844 | 18521 | 17198 | 19934 | 21678 | 21256 | 21908 | 20210 | 18882 | 22784 | 23075 | 22526
7237 | 7237 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 13 | 16409 | 17486 | 17144 | 17681 | 16759 | 18362 | 19400 | 19432 | 18666 | 18377 | 17033 | 19845 | 21631 | 21195 | 21845 | 20051 | 18699 | 22724 | 23006 | 22466
7238 | 7238 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 14 | 16291 | 17399 | 16936 | 17481 | 16574 | 18201 | 19199 | 19338 | 18492 | 18108 | 16844 | 19653 | 21328 | 20869 | 21530 | 19735 | 18717 | 22378 | 22819 | 22116
7239 | 7239 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 15 | 16467 | 17483 | 16884 | 17436 | 16565 | 18331 | 19149 | 19420 | 18521 | 18010 | 16833 | 19764 | 20966 | 20469 | 21135 | 19599 | 18558 | 21990 | 22579 | 21685
7240 | 7240 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 16 | 16862 | 17878 | 17118 | 17577 | 16761 | 18623 | 19582 | 19776 | 18758 | 18040 | 17079 | 19979 | 21167 | 20196 | 20765 | 19539 | 18724 | 22156 | 22519 | 21354
7241 | 7241 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 17 | 17242 | 18214 | 17366 | 17816 | 16967 | 19083 | 19916 | 20047 | 18956 | 18388 | 17527 | 20478 | 21426 | 20232 | 20882 | 19931 | 19223 | 22428 | 22746 | 21398
7242 | 7242 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 18 | 17357 | 18404 | 17841 | 18007 | 17384 | 19450 | 19971 | 20115 | 19369 | 18940 | 18259 | 21018 | 21635 | 20826 | 21271 | 20839 | 19906 | 22729 | 22753 | 22084
7243 | 7243 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 19 | 17453 | 18356 | 17862 | 18069 | 17451 | 19611 | 20246 | 20269 | 19484 | 19242 | 18596 | 21359 | 22219 | 21358 | 21812 | 21546 | 20518 | 23517 | 23415 | 22762
7244 | 7244 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 20 | 17127 | 18118 | 17527 | 17827 | 17136 | 19306 | 20125 | 20260 | 19482 | 19224 | 18765 | 21451 | 22446 | 21761 | 22263 | 21920 | 21019 | 23959 | 24045 | 23330
7245 | 7245 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 21 | 16441 | 17497 | 16998 | 17389 | 16721 | 18742 | 19830 | 19912 | 19259 | 19196 | 18859 | 21268 | 22645 | 22012 | 22666 | 22447 | 21505 | 24429 | 24466 | 23794
7246 | 7246 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 22 | 15488 | 16493 | 16072 | 16518 | 16177 | 17841 | 18978 | 19118 | 18581 | 18900 | 18495 | 20606 | 22134 | 21594 | 22336 | 22472 | 21405 | 24050 | 24152 | 23519
7247 | 7247 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 23 | 14489 | 15350 | 15122 | 15628 | 15582 | 16903 | 18004 | 18051 | 17792 | 18481 | 17919 | 19805 | 21346 | 20913 | 21747 | 22220 | 21070 | 23345 | 23342 | 22912
7248 | 7248 | 302 | 10 | 29 | Autumn | 10 | 28 | Autumn | 24 | 13720 | 14544 | 14374 | 14795 | 15114 | 16257 | 17238 | 17396 | 17231 | 18154 | 17531 | 19262 | 20696 | 20406 | 21178 | 21993 | 20656 | 22759 | 22838 | 22469
7249 | 7249 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 1 | 13273 | 13739 | 13777 | 14524 | 14224 | 15873 | 16503 | 16610 | 16675 | 16856 | 17334 | 19257 | 20081 | 19890 | 21282 | 20062 | 20334 | 22223 | 22213 | 21969
7250 | 7250 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 2 | 13044 | 13458 | 13498 | 14229 | 13979 | 15638 | 16298 | 16383 | 16366 | 16629 | 17125 | 18962 | 19815 | 19516 | 20852 | 19712 | 20040 | 21891 | 21845 | 21539
7251 | 7251 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 3 | 13001 | 13339 | 13348 | 14121 | 13915 | 15656 | 16344 | 16328 | 16277 | 16563 | 17163 | 18943 | 19771 | 19265 | 20654 | 19538 | 19961 | 21763 | 21593 | 21220
7252 | 7252 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 4 | 13095 | 13413 | 13395 | 14130 | 13836 | 15716 | 16353 | 16283 | 16138 | 16334 | 17045 | 18736 | 19451 | 18819 | 20096 | 18986 | 19575 | 21252 | 21024 | 20600
7253 | 7253 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 5 | 13670 | 13839 | 13801 | 14346 | 13876 | 16148 | 16747 | 16535 | 16321 | 16174 | 17248 | 18822 | 19403 | 18614 | 19579 | 18436 | 19516 | 20976 | 20704 | 20192
7254 | 7254 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 6 | 14991 | 14926 | 15016 | 14908 | 14162 | 17391 | 17949 | 17403 | 17196 | 16251 | 18091 | 19654 | 20196 | 19085 | 19298 | 18108 | 20113 | 21528 | 20958 | 20466
7255 | 7255 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 7 | 16550 | 16337 | 16652 | 15578 | 14705 | 18837 | 19448 | 18694 | 18527 | 16512 | 19460 | 20676 | 21403 | 20133 | 19357 | 18128 | 21194 | 22559 | 21723 | 21396
7256 | 7256 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 8 | 17009 | 16754 | 17223 | 15864 | 14997 | 19227 | 19919 | 19090 | 19025 | 16700 | 20145 | 20884 | 21665 | 20522 | 19422 | 18166 | 21684 | 22722 | 21831 | 21701
7257 | 7257 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 9 | 16983 | 16691 | 17326 | 16222 | 15182 | 19209 | 19736 | 18962 | 19117 | 16846 | 20197 | 20817 | 21333 | 20475 | 19674 | 18219 | 21629 | 22313 | 21576 | 21606
7258 | 7258 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 10 | 17141 | 16739 | 17589 | 16582 | 15283 | 19514 | 19770 | 19057 | 19287 | 17128 | 20285 | 21225 | 21448 | 20878 | 19958 | 18330 | 21768 | 22452 | 21773 | 22048
7259 | 7259 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 11 | 16956 | 16714 | 17606 | 16714 | 15184 | 19517 | 19667 | 19076 | 19002 | 17298 | 20207 | 21305 | 21503 | 21102 | 19787 | 18256 | 21839 | 22548 | 22006 | 22333
7260 | 7260 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 12 | 16688 | 16523 | 17553 | 16640 | 15051 | 19235 | 19479 | 18822 | 18769 | 17226 | 20004 | 20994 | 21447 | 21165 | 19508 | 18213 | 21777 | 22507 | 21913 | 22432
7261 | 7261 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 13 | 16423 | 16270 | 17290 | 16413 | 14719 | 19010 | 19209 | 18556 | 18408 | 16963 | 19777 | 20757 | 21183 | 20914 | 19163 | 17838 | 21537 | 22250 | 21664 | 22179
7262 | 7262 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 14 | 16292 | 16100 | 17109 | 16191 | 14581 | 18817 | 19111 | 18314 | 18206 | 16762 | 19683 | 20496 | 21039 | 20649 | 18898 | 17892 | 21403 | 22107 | 21363 | 21893
7263 | 7263 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 15 | 16480 | 16134 | 17134 | 16155 | 14797 | 18775 | 19176 | 18201 | 18353 | 16684 | 19676 | 20349 | 21034 | 20470 | 18975 | 17944 | 21368 | 22080 | 21141 | 21687
7264 | 7264 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 16 | 16969 | 16411 | 17303 | 16278 | 15296 | 19160 | 19472 | 18252 | 18569 | 16811 | 19875 | 20703 | 21188 | 20283 | 19092 | 18282 | 21503 | 22188 | 20980 | 21442
7265 | 7265 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 17 | 17446 | 16832 | 17702 | 16687 | 16004 | 19651 | 19885 | 18644 | 19046 | 17373 | 20399 | 21182 | 21612 | 20622 | 19705 | 18999 | 21916 | 22637 | 21248 | 21794
7266 | 7266 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 18 | 17795 | 17374 | 17937 | 17292 | 16701 | 19811 | 20038 | 19269 | 19496 | 18122 | 21109 | 21461 | 21593 | 21087 | 20689 | 19761 | 22636 | 22729 | 22031 | 22343
7267 | 7267 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 19 | 17995 | 17382 | 17961 | 17329 | 16717 | 20050 | 20142 | 19333 | 19729 | 18370 | 21298 | 21996 | 22046 | 21574 | 21348 | 20356 | 23186 | 23384 | 22707 | 22981
7268 | 7268 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 20 | 17702 | 16995 | 17657 | 16955 | 16553 | 19866 | 20052 | 19238 | 19616 | 18429 | 21404 | 22130 | 22419 | 21944 | 21646 | 20803 | 23620 | 23979 | 23255 | 23520
7269 | 7269 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 21 | 17193 | 16458 | 17192 | 16517 | 16264 | 19533 | 19655 | 18947 | 19486 | 18440 | 21417 | 22263 | 22562 | 22279 | 22117 | 21266 | 24030 | 24397 | 23713 | 24092
7270 | 7270 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 22 | 16186 | 15518 | 16305 | 15933 | 15630 | 18649 | 18816 | 18202 | 18838 | 18038 | 20736 | 21682 | 22070 | 21918 | 22114 | 21125 | 23591 | 24074 | 23440 | 23871
7271 | 7271 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 23 | 15057 | 14508 | 15344 | 15273 | 14861 | 17600 | 17670 | 17321 | 18049 | 17387 | 19837 | 20813 | 21127 | 21260 | 21793 | 20726 | 22786 | 23206 | 22790 | 23290
7272 | 7272 | 303 | 10 | 30 | Autumn | 10 | 29 | Autumn | 24 | 14230 | 13774 | 14498 | 14796 | 14332 | 16815 | 16991 | 16721 | 17404 | 17000 | 19189 | 20167 | 20557 | 20692 | 21564 | 20324 | 22204 | 22702 | 22358 | 22802
7273 | 7273 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 1 | 13687 | 13386 | 14368 | 14151 | 14377 | 16230 | 16354 | 16350 | 17472 | 17006 | 19344 | 19710 | 20035 | 20951 | 19879 | 20199 | 22697 | 22248 | 22038 | 23162
7274 | 7274 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 2 | 13461 | 13104 | 14088 | 13916 | 14179 | 16035 | 16140 | 16078 | 17213 | 16844 | 19076 | 19474 | 19748 | 20553 | 19551 | 19931 | 22320 | 21892 | 21620 | 22702
7275 | 7275 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 3 | 13382 | 12914 | 13937 | 13788 | 14182 | 16035 | 16047 | 15923 | 17119 | 16865 | 19005 | 19423 | 19561 | 20352 | 19374 | 19826 | 22143 | 21622 | 21274 | 22429
7276 | 7276 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 4 | 13465 | 12968 | 13944 | 13717 | 14264 | 16054 | 16025 | 15840 | 16954 | 16790 | 18796 | 19149 | 19195 | 19831 | 18843 | 19456 | 21605 | 21053 | 20649 | 21724
7277 | 7277 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 5 | 13955 | 13373 | 14173 | 13761 | 14758 | 16483 | 16324 | 16069 | 16880 | 17057 | 18824 | 19164 | 19120 | 19368 | 18327 | 19425 | 21278 | 20745 | 20245 | 21037
7278 | 7278 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 6 | 15165 | 14592 | 14758 | 14067 | 15910 | 17725 | 17256 | 17029 | 17138 | 17972 | 19574 | 20015 | 19605 | 19145 | 18034 | 20038 | 21619 | 21014 | 20520 | 20600
7279 | 7279 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 7 | 16799 | 16253 | 15456 | 14629 | 17502 | 19264 | 18599 | 18430 | 17626 | 19407 | 20698 | 21285 | 20518 | 19247 | 18077 | 21147 | 22471 | 21782 | 21442 | 20546
7280 | 7280 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 8 | 17341 | 16837 | 15760 | 14972 | 18241 | 19753 | 19019 | 18989 | 17858 | 20109 | 20998 | 21604 | 20728 | 19334 | 18145 | 21662 | 22559 | 21896 | 21746 | 20569
7281 | 7281 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 9 | 17145 | 16874 | 16066 | 15096 | 18322 | 19506 | 18835 | 19032 | 18111 | 20119 | 20889 | 21238 | 20450 | 19533 | 18141 | 21558 | 22297 | 21578 | 21591 | 20722
7282 | 7282 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 10 | 16841 | 16844 | 16148 | 15011 | 18061 | 19237 | 18632 | 19069 | 18223 | 19919 | 20850 | 21046 | 20310 | 19524 | 17955 | 21402 | 22142 | 21483 | 21748 | 20751
7283 | 7283 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 11 | 16556 | 16738 | 16172 | 15047 | 17801 | 19020 | 18541 | 19030 | 18196 | 19753 | 20834 | 20904 | 20319 | 19171 | 17702 | 21288 | 21873 | 21532 | 21859 | 20439
7284 | 7284 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 12 | 16319 | 16635 | 16070 | 14991 | 17546 | 18828 | 18288 | 18949 | 17950 | 19571 | 20600 | 20732 | 20092 | 18780 | 17546 | 21116 | 21510 | 21330 | 21835 | 20061
7285 | 7285 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 13 | 16290 | 16599 | 16073 | 14958 | 17552 | 18790 | 18256 | 18921 | 17917 | 19584 | 20505 | 20700 | 20049 | 18658 | 17392 | 21111 | 21295 | 21300 | 21806 | 19927
7286 | 7286 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 14 | 16399 | 16648 | 16029 | 14980 | 17697 | 18876 | 18200 | 18873 | 17822 | 19679 | 20409 | 20748 | 19958 | 18564 | 17614 | 21167 | 21222 | 21164 | 21687 | 19806
7287 | 7287 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 15 | 16621 | 16712 | 16034 | 15050 | 17844 | 18984 | 18132 | 18794 | 17709 | 19697 | 20363 | 20765 | 19809 | 18669 | 17692 | 21150 | 21424 | 20967 | 21508 | 19890
7288 | 7288 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 16 | 17262 | 17124 | 16406 | 15587 | 18440 | 19526 | 18433 | 18975 | 17845 | 20119 | 20931 | 21141 | 19926 | 19010 | 18248 | 21497 | 22253 | 21022 | 21479 | 20194
7289 | 7289 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 17 | 17824 | 17522 | 16827 | 16240 | 19014 | 19946 | 18821 | 19345 | 18365 | 20609 | 21493 | 21613 | 20232 | 19668 | 19011 | 21955 | 22949 | 21338 | 21879 | 20874
7290 | 7290 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 18 | 18099 | 17655 | 17284 | 16780 | 19597 | 19963 | 19251 | 19545 | 18941 | 21057 | 21698 | 21556 | 20878 | 20609 | 19736 | 22645 | 23353 | 22102 | 22417 | 21917
7291 | 7291 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 19 | 18053 | 17668 | 17303 | 16766 | 19665 | 20051 | 19286 | 19713 | 19178 | 21189 | 21985 | 21958 | 21369 | 21227 | 20302 | 23183 | 23922 | 22785 | 23055 | 22687
7292 | 7292 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 20 | 17744 | 17294 | 16881 | 16561 | 19349 | 19910 | 19131 | 19500 | 19028 | 21192 | 22160 | 22237 | 21668 | 21452 | 20707 | 23557 | 24570 | 23317 | 23573 | 23105
7293 | 7293 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 21 | 17138 | 16834 | 16438 | 16262 | 19003 | 19495 | 18806 | 19323 | 18934 | 21150 | 22335 | 22318 | 21869 | 21877 | 21151 | 23956 | 25209 | 23797 | 24177 | 23785
7294 | 7294 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 22 | 16096 | 15897 | 15808 | 15578 | 18021 | 18592 | 17996 | 18594 | 18551 | 20410 | 21786 | 21741 | 21385 | 21807 | 20954 | 23463 | 24938 | 23491 | 23929 | 23870
7295 | 7295 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 23 | 14924 | 14925 | 15140 | 14805 | 16968 | 17434 | 17094 | 17769 | 18056 | 19494 | 20945 | 20779 | 20644 | 21481 | 20558 | 22658 | 24250 | 22848 | 23364 | 23629
7296 | 7296 | 304 | 10 | 31 | Autumn | 10 | 30 | Autumn | 24 | 14107 | 14057 | 14612 | 14228 | 16164 | 16710 | 16446 | 17064 | 17694 | 18829 | 20317 | 20173 | 20120 | 21217 | 20118 | 22052 | 23715 | 22375 | 22842 | 23422
7297 | 7297 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 1 | 13199 | 13593 | 13664 | 13933 | 15566 | 15699 | 15710 | 16736 | 16329 | 18560 | 19427 | 19283 | 19429 | 19268 | 19658 | 22143 | 22974 | 21689 | 22842 | 21166
7298 | 7298 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 2 | 12933 | 13301 | 13426 | 13723 | 15332 | 15472 | 15430 | 16481 | 16119 | 18313 | 19082 | 19011 | 19081 | 18947 | 19398 | 21773 | 22468 | 21271 | 22387 | 20802
7299 | 7299 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 3 | 12777 | 13123 | 13280 | 13694 | 15269 | 15361 | 15269 | 16368 | 16018 | 18265 | 18969 | 18842 | 18818 | 18781 | 19300 | 21612 | 22248 | 20933 | 22112 | 20578
7300 | 7300 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 4 | 12864 | 13143 | 13237 | 13802 | 15337 | 15383 | 15243 | 16274 | 15841 | 18142 | 18643 | 18554 | 18433 | 18312 | 18983 | 21125 | 21574 | 20342 | 21441 | 19963
7301 | 7301 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 5 | 13303 | 13413 | 13325 | 14346 | 15726 | 15751 | 15557 | 16303 | 15746 | 18279 | 18487 | 18584 | 18294 | 17875 | 19022 | 20867 | 21020 | 19987 | 20796 | 19341
7302 | 7302 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 6 | 14411 | 14000 | 13635 | 15526 | 16906 | 16702 | 16567 | 16650 | 15890 | 19091 | 18914 | 19152 | 18834 | 17613 | 19655 | 21246 | 21009 | 20263 | 20342 | 18902
7303 | 7303 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 7 | 15852 | 14705 | 14227 | 17147 | 18481 | 18070 | 18023 | 17225 | 16212 | 20290 | 19843 | 20141 | 19942 | 17692 | 20797 | 22135 | 21583 | 21198 | 20291 | 18857
7304 | 7304 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 8 | 16248 | 15023 | 14582 | 17857 | 18934 | 18474 | 18589 | 17481 | 16436 | 20619 | 20520 | 20356 | 20328 | 17770 | 21309 | 22231 | 22101 | 21502 | 20307 | 18890
7305 | 7305 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 9 | 16330 | 15548 | 14930 | 18147 | 19047 | 18505 | 18851 | 17971 | 16749 | 20745 | 20600 | 20311 | 20443 | 17983 | 21423 | 22190 | 22127 | 21554 | 20667 | 19070
7306 | 7306 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 10 | 16357 | 15904 | 15110 | 18154 | 19146 | 18548 | 19138 | 18343 | 17004 | 20954 | 20763 | 20428 | 20831 | 18049 | 21523 | 22298 | 22180 | 21972 | 20960 | 19180
7307 | 7307 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 11 | 16461 | 16232 | 15426 | 18235 | 19273 | 18729 | 19375 | 18679 | 17368 | 21217 | 20881 | 20692 | 21140 | 18069 | 21690 | 22289 | 21878 | 22348 | 20927 | 19244
7308 | 7308 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 12 | 16473 | 16395 | 15617 | 18317 | 19289 | 18717 | 19529 | 18800 | 17568 | 21223 | 20924 | 20703 | 21339 | 18154 | 21760 | 22166 | 21667 | 22560 | 20786 | 19337
7309 | 7309 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 13 | 16195 | 16125 | 15310 | 18079 | 18950 | 18409 | 19227 | 18522 | 17284 | 20855 | 20776 | 20401 | 21055 | 17728 | 21484 | 21692 | 21415 | 22256 | 20380 | 18903
7310 | 7310 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 14 | 15913 | 15780 | 15049 | 17938 | 18654 | 18072 | 18898 | 18148 | 16980 | 20482 | 20653 | 20012 | 20675 | 17667 | 21256 | 21321 | 21294 | 21852 | 19972 | 18821
7311 | 7311 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 15 | 15812 | 15646 | 14988 | 17945 | 18590 | 17887 | 18692 | 17891 | 16776 | 20296 | 20539 | 19710 | 20360 | 17601 | 21094 | 21364 | 21413 | 21524 | 19909 | 18739
7312 | 7312 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 16 | 16109 | 15831 | 15364 | 18388 | 19037 | 18041 | 18719 | 17877 | 16941 | 20671 | 20534 | 19660 | 20203 | 17975 | 21257 | 22010 | 21626 | 21306 | 20019 | 19086
7313 | 7313 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 17 | 16477 | 16168 | 15930 | 18841 | 19577 | 18366 | 19015 | 18250 | 17411 | 21143 | 21049 | 19880 | 20515 | 18651 | 21623 | 22609 | 22361 | 21623 | 20615 | 19787
7314 | 7314 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 18 | 16840 | 16550 | 16393 | 19244 | 19723 | 18759 | 19148 | 18556 | 17876 | 21244 | 21352 | 20412 | 20876 | 19292 | 22229 | 22939 | 23166 | 22084 | 21584 | 20504
7315 | 7315 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 19 | 16847 | 16559 | 16366 | 19285 | 19732 | 18777 | 19285 | 18730 | 18070 | 21456 | 21666 | 20837 | 21309 | 19822 | 22739 | 23473 | 23851 | 22733 | 22360 | 21159
7316 | 7316 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 20 | 16424 | 16129 | 16133 | 18949 | 19580 | 18587 | 19025 | 18515 | 18062 | 21539 | 21971 | 21070 | 21601 | 20181 | 23080 | 24098 | 24509 | 23253 | 22778 | 21665
7317 | 7317 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 21 | 15914 | 15654 | 15805 | 18579 | 19277 | 18220 | 18776 | 18339 | 18025 | 21612 | 22188 | 21198 | 21903 | 20566 | 23432 | 24693 | 25244 | 23834 | 23452 | 22250
7318 | 7318 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 22 | 14941 | 15013 | 15097 | 17594 | 18387 | 17372 | 18004 | 17913 | 17557 | 21009 | 21891 | 20669 | 21481 | 20337 | 22920 | 24417 | 25259 | 23583 | 23538 | 22154
7319 | 7319 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 23 | 13922 | 14327 | 14283 | 16511 | 17316 | 16424 | 17123 | 17355 | 16864 | 20114 | 21169 | 19885 | 20794 | 19901 | 22077 | 23693 | 24703 | 22995 | 23276 | 21790
7320 | 7320 | 305 | 11 | 1 | Winter | 10 | 31 | Autumn | 24 | 13199 | 13813 | 13717 | 15731 | 16534 | 15782 | 16414 | 16976 | 16458 | 19510 | 20421 | 19377 | 20226 | 19485 | 21485 | 23170 | 24054 | 22489 | 23100 | 21423
7321 | 7321 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 1 | 12595 | 13047 | 13565 | 15234 | 15635 | 15174 | 16183 | 15836 | 16259 | 18735 | 19517 | 18810 | 20231 | 19171 | 21687 | 22547 | 23133 | 22620 | 21018 | 21061
7322 | 7322 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 2 | 12328 | 12805 | 13359 | 15003 | 15318 | 14896 | 15932 | 15631 | 16103 | 18425 | 19206 | 18493 | 19854 | 18928 | 21344 | 22065 | 22691 | 22173 | 20656 | 20774
7323 | 7323 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 3 | 12178 | 12657 | 13339 | 14941 | 15248 | 14745 | 15834 | 15551 | 16153 | 18360 | 19100 | 18278 | 19692 | 18870 | 21202 | 21881 | 22491 | 21911 | 20449 | 20660
7324 | 7324 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 4 | 12254 | 12615 | 13448 | 15016 | 15190 | 14738 | 15774 | 15410 | 16138 | 18098 | 18761 | 17950 | 19243 | 18586 | 20748 | 21241 | 21795 | 21246 | 19828 | 20231
7325 | 7325 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 5 | 12689 | 12674 | 13966 | 15417 | 15431 | 15053 | 15826 | 15356 | 16483 | 17987 | 18608 | 17871 | 18871 | 18633 | 20503 | 20714 | 21233 | 20594 | 19178 | 20103
7326 | 7326 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 6 | 13901 | 13001 | 15177 | 16618 | 16251 | 16115 | 16258 | 15563 | 17436 | 18510 | 18835 | 18486 | 18695 | 19319 | 20945 | 20733 | 20988 | 20174 | 18758 | 20631
7327 | 7327 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 7 | 15586 | 13601 | 16812 | 18222 | 17462 | 17590 | 16893 | 15933 | 18909 | 19499 | 19740 | 19644 | 18851 | 20471 | 21870 | 21322 | 21649 | 20130 | 18705 | 21679
7328 | 7328 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 8 | 16167 | 13993 | 17544 | 18694 | 18308 | 18171 | 17175 | 16202 | 19633 | 20225 | 20527 | 20075 | 18954 | 21020 | 21974 | 21870 | 22268 | 20151 | 18744 | 22177
7329 | 7329 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 9 | 16356 | 14300 | 17796 | 18739 | 18429 | 18387 | 17626 | 16475 | 19816 | 20284 | 20646 | 20145 | 19331 | 21095 | 21894 | 21845 | 22340 | 20462 | 18871 | 22209
7330 | 7330 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 10 | 16433 | 14345 | 17650 | 18647 | 18355 | 18501 | 17828 | 16547 | 19712 | 20278 | 20665 | 20347 | 19423 | 21024 | 21839 | 21718 | 22245 | 20592 | 18819 | 22172
7331 | 7331 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 11 | 16680 | 14701 | 17791 | 18821 | 18451 | 18777 | 18208 | 16973 | 19890 | 20445 | 20820 | 20715 | 19395 | 21246 | 21878 | 21481 | 21990 | 20609 | 18938 | 22439
7332 | 7332 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 12 | 16732 | 14826 | 17809 | 18760 | 18408 | 18854 | 18256 | 17088 | 19864 | 20413 | 20750 | 20825 | 19159 | 21249 | 21690 | 21186 | 21646 | 20395 | 18960 | 22429
7333 | 7333 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 13 | 16471 | 14574 | 17630 | 18462 | 18318 | 18603 | 18036 | 16838 | 19654 | 20320 | 20498 | 20580 | 18818 | 21028 | 21274 | 20976 | 21269 | 20046 | 18581 | 22208
7334 | 7334 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 14 | 16410 | 14448 | 17629 | 18323 | 18405 | 18418 | 17808 | 16679 | 19620 | 20339 | 20389 | 20344 | 18598 | 20940 | 21045 | 20996 | 21175 | 19778 | 18635 | 22094
7335 | 7335 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 15 | 16332 | 14403 | 17656 | 18306 | 18398 | 18237 | 17574 | 16512 | 19508 | 20230 | 20224 | 20052 | 18562 | 20784 | 21091 | 21133 | 21242 | 19718 | 18553 | 21923
7336 | 7336 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 16 | 16565 | 14773 | 18120 | 18760 | 18588 | 18296 | 17586 | 16706 | 19767 | 20229 | 20185 | 19908 | 18727 | 20944 | 21730 | 21337 | 21403 | 19819 | 18886 | 22055
7337 | 7337 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 17 | 16841 | 15341 | 18558 | 19288 | 19025 | 18593 | 17950 | 17154 | 20150 | 20719 | 20642 | 20189 | 19272 | 21295 | 22320 | 22047 | 22123 | 20399 | 19570 | 22422
7338 | 7338 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 18 | 16928 | 15832 | 18974 | 19500 | 19479 | 18780 | 18277 | 17623 | 20551 | 21008 | 21411 | 20517 | 20147 | 21906 | 22662 | 22862 | 23273 | 21400 | 20313 | 23130
7339 | 7339 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 19 | 16932 | 15756 | 18986 | 19488 | 19484 | 18884 | 18394 | 17770 | 20629 | 21227 | 21705 | 20885 | 20701 | 22360 | 23149 | 23513 | 23954 | 22151 | 20958 | 23708
7340 | 7340 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 20 | 16543 | 15513 | 18627 | 19287 | 19351 | 18591 | 18116 | 17702 | 20584 | 21428 | 21995 | 21103 | 20857 | 22664 | 23708 | 24124 | 24666 | 22556 | 21467 | 24151
7341 | 7341 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 21 | 16029 | 15146 | 18203 | 18917 | 19024 | 18267 | 17853 | 17567 | 20435 | 21517 | 22165 | 21291 | 21181 | 22933 | 24230 | 24783 | 25328 | 23196 | 22027 | 24616
7342 | 7342 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 22 | 15084 | 14435 | 17200 | 18004 | 18349 | 17466 | 17381 | 17054 | 19647 | 21170 | 21795 | 20820 | 21066 | 22396 | 23928 | 24786 | 25250 | 23282 | 21937 | 24205
7343 | 7343 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 23 | 14094 | 13612 | 16103 | 16921 | 17404 | 16562 | 16795 | 16330 | 18698 | 20417 | 21124 | 20114 | 20707 | 21549 | 23191 | 24217 | 24769 | 23022 | 21573 | 23416
7344 | 7344 | 306 | 11 | 2 | Winter | 11 | 1 | Winter | 24 | 13249 | 13009 | 15289 | 16114 | 16489 | 15808 | 16368 | 15878 | 18030 | 19647 | 20511 | 19515 | 20443 | 20936 | 22644 | 23545 | 24227 | 22826 | 21191 | 22846
7345 | 7345 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 1 | 12602 | 12614 | 14509 | 14926 | 15348 | 15280 | 15040 | 15416 | 17562 | 18470 | 19870 | 19216 | 18460 | 20814 | 21734 | 22380 | 23677 | 20492 | 20571 | 22930
7346 | 7346 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 2 | 12333 | 12414 | 14267 | 14581 | 15063 | 15002 | 14808 | 15230 | 17339 | 18161 | 19462 | 18862 | 18165 | 20490 | 21266 | 21936 | 23153 | 20138 | 20282 | 22550
7347 | 7347 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 3 | 12188 | 12379 | 14214 | 14512 | 14992 | 14923 | 14754 | 15304 | 17317 | 18123 | 19288 | 18726 | 18042 | 20372 | 21106 | 21738 | 22807 | 19938 | 20179 | 22365
7348 | 7348 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 4 | 12210 | 12499 | 14295 | 14462 | 14953 | 14884 | 14636 | 15319 | 17250 | 17849 | 18880 | 18348 | 17618 | 19970 | 20511 | 21076 | 22057 | 19335 | 19762 | 21797
7349 | 7349 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 5 | 12462 | 13031 | 14730 | 14719 | 15143 | 15002 | 14656 | 15718 | 17437 | 17810 | 18641 | 18043 | 17215 | 19795 | 20048 | 20543 | 21427 | 18717 | 19655 | 21409
7350 | 7350 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 6 | 13077 | 14260 | 15943 | 15591 | 15762 | 15482 | 14925 | 16762 | 18354 | 18131 | 18771 | 17995 | 17038 | 20309 | 20134 | 20374 | 21177 | 18329 | 20202 | 21714
7351 | 7351 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 7 | 13773 | 15908 | 17587 | 16831 | 17013 | 16157 | 15359 | 18305 | 19619 | 19122 | 19674 | 18219 | 17152 | 21276 | 20761 | 21063 | 21695 | 18281 | 21243 | 22516
7352 | 7352 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 8 | 14088 | 16626 | 18071 | 17679 | 17948 | 16430 | 15629 | 19041 | 19974 | 19923 | 20545 | 18355 | 17250 | 21399 | 21323 | 21704 | 22368 | 18313 | 21740 | 22542
7353 | 7353 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 9 | 14619 | 16949 | 18208 | 17882 | 18170 | 16956 | 15994 | 19326 | 20123 | 20141 | 20733 | 18816 | 17482 | 21402 | 21387 | 21848 | 22456 | 18508 | 21843 | 22495
7354 | 7354 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 10 | 14916 | 16853 | 18126 | 17801 | 18201 | 17127 | 16016 | 19159 | 20240 | 20076 | 20691 | 19006 | 17460 | 21448 | 21367 | 21854 | 22417 | 18563 | 21916 | 22595
7355 | 7355 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 11 | 15268 | 16727 | 17988 | 17557 | 18232 | 17087 | 15980 | 18854 | 20500 | 19688 | 20448 | 18906 | 17486 | 21406 | 21055 | 21527 | 22502 | 18608 | 22100 | 22612
7356 | 7356 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 12 | 15415 | 16687 | 17832 | 17409 | 18200 | 16966 | 15901 | 18633 | 20478 | 19370 | 20243 | 18719 | 17544 | 21260 | 20795 | 21236 | 22811 | 18666 | 22155 | 22467
7357 | 7357 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 13 | 15103 | 16377 | 17374 | 17154 | 17864 | 16559 | 15454 | 18225 | 20070 | 18904 | 19847 | 18276 | 17075 | 20737 | 20481 | 20756 | 22517 | 18179 | 21813 | 21938
7358 | 7358 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 14 | 14810 | 16340 | 17216 | 17203 | 17748 | 16320 | 15284 | 18166 | 19764 | 18795 | 19666 | 17995 | 17073 | 20462 | 20451 | 20590 | 22431 | 18180 | 21649 | 21630
7359 | 7359 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 15 | 14672 | 16507 | 17371 | 17389 | 17730 | 16322 | 15372 | 18331 | 19597 | 18927 | 19547 | 17970 | 17012 | 20523 | 20598 | 20666 | 21974 | 18105 | 21482 | 21662
7360 | 7360 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 16 | 14994 | 17255 | 18094 | 17919 | 18064 | 16739 | 15991 | 19025 | 20116 | 19358 | 19604 | 18287 | 17520 | 21329 | 20969 | 20978 | 21627 | 18587 | 21747 | 22432
7361 | 7361 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 17 | 15208 | 17661 | 18613 | 18374 | 18529 | 17141 | 16480 | 19475 | 20473 | 19877 | 20123 | 18735 | 18072 | 21815 | 21560 | 21611 | 21926 | 19167 | 22024 | 22934
7362 | 7362 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 18 | 15621 | 18190 | 19000 | 19010 | 19232 | 17680 | 17145 | 20075 | 20622 | 20838 | 21141 | 19574 | 18733 | 22148 | 22370 | 22752 | 22946 | 19941 | 22747 | 23347
7363 | 7363 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 19 | 15589 | 18180 | 18963 | 18966 | 19119 | 17763 | 17253 | 20094 | 20752 | 21042 | 21338 | 20032 | 19189 | 22560 | 22954 | 23371 | 23583 | 20562 | 23297 | 23934
7364 | 7364 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 20 | 15151 | 17806 | 18737 | 18793 | 19018 | 17461 | 17154 | 19996 | 20754 | 21242 | 21541 | 20115 | 19506 | 23069 | 23522 | 24056 | 24214 | 21075 | 23747 | 24643
7365 | 7365 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 21 | 14640 | 17352 | 18328 | 18419 | 18701 | 17132 | 16956 | 19778 | 20714 | 21298 | 21749 | 20342 | 19805 | 23518 | 24121 | 24670 | 24946 | 21624 | 24207 | 25340
7366 | 7366 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 22 | 14001 | 16318 | 17370 | 17700 | 18006 | 16600 | 16377 | 18930 | 20062 | 20843 | 21440 | 20164 | 19545 | 23161 | 24065 | 24558 | 24967 | 21503 | 23780 | 25145
7367 | 7367 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 23 | 13347 | 15241 | 16294 | 16758 | 17162 | 16015 | 15654 | 17963 | 19155 | 20171 | 20828 | 19784 | 19119 | 22419 | 23498 | 24074 | 24584 | 21159 | 23012 | 24494
7368 | 7368 | 307 | 11 | 3 | Winter | 11 | 2 | Winter | 24 | 12819 | 14422 | 15468 | 15836 | 16363 | 15563 | 15176 | 17271 | 18514 | 19551 | 20188 | 19505 | 18677 | 21866 | 22821 | 23528 | 23933 | 20779 | 22456 | 23995
7369 | 7369 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 1 | 12367 | 14170 | 14844 | 15257 | 16116 | 14857 | 15263 | 17265 | 17986 | 19439 | 19372 | 18177 | 18661 | 21485 | 22197 | 23507 | 22893 | 20705 | 23055 | 23701
7370 | 7370 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 2 | 12121 | 13912 | 14502 | 14943 | 15742 | 14619 | 15073 | 17011 | 17659 | 19061 | 18929 | 17897 | 18426 | 21034 | 21764 | 23004 | 22336 | 20416 | 22681 | 23200
7371 | 7371 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 3 | 11987 | 13833 | 14398 | 14866 | 15586 | 14540 | 15131 | 17015 | 17626 | 18913 | 18765 | 17783 | 18380 | 20876 | 21575 | 22663 | 22026 | 20299 | 22492 | 22971
7372 | 7372 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 4 | 11933 | 13907 | 14342 | 14816 | 15479 | 14429 | 15160 | 16965 | 17395 | 18568 | 18337 | 17397 | 18128 | 20315 | 20946 | 21933 | 21255 | 19876 | 21910 | 22228
7373 | 7373 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 5 | 12014 | 14349 | 14612 | 15040 | 15637 | 14482 | 15605 | 17227 | 17385 | 18420 | 17871 | 17061 | 18240 | 19915 | 20466 | 21350 | 20392 | 19788 | 21532 | 21605
7374 | 7374 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 6 | 12365 | 15575 | 15507 | 15704 | 16261 | 14804 | 16730 | 18216 | 18008 | 18670 | 17546 | 16981 | 19017 | 20085 | 20371 | 21166 | 19650 | 20367 | 21863 | 21546
7375 | 7375 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 7 | 12971 | 17235 | 16752 | 16973 | 17440 | 15268 | 18321 | 19557 | 19072 | 19648 | 17645 | 17157 | 20202 | 20766 | 21092 | 21708 | 19462 | 21407 | 22659 | 22032
7376 | 7376 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 8 | 13368 | 17788 | 17606 | 17912 | 18449 | 15559 | 19094 | 19989 | 19815 | 20577 | 18178 | 17296 | 20780 | 21361 | 21768 | 22404 | 19838 | 21924 | 22725 | 22521
7377 | 7377 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 9 | 13706 | 17874 | 17760 | 18087 | 18693 | 15865 | 19328 | 20133 | 19926 | 20723 | 18700 | 17503 | 20884 | 21385 | 21859 | 22446 | 20194 | 21966 | 22619 | 22470
7378 | 7378 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 10 | 13827 | 17783 | 17688 | 18020 | 18681 | 15860 | 19130 | 20065 | 19877 | 20629 | 18991 | 17511 | 20945 | 21368 | 21863 | 22439 | 20613 | 22041 | 22716 | 22494
7379 | 7379 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 11 | 13948 | 17734 | 17557 | 17834 | 18548 | 15932 | 18938 | 19970 | 19548 | 20483 | 19032 | 17545 | 21125 | 21091 | 21574 | 22540 | 20648 | 22266 | 22775 | 22259
7380 | 7380 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 12 | 14066 | 17724 | 17586 | 17797 | 18489 | 16058 | 18934 | 19898 | 19349 | 20503 | 19080 | 17656 | 21223 | 20899 | 21338 | 22904 | 20553 | 22385 | 22691 | 22081
7381 | 7381 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 13 | 13579 | 17205 | 17255 | 17306 | 18057 | 15531 | 18445 | 19291 | 18962 | 20015 | 18677 | 17101 | 20811 | 20503 | 20780 | 22521 | 20146 | 21965 | 22087 | 21684
7382 | 7382 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 14 | 13538 | 17273 | 17534 | 17502 | 18055 | 15649 | 18692 | 19380 | 19101 | 20186 | 18726 | 17249 | 20794 | 20596 | 20736 | 22581 | 19932 | 21918 | 21896 | 21751
7383 | 7383 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 15 | 13617 | 17384 | 17651 | 17611 | 17984 | 15652 | 18761 | 19387 | 19284 | 19955 | 18616 | 17202 | 20652 | 20745 | 20816 | 22134 | 19908 | 21751 | 21930 | 21884
7384 | 7384 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 16 | 14289 | 18088 | 18208 | 18189 | 18212 | 16299 | 19483 | 20186 | 19776 | 20044 | 18764 | 17766 | 21000 | 21153 | 21170 | 21839 | 19989 | 22055 | 22728 | 22256
7385 | 7385 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 17 | 14745 | 18479 | 18536 | 18640 | 18627 | 16652 | 19785 | 20557 | 20252 | 20400 | 19325 | 18230 | 21169 | 21654 | 21710 | 22054 | 20669 | 22233 | 23139 | 22788
7386 | 7386 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 18 | 15275 | 18759 | 19045 | 19307 | 19414 | 17130 | 20155 | 20694 | 20707 | 21118 | 20146 | 18778 | 21718 | 22378 | 22777 | 23009 | 21902 | 22898 | 23493 | 23619
7387 | 7387 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 19 | 15180 | 18737 | 19004 | 19180 | 19378 | 17228 | 20157 | 20789 | 20869 | 21243 | 20317 | 19179 | 22117 | 22925 | 23366 | 23619 | 22344 | 23468 | 24079 | 24351
7388 | 7388 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 20 | 14901 | 18439 | 18755 | 19019 | 19070 | 17061 | 19987 | 20704 | 20960 | 21315 | 20351 | 19391 | 22343 | 23394 | 23970 | 24174 | 22863 | 23887 | 24768 | 25047
7389 | 7389 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 21 | 14544 | 17990 | 18362 | 18680 | 18797 | 16852 | 19735 | 20591 | 20961 | 21429 | 20621 | 19637 | 22562 | 23941 | 24546 | 24867 | 23624 | 24359 | 25477 | 25862
7390 | 7390 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 22 | 13782 | 16974 | 17591 | 17921 | 18144 | 16208 | 18817 | 19832 | 20508 | 21032 | 20476 | 19291 | 21948 | 23809 | 24373 | 24822 | 23777 | 23895 | 25243 | 25914
7391 | 7391 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 23 | 12975 | 15926 | 16660 | 17110 | 17309 | 15522 | 17889 | 18964 | 19732 | 20477 | 20215 | 18824 | 21104 | 23205 | 23858 | 24419 | 23575 | 23110 | 24581 | 25397
7392 | 7392 | 308 | 11 | 4 | Winter | 11 | 3 | Winter | 24 | 12363 | 15042 | 15677 | 16257 | 16477 | 14958 | 17106 | 18228 | 18935 | 19748 | 19718 | 18361 | 20476 | 22509 | 23289 | 23761 | 23233 | 22533 | 24077 | 24757
7393 | 7393 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 1 | 12214 | 14108 | 14837 | 15657 | 15550 | 14733 | 16707 | 17339 | 17979 | 18647 | 18487 | 18047 | 20523 | 21566 | 22947 | 22422 | 21514 | 22807 | 23473 | 23841
7394 | 7394 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 2 | 12062 | 13804 | 14556 | 15319 | 15185 | 14572 | 16490 | 17063 | 17708 | 18269 | 18164 | 17855 | 20229 | 21173 | 22482 | 21895 | 21044 | 22447 | 22989 | 23387
7395 | 7395 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 3 | 12003 | 13644 | 14429 | 15114 | 15035 | 14573 | 16445 | 16985 | 17660 | 18093 | 18002 | 17819 | 20113 | 20994 | 22149 | 21595 | 20802 | 22251 | 22752 | 23135
7396 | 7396 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 4 | 12120 | 13606 | 14401 | 15039 | 14907 | 14635 | 16447 | 16825 | 17439 | 17755 | 17626 | 17621 | 19751 | 20416 | 21466 | 20861 | 20143 | 21683 | 22015 | 22370
7397 | 7397 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 5 | 12658 | 13885 | 14641 | 15224 | 14821 | 15107 | 16758 | 16876 | 17480 | 17362 | 17264 | 17803 | 19642 | 20000 | 20940 | 20038 | 19470 | 21329 | 21405 | 21733
7398 | 7398 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 6 | 13883 | 14772 | 15328 | 15881 | 14942 | 16259 | 17808 | 17567 | 17883 | 17123 | 17029 | 18630 | 20214 | 19943 | 20788 | 19312 | 18832 | 21658 | 21334 | 21455
7399 | 7399 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 7 | 15564 | 16064 | 16658 | 17116 | 15485 | 17905 | 19248 | 18717 | 18968 | 17318 | 17088 | 19915 | 21261 | 20743 | 21406 | 19187 | 18587 | 22508 | 21871 | 22119
7400 | 7400 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 8 | 16268 | 16905 | 17591 | 18115 | 16126 | 18666 | 19712 | 19492 | 19803 | 17902 | 17433 | 20507 | 21439 | 21422 | 22107 | 19581 | 18848 | 22569 | 22350 | 22727
7401 | 7401 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 9 | 16581 | 17130 | 17805 | 18384 | 16731 | 18921 | 19896 | 19652 | 20026 | 18484 | 17912 | 20676 | 21454 | 21568 | 22205 | 19991 | 19306 | 22512 | 22352 | 22839
7402 | 7402 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 10 | 16581 | 17257 | 17959 | 18561 | 17104 | 18982 | 20090 | 19832 | 20012 | 19074 | 18422 | 20797 | 21580 | 21649 | 22276 | 20465 | 19690 | 22688 | 22460 | 22953
7403 | 7403 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 11 | 16510 | 17359 | 18034 | 18772 | 17193 | 19135 | 20353 | 19974 | 19720 | 19538 | 18726 | 21003 | 21558 | 21368 | 22389 | 20528 | 19572 | 22758 | 22242 | 22729
7404 | 7404 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 12 | 16533 | 17363 | 17978 | 18809 | 17176 | 19134 | 20287 | 19945 | 19545 | 19601 | 18904 | 21001 | 21370 | 21035 | 22644 | 20332 | 19448 | 22574 | 21960 | 22418
7405 | 7405 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 13 | 16360 | 17278 | 17750 | 18647 | 17011 | 18937 | 19978 | 19854 | 19190 | 19507 | 18813 | 20788 | 20971 | 20671 | 22451 | 20119 | 19228 | 22161 | 21744 | 22049
7406 | 7406 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 14 | 16449 | 17338 | 17724 | 18548 | 16939 | 18897 | 19768 | 19881 | 19343 | 19217 | 18651 | 20700 | 20738 | 20562 | 22444 | 19830 | 19121 | 21900 | 21741 | 21909
7407 | 7407 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 15 | 16549 | 17375 | 17754 | 18307 | 16882 | 18850 | 19648 | 19806 | 19357 | 18943 | 18530 | 20553 | 20796 | 20643 | 21996 | 19799 | 19358 | 21929 | 21865 | 21956
7408 | 7408 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 16 | 17157 | 17648 | 18043 | 18216 | 16983 | 19222 | 20041 | 19890 | 19662 | 18666 | 18590 | 20756 | 21477 | 20854 | 21555 | 19727 | 19766 | 22569 | 22082 | 22103
7409 | 7409 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 17 | 17442 | 17924 | 18436 | 18519 | 17539 | 19457 | 20335 | 20202 | 20029 | 19116 | 19128 | 20909 | 21877 | 21396 | 21764 | 20396 | 20443 | 22977 | 22621 | 22657
7410 | 7410 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 18 | 17804 | 18451 | 19039 | 19139 | 18175 | 19807 | 20448 | 20443 | 20704 | 19822 | 19936 | 21387 | 22108 | 22414 | 22684 | 21604 | 21566 | 23317 | 23431 | 23780
7411 | 7411 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 19 | 17817 | 18380 | 18882 | 19069 | 18043 | 19788 | 20498 | 20540 | 20861 | 19894 | 20157 | 21731 | 22478 | 22948 | 23254 | 22015 | 22089 | 23902 | 24156 | 24495
7412 | 7412 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 20 | 17403 | 18083 | 18690 | 18735 | 17774 | 19595 | 20358 | 20558 | 20955 | 19844 | 20212 | 21910 | 22912 | 23501 | 23766 | 22521 | 22405 | 24585 | 24848 | 25236
7413 | 7413 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 21 | 16903 | 17618 | 18265 | 18380 | 17505 | 19251 | 20125 | 20424 | 20885 | 19957 | 20359 | 22000 | 23252 | 23956 | 24337 | 23179 | 22952 | 25229 | 25602 | 25945
7414 | 7414 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 22 | 15857 | 16859 | 17522 | 17743 | 17049 | 18336 | 19351 | 19946 | 20370 | 19794 | 20130 | 21375 | 22840 | 23767 | 24300 | 23333 | 22942 | 25014 | 25682 | 25921
7415 | 7415 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 23 | 14793 | 15869 | 16633 | 16894 | 16545 | 17309 | 18364 | 19123 | 19731 | 19401 | 19660 | 20507 | 22064 | 23236 | 23878 | 23118 | 22585 | 24354 | 25170 | 25487
7416 | 7416 | 309 | 11 | 5 | Winter | 11 | 4 | Winter | 24 | 13932 | 14905 | 15781 | 16039 | 15871 | 16541 | 17640 | 18279 | 19009 | 18946 | 19172 | 19857 | 21482 | 22646 | 23195 | 22750 | 22206 | 23828 | 24521 | 24962
7417 | 7417 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 1 | 13265 | 14015 | 15084 | 15057 | 15101 | 16011 | 16636 | 17225 | 18458 | 17760 | 18582 | 19735 | 20682 | 22199 | 21790 | 21007 | 21527 | 23109 | 23513 | 24571
7418 | 7418 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 2 | 13057 | 13730 | 14746 | 14691 | 14795 | 15778 | 16341 | 16969 | 18144 | 17449 | 18352 | 19466 | 20272 | 21757 | 21284 | 20553 | 21218 | 22631 | 23077 | 24057
7419 | 7419 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 3 | 12969 | 13591 | 14556 | 14532 | 14657 | 15754 | 16301 | 16918 | 17971 | 17352 | 18348 | 19394 | 20142 | 21464 | 21020 | 20340 | 21076 | 22418 | 22834 | 23681
7420 | 7420 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 4 | 13062 | 13560 | 14490 | 14420 | 14510 | 15771 | 16169 | 16752 | 17714 | 17020 | 18149 | 19094 | 19638 | 20838 | 20332 | 19704 | 20629 | 21698 | 22079 | 22858
7421 | 7421 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 5 | 13499 | 13809 | 14694 | 14351 | 14486 | 16125 | 16276 | 16858 | 17630 | 16730 | 18135 | 19050 | 19296 | 20366 | 19556 | 19054 | 20246 | 21097 | 21440 | 22150
7422 | 7422 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 6 | 14727 | 14550 | 15399 | 14533 | 14612 | 17231 | 17037 | 17382 | 17988 | 16570 | 18557 | 19723 | 19528 | 20301 | 18902 | 18471 | 20354 | 21069 | 21195 | 21850
7423 | 7423 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 7 | 16385 | 15834 | 16620 | 15054 | 14858 | 18674 | 18194 | 18495 | 19010 | 16649 | 19675 | 20791 | 20244 | 20906 | 18760 | 18194 | 21287 | 21557 | 21811 | 22298
7424 | 7424 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 8 | 16956 | 16739 | 17637 | 15720 | 15335 | 19173 | 19021 | 19361 | 19982 | 17036 | 20639 | 21042 | 20894 | 21644 | 19189 | 18481 | 22144 | 22081 | 22423 | 22967
7425 | 7425 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 9 | 17034 | 16930 | 17886 | 16287 | 15844 | 19324 | 19169 | 19554 | 20123 | 17525 | 20759 | 21038 | 20946 | 21716 | 19577 | 18907 | 22176 | 22053 | 22495 | 23002
7426 | 7426 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 10 | 16952 | 16854 | 17816 | 16536 | 16121 | 19197 | 19018 | 19425 | 20169 | 17683 | 20668 | 20984 | 20838 | 21620 | 19883 | 19120 | 22316 | 21990 | 22457 | 22944
7427 | 7427 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 11 | 17107 | 16776 | 17862 | 16731 | 16389 | 19177 | 18863 | 19240 | 20472 | 17628 | 20567 | 20991 | 20602 | 21734 | 19949 | 19043 | 22654 | 21779 | 22237 | 23113
7428 | 7428 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 12 | 17058 | 16691 | 17833 | 16702 | 16562 | 19002 | 18711 | 19039 | 20516 | 17653 | 20502 | 20794 | 20313 | 21990 | 19752 | 18911 | 22767 | 21495 | 21935 | 23372
7429 | 7429 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 13 | 16712 | 16387 | 17562 | 16489 | 16401 | 18563 | 18481 | 18646 | 20265 | 17406 | 20221 | 20319 | 20031 | 21734 | 19475 | 18617 | 22564 | 21224 | 21498 | 23110
7430 | 7430 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 14 | 16517 | 16293 | 17405 | 16187 | 16200 | 18314 | 18467 | 18514 | 20015 | 17213 | 20103 | 20006 | 19969 | 21635 | 19092 | 18422 | 22358 | 21122 | 21261 | 23002
7431 | 7431 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 15 | 16535 | 16400 | 17290 | 16172 | 16166 | 18394 | 18604 | 18612 | 19607 | 17340 | 20058 | 20038 | 20090 | 21157 | 19027 | 18626 | 22005 | 21211 | 21272 | 22491
7432 | 7432 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 16 | 17193 | 17077 | 17622 | 16531 | 16656 | 19272 | 19200 | 19192 | 19534 | 17946 | 20348 | 20946 | 20594 | 20969 | 19202 | 19277 | 21918 | 21663 | 21656 | 22238
7433 | 7433 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 17 | 17610 | 17589 | 18062 | 17164 | 17221 | 19741 | 19686 | 19635 | 19863 | 18658 | 20900 | 21420 | 21168 | 21265 | 19951 | 20030 | 22470 | 22275 | 22286 | 22551
7434 | 7434 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 18 | 17920 | 18243 | 18715 | 17835 | 18113 | 19961 | 20011 | 20314 | 20555 | 19482 | 21873 | 21662 | 21888 | 22188 | 21175 | 21182 | 23543 | 23118 | 23454 | 23577
7435 | 7435 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 19 | 17897 | 18062 | 18613 | 17656 | 18101 | 19983 | 20060 | 20396 | 20593 | 19630 | 22061 | 21954 | 22363 | 22691 | 21531 | 21658 | 24007 | 23815 | 24157 | 24259
7436 | 7436 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 20 | 17563 | 17841 | 18252 | 17355 | 17829 | 19803 | 20032 | 20406 | 20573 | 19612 | 22308 | 22314 | 22764 | 23150 | 21993 | 21950 | 24563 | 24517 | 24888 | 24917
7437 | 7437 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 21 | 17077 | 17441 | 17912 | 17091 | 17629 | 19558 | 19864 | 20293 | 20591 | 19714 | 22418 | 22600 | 23216 | 23696 | 22638 | 22508 | 25064 | 25292 | 25637 | 25733
7438 | 7438 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 22 | 16061 | 16683 | 17225 | 16594 | 17094 | 18706 | 19295 | 19709 | 20152 | 19412 | 21948 | 22112 | 23044 | 23582 | 22731 | 22467 | 24826 | 25330 | 25581 | 25774
7439 | 7439 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 23 | 14979 | 15794 | 16351 | 16021 | 16446 | 17686 | 18435 | 18937 | 19464 | 18913 | 21137 | 21315 | 22430 | 23140 | 22493 | 22112 | 24151 | 24802 | 25141 | 25415
7440 | 7440 | 310 | 11 | 6 | Winter | 11 | 5 | Winter | 24 | 14120 | 14958 | 15496 | 15392 | 15832 | 16954 | 17577 | 18254 | 18773 | 18443 | 20315 | 20729 | 21722 | 22463 | 22132 | 21739 | 23359 | 24159 | 24639 | 24800
7441 | 7441 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 1 | 13454 | 14557 | 14866 | 15004 | 15618 | 16248 | 16848 | 18013 | 17967 | 18206 | 20364 | 20216 | 21009 | 21413 | 20782 | 21388 | 23745 | 23476 | 24570 | 23621
7442 | 7442 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 2 | 13125 | 14177 | 14469 | 14638 | 15375 | 15912 | 16554 | 17651 | 17562 | 17967 | 20001 | 19801 | 20622 | 20899 | 20306 | 21067 | 23300 | 23011 | 24029 | 23041
7443 | 7443 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 3 | 12993 | 13995 | 14304 | 14517 | 15361 | 15871 | 16515 | 17519 | 17438 | 17999 | 19859 | 19704 | 20481 | 20658 | 20116 | 20944 | 22996 | 22785 | 23659 | 22729
7444 | 7444 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 4 | 12969 | 13953 | 14224 | 14386 | 15400 | 15785 | 16410 | 17320 | 17163 | 17876 | 19565 | 19282 | 19981 | 20042 | 19532 | 20540 | 22405 | 22059 | 22856 | 21922
7445 | 7445 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 5 | 13253 | 14165 | 14175 | 14387 | 15632 | 15936 | 16576 | 17325 | 16856 | 17931 | 19378 | 19020 | 19634 | 19326 | 18924 | 20194 | 21881 | 21443 | 22162 | 20979
7446 | 7446 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 6 | 14144 | 14882 | 14379 | 14522 | 16336 | 16744 | 17171 | 17761 | 16699 | 18421 | 19621 | 19331 | 19672 | 18727 | 18372 | 20332 | 21827 | 21211 | 21865 | 20165
7447 | 7447 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 7 | 15407 | 16143 | 14964 | 14818 | 17788 | 17978 | 18368 | 18896 | 16946 | 19633 | 20413 | 20138 | 20499 | 18661 | 18149 | 21314 | 22232 | 21865 | 22344 | 19938
7448 | 7448 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 8 | 16256 | 17137 | 15646 | 15301 | 18863 | 18822 | 19253 | 19885 | 17563 | 20608 | 21063 | 20820 | 21198 | 19108 | 18463 | 22163 | 22630 | 22480 | 23014 | 20318
7449 | 7449 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 9 | 16401 | 17327 | 16167 | 15770 | 18944 | 18909 | 19395 | 20007 | 18085 | 20688 | 21121 | 20843 | 21256 | 19448 | 18838 | 22136 | 22556 | 22493 | 22989 | 20612
7450 | 7450 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 10 | 16250 | 17226 | 16399 | 15902 | 18803 | 18724 | 19232 | 19852 | 18286 | 20562 | 21019 | 20692 | 21132 | 19710 | 19004 | 22246 | 22704 | 22418 | 22892 | 20922
7451 | 7451 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 11 | 16189 | 17219 | 16523 | 15830 | 18713 | 18457 | 18920 | 19664 | 18373 | 20295 | 20930 | 20378 | 20822 | 19717 | 18874 | 22509 | 23179 | 22139 | 23011 | 20977
7452 | 7452 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 12 | 16147 | 17162 | 16451 | 15845 | 18689 | 18228 | 18625 | 19460 | 18297 | 20101 | 20662 | 20085 | 20489 | 19527 | 18747 | 22630 | 23191 | 21831 | 23277 | 20795
7453 | 7453 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 13 | 15797 | 16748 | 16076 | 15470 | 18281 | 17834 | 18066 | 18965 | 17890 | 19645 | 20206 | 19658 | 19899 | 19094 | 18293 | 22268 | 22834 | 21243 | 22855 | 20358
7454 | 7454 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 14 | 15805 | 16614 | 15798 | 15324 | 18223 | 17847 | 17961 | 18788 | 17597 | 19548 | 19981 | 19628 | 19729 | 18751 | 18137 | 22089 | 22509 | 21043 | 22772 | 19990
7455 | 7455 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 15 | 16001 | 16599 | 15868 | 15555 | 18294 | 18072 | 18155 | 18731 | 17656 | 19598 | 20023 | 19831 | 19864 | 18780 | 18433 | 21812 | 22220 | 21145 | 22351 | 19998
7456 | 7456 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 16 | 16724 | 17030 | 16333 | 16339 | 18776 | 18776 | 18850 | 19053 | 18017 | 19997 | 20719 | 20440 | 20418 | 19060 | 19183 | 21815 | 22580 | 21624 | 22194 | 20238
7457 | 7457 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 17 | 17233 | 17591 | 17096 | 17122 | 19514 | 19415 | 19447 | 19648 | 18760 | 20705 | 21385 | 21117 | 21151 | 19900 | 20031 | 22474 | 23042 | 22352 | 22605 | 21104
7458 | 7458 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 18 | 17832 | 18348 | 17856 | 18154 | 20433 | 19928 | 20283 | 20510 | 19521 | 21824 | 22152 | 21807 | 22185 | 21110 | 21172 | 23533 | 23749 | 23526 | 23642 | 22408
7459 | 7459 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 19 | 17730 | 18214 | 17634 | 18104 | 20309 | 19932 | 20306 | 20480 | 19512 | 21933 | 22211 | 22189 | 22641 | 21397 | 21595 | 23957 | 24216 | 24197 | 24298 | 22850
7460 | 7460 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 20 | 17405 | 17799 | 17265 | 17801 | 20233 | 19819 | 20229 | 20369 | 19373 | 22065 | 22408 | 22493 | 23098 | 21765 | 21825 | 24467 | 24843 | 24902 | 24927 | 23411
7461 | 7461 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 21 | 16936 | 17433 | 16939 | 17537 | 19945 | 19563 | 20018 | 20265 | 19410 | 22065 | 22544 | 22817 | 23493 | 22315 | 22309 | 24901 | 25454 | 25611 | 25713 | 24211
7462 | 7462 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 22 | 16120 | 16723 | 16408 | 16962 | 19205 | 18928 | 19372 | 19749 | 19152 | 21545 | 22231 | 22579 | 23223 | 22360 | 22226 | 24641 | 25419 | 25545 | 25747 | 24429
7463 | 7463 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 23 | 15136 | 15852 | 15824 | 16309 | 18251 | 18051 | 18574 | 19021 | 18728 | 20724 | 21547 | 21920 | 22670 | 22108 | 21873 | 23955 | 24870 | 25101 | 25394 | 24260
7464 | 7464 | 311 | 11 | 7 | Winter | 11 | 6 | Winter | 24 | 14166 | 14934 | 15136 | 15654 | 17253 | 17126 | 17819 | 18265 | 18240 | 19867 | 20813 | 21166 | 22054 | 21701 | 21454 | 23129 | 24204 | 24548 | 24749 | 23914
7465 | 7465 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 1 | 13287 | 13924 | 14388 | 15043 | 16492 | 15983 | 17143 | 17087 | 17068 | 19434 | 20159 | 20036 | 21505 | 20016 | 20712 | 23064 | 23668 | 24061 | 23186 | 21940
7466 | 7466 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 2 | 12999 | 13565 | 14051 | 14814 | 16177 | 15709 | 16819 | 16708 | 16751 | 19128 | 19755 | 19695 | 21089 | 19593 | 20433 | 22658 | 23160 | 23560 | 22641 | 21462
7467 | 7467 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 3 | 12858 | 13363 | 13898 | 14773 | 16035 | 15647 | 16663 | 16579 | 16673 | 19002 | 19609 | 19571 | 20808 | 19404 | 20302 | 22354 | 22878 | 23179 | 22306 | 21207
7468 | 7468 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 4 | 12842 | 13278 | 13769 | 14816 | 16006 | 15564 | 16503 | 16353 | 16402 | 18768 | 19222 | 19131 | 20257 | 18854 | 19924 | 21792 | 22161 | 22393 | 21502 | 20508
7469 | 7469 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 5 | 13103 | 13258 | 13804 | 15082 | 16173 | 15791 | 16593 | 16134 | 16174 | 18680 | 18960 | 18881 | 19866 | 18316 | 19638 | 21326 | 21482 | 21744 | 20588 | 19791
7470 | 7470 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 6 | 13862 | 13476 | 13973 | 15823 | 16806 | 16440 | 17127 | 16078 | 16079 | 19015 | 19221 | 19022 | 19884 | 17825 | 19828 | 21319 | 21325 | 21484 | 19792 | 19125
7471 | 7471 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 7 | 15161 | 14064 | 14269 | 17275 | 17919 | 17628 | 18305 | 16386 | 16222 | 19854 | 20130 | 19896 | 20569 | 17611 | 20811 | 21735 | 21958 | 21954 | 19543 | 18788
7472 | 7472 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 8 | 16074 | 14791 | 14785 | 18368 | 18810 | 18544 | 19319 | 17061 | 16660 | 20568 | 20913 | 20663 | 21337 | 17956 | 21691 | 22172 | 22564 | 22629 | 19936 | 19084
7473 | 7473 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 9 | 16271 | 15390 | 15332 | 18511 | 19054 | 18749 | 19518 | 17674 | 17184 | 20720 | 21023 | 20805 | 21436 | 18407 | 21739 | 22174 | 22516 | 22663 | 20296 | 19498
7474 | 7474 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 10 | 16368 | 15842 | 15674 | 18581 | 19096 | 18780 | 19565 | 18082 | 17512 | 20800 | 21018 | 20865 | 21510 | 18760 | 22034 | 22516 | 22595 | 22764 | 20794 | 19894
7475 | 7475 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 11 | 16167 | 15951 | 15612 | 18403 | 19000 | 18457 | 19357 | 18041 | 17280 | 20664 | 20868 | 20494 | 21526 | 18588 | 22257 | 22934 | 22516 | 22834 | 20812 | 19762
7476 | 7476 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 12 | 16058 | 15904 | 15657 | 18323 | 18831 | 18187 | 19173 | 17861 | 17188 | 20395 | 20724 | 20162 | 21781 | 18464 | 22374 | 22961 | 22391 | 23110 | 20637 | 19644
7477 | 7477 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 13 | 15968 | 15901 | 15657 | 18280 | 18794 | 18004 | 19053 | 17812 | 17136 | 20307 | 20623 | 19940 | 21736 | 18379 | 22390 | 22971 | 22288 | 23065 | 20560 | 19548
7478 | 7478 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 14 | 15895 | 15606 | 15507 | 18215 | 18630 | 17902 | 18879 | 17509 | 16954 | 20087 | 20544 | 19780 | 21670 | 18223 | 22209 | 22646 | 22161 | 22975 | 20188 | 19368
7479 | 7479 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 15 | 15954 | 15539 | 15605 | 18159 | 18592 | 17972 | 18695 | 17440 | 17047 | 20004 | 20552 | 19797 | 21159 | 18392 | 21805 | 22232 | 22141 | 22424 | 20064 | 19521
7480 | 7480 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 16 | 16348 | 15646 | 16037 | 18297 | 18891 | 18327 | 18679 | 17465 | 17392 | 20339 | 20696 | 20015 | 20715 | 18791 | 21463 | 22245 | 22195 | 21913 | 19943 | 19892
7481 | 7481 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 17 | 16850 | 16315 | 16707 | 18955 | 19419 | 18823 | 19164 | 18144 | 18142 | 20892 | 21397 | 20623 | 20976 | 19532 | 22000 | 22572 | 22907 | 22204 | 20701 | 20645
7482 | 7482 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 18 | 17551 | 17037 | 17686 | 19972 | 20171 | 19638 | 19976 | 19030 | 19128 | 21595 | 22066 | 21584 | 21860 | 20634 | 23031 | 23256 | 23771 | 23221 | 21982 | 21830
7483 | 7483 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 19 | 17348 | 16804 | 17631 | 19834 | 20045 | 19641 | 19915 | 18972 | 19216 | 21583 | 22146 | 21973 | 22298 | 21027 | 23432 | 23699 | 24123 | 23890 | 22439 | 22347
7484 | 7484 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 20 | 17077 | 16390 | 17292 | 19710 | 19761 | 19529 | 19731 | 18735 | 19101 | 21689 | 22241 | 22333 | 22638 | 21204 | 23893 | 24256 | 24735 | 24490 | 22992 | 22671
7485 | 7485 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 21 | 16620 | 16025 | 16981 | 19373 | 19417 | 19244 | 19536 | 18664 | 19090 | 21705 | 22379 | 22606 | 23066 | 21609 | 24255 | 24803 | 25386 | 25238 | 23770 | 23276
7486 | 7486 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 22 | 15888 | 15532 | 16419 | 18652 | 18787 | 18592 | 19007 | 18380 | 18759 | 21369 | 22138 | 22311 | 22931 | 21528 | 24007 | 24779 | 25445 | 25301 | 24005 | 23335
7487 | 7487 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 23 | 15005 | 14920 | 15739 | 17682 | 17880 | 17759 | 18233 | 17911 | 18238 | 20643 | 21440 | 21720 | 22452 | 21144 | 23304 | 24206 | 24905 | 24935 | 23831 | 23023
7488 | 7488 | 312 | 11 | 8 | Winter | 11 | 7 | Winter | 24 | 14163 | 14258 | 15098 | 16705 | 17016 | 17008 | 17479 | 17415 | 17741 | 19939 | 20744 | 21120 | 21759 | 20755 | 22502 | 23574 | 24287 | 24316 | 23529 | 22684
7489 | 7489 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 1 | 13576 | 13802 | 14734 | 16159 | 16418 | 16551 | 16572 | 16582 | 17338 | 19509 | 20311 | 20794 | 20575 | 20253 | 22639 | 23263 | 24068 | 22999 | 21808 | 22153
7490 | 7490 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 2 | 13226 | 13444 | 14491 | 15837 | 16052 | 16221 | 16189 | 16264 | 17114 | 19132 | 19907 | 20386 | 20095 | 19969 | 22239 | 22759 | 23531 | 22440 | 21317 | 21821
7491 | 7491 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 3 | 13056 | 13282 | 14454 | 15677 | 15956 | 16068 | 16066 | 16182 | 17166 | 19024 | 19746 | 20154 | 19887 | 19888 | 21968 | 22513 | 23213 | 22141 | 21095 | 21681
7492 | 7492 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 4 | 12998 | 13154 | 14493 | 15650 | 15846 | 15934 | 15878 | 15947 | 17064 | 18707 | 19350 | 19651 | 19299 | 19528 | 21422 | 21801 | 22474 | 21323 | 20382 | 21174
7493 | 7493 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 5 | 13242 | 13166 | 14753 | 15846 | 15953 | 16053 | 15701 | 15774 | 17191 | 18507 | 19098 | 19356 | 18668 | 19279 | 20998 | 21175 | 21817 | 20420 | 19660 | 20750
7494 | 7494 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 6 | 13971 | 13331 | 15507 | 16514 | 16642 | 16636 | 15720 | 15759 | 17738 | 18853 | 19283 | 19462 | 18136 | 19494 | 21024 | 21051 | 21529 | 19629 | 18981 | 20798
7495 | 7495 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 7 | 15236 | 13637 | 16980 | 17657 | 17957 | 17836 | 16087 | 15948 | 18981 | 19820 | 20168 | 20219 | 18117 | 20505 | 21491 | 21714 | 22065 | 19397 | 18649 | 21707
7496 | 7496 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 8 | 16213 | 14159 | 18081 | 18548 | 18867 | 18847 | 16779 | 16413 | 20004 | 20636 | 20943 | 21011 | 18600 | 21397 | 21917 | 22327 | 22758 | 19775 | 18925 | 22557
7497 | 7497 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 9 | 16415 | 14673 | 18186 | 18723 | 18965 | 18994 | 17351 | 16892 | 20114 | 20721 | 21084 | 21075 | 18977 | 21410 | 21889 | 22237 | 22877 | 20092 | 19297 | 22550
7498 | 7498 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 10 | 16530 | 15048 | 18278 | 18760 | 18942 | 19050 | 17756 | 17211 | 20191 | 20701 | 21090 | 21145 | 19438 | 21717 | 22250 | 22316 | 23144 | 20608 | 19712 | 22896
7499 | 7499 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 11 | 16443 | 15080 | 18200 | 18768 | 18796 | 18982 | 17871 | 17162 | 19844 | 20723 | 21041 | 21094 | 19342 | 21874 | 22597 | 22172 | 23385 | 20560 | 19517 | 23097
7500 | 7500 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 12 | 16321 | 15295 | 18305 | 18838 | 18641 | 19092 | 18018 | 17437 | 19583 | 20973 | 21129 | 21274 | 19071 | 21914 | 22558 | 21979 | 23296 | 20312 | 19327 | 23156
7501 | 7501 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 13 | 16395 | 15424 | 18430 | 18983 | 18682 | 19167 | 18169 | 17590 | 19608 | 21084 | 21046 | 21338 | 19116 | 22038 | 22673 | 21978 | 23209 | 20344 | 19341 | 23279
7502 | 7502 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 14 | 16361 | 15464 | 18556 | 19046 | 18735 | 19235 | 18118 | 17678 | 19611 | 21290 | 21086 | 21395 | 18872 | 21970 | 22464 | 21969 | 22967 | 20082 | 19271 | 23189
7503 | 7503 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 15 | 16228 | 15464 | 18387 | 18874 | 18765 | 18879 | 17851 | 17547 | 19543 | 21051 | 20877 | 20916 | 18782 | 21602 | 22082 | 21974 | 22683 | 19988 | 19451 | 22794
7504 | 7504 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 16 | 16210 | 15684 | 18283 | 18890 | 18905 | 18565 | 17549 | 17552 | 19498 | 20817 | 20718 | 20388 | 18614 | 21157 | 21989 | 21929 | 22409 | 19753 | 19706 | 22304
7505 | 7505 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 17 | 16719 | 16336 | 18891 | 19384 | 19645 | 18972 | 18131 | 18211 | 20159 | 21386 | 21279 | 20706 | 19404 | 21749 | 22366 | 22706 | 23015 | 20552 | 20509 | 22912
7506 | 7506 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 18 | 17458 | 17209 | 19778 | 20041 | 20236 | 19639 | 18829 | 18977 | 21257 | 21801 | 22019 | 21545 | 20577 | 22750 | 23035 | 23554 | 24058 | 21850 | 21706 | 24008
7507 | 7507 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 19 | 17308 | 17104 | 19590 | 19862 | 20003 | 19514 | 18695 | 18983 | 21300 | 21761 | 22271 | 21887 | 20794 | 23082 | 23417 | 23851 | 24681 | 22279 | 22197 | 24462
7508 | 7508 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 20 | 16874 | 16757 | 19454 | 19540 | 19780 | 19299 | 18408 | 18817 | 21383 | 21780 | 22392 | 22156 | 21103 | 23525 | 23933 | 24440 | 25136 | 22841 | 22533 | 25036
7509 | 7509 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 21 | 16506 | 16440 | 19121 | 19178 | 19435 | 19079 | 18296 | 18757 | 21305 | 21840 | 22604 | 22505 | 21574 | 23866 | 24453 | 25054 | 25834 | 23625 | 23170 | 25577
7510 | 7510 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 22 | 15803 | 15834 | 18351 | 18500 | 18800 | 18487 | 17933 | 18356 | 20746 | 21515 | 22248 | 22278 | 21580 | 23544 | 24369 | 25061 | 25783 | 23824 | 23193 | 25384
7511 | 7511 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 23 | 14930 | 15175 | 17414 | 17636 | 17895 | 17756 | 17511 | 17885 | 19893 | 20883 | 21641 | 21776 | 21304 | 22842 | 23777 | 24512 | 25231 | 23652 | 22887 | 24733
7512 | 7512 | 313 | 11 | 9 | Winter | 11 | 8 | Winter | 24 | 14045 | 14478 | 16364 | 16707 | 16992 | 16901 | 16904 | 17276 | 19043 | 20079 | 20894 | 21064 | 20919 | 22025 | 23129 | 23881 | 24668 | 23327 | 22537 | 23959
7513 | 7513 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 1 | 13326 | 14153 | 15820 | 16116 | 16292 | 16048 | 16159 | 16895 | 18827 | 19619 | 19813 | 19954 | 19605 | 22140 | 22833 | 23675 | 23561 | 21670 | 22039 | 24276
7514 | 7514 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 2 | 12983 | 13905 | 15489 | 15742 | 15933 | 15653 | 15823 | 16670 | 18542 | 19227 | 19321 | 19503 | 19181 | 21756 | 22338 | 23150 | 22970 | 21175 | 21712 | 23837
7515 | 7515 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 3 | 12782 | 13849 | 15324 | 15630 | 15786 | 15529 | 15752 | 16716 | 18410 | 19119 | 19079 | 19318 | 19024 | 21504 | 22109 | 22847 | 22537 | 20956 | 21572 | 23516
7516 | 7516 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 4 | 12691 | 13882 | 15296 | 15536 | 15685 | 15357 | 15533 | 16653 | 18230 | 18780 | 18596 | 18796 | 18499 | 21011 | 21440 | 22144 | 21715 | 20250 | 21070 | 22851
7517 | 7517 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 5 | 12684 | 14166 | 15512 | 15664 | 15879 | 15236 | 15417 | 16829 | 18212 | 18629 | 18177 | 18244 | 18025 | 20642 | 20863 | 21525 | 20837 | 19545 | 20653 | 22268
7518 | 7518 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 6 | 12889 | 14937 | 16165 | 16374 | 16502 | 15281 | 15440 | 17442 | 18622 | 18882 | 18074 | 17801 | 17573 | 20713 | 20782 | 21270 | 20316 | 18872 | 20695 | 22132
7519 | 7519 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 7 | 13509 | 16461 | 17391 | 17741 | 17659 | 15741 | 15733 | 18771 | 19541 | 19895 | 18694 | 17891 | 17422 | 21259 | 21522 | 21857 | 20629 | 18585 | 21637 | 22514
7520 | 7520 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 8 | 14228 | 17598 | 18342 | 18689 | 18559 | 16457 | 16245 | 19848 | 20287 | 20731 | 19839 | 18419 | 17783 | 21747 | 22191 | 22582 | 21598 | 18899 | 22517 | 22894
7521 | 7521 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 9 | 14846 | 17784 | 18596 | 18854 | 18813 | 17094 | 16803 | 20035 | 20465 | 20955 | 20123 | 18880 | 18271 | 21792 | 22171 | 22767 | 21792 | 19328 | 22568 | 22886
7522 | 7522 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 10 | 15272 | 17864 | 18594 | 18787 | 18771 | 17467 | 17085 | 20065 | 20488 | 20915 | 20173 | 19284 | 18585 | 22083 | 22184 | 22977 | 22092 | 19678 | 22845 | 23228
7523 | 7523 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 11 | 15448 | 17738 | 18534 | 18716 | 18748 | 17448 | 16885 | 19786 | 20560 | 20660 | 19932 | 19217 | 18377 | 22463 | 22076 | 23255 | 22367 | 19522 | 23087 | 23663
7524 | 7524 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 12 | 15528 | 17619 | 18358 | 18585 | 18764 | 17228 | 16755 | 19542 | 20683 | 20265 | 19737 | 18944 | 18181 | 22409 | 21872 | 23161 | 22482 | 19324 | 23137 | 23624
7525 | 7525 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 13 | 15643 | 17669 | 18420 | 18596 | 18667 | 17270 | 16791 | 19537 | 20778 | 20046 | 19651 | 18956 | 18173 | 22496 | 21845 | 23033 | 22505 | 19304 | 23227 | 23695
7526 | 7526 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 14 | 15377 | 17550 | 18234 | 18502 | 18573 | 16926 | 16572 | 19396 | 20696 | 19766 | 19479 | 18572 | 17988 | 22135 | 21681 | 22647 | 22252 | 19076 | 22979 | 23302
7527 | 7527 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 15 | 15236 | 17524 | 18230 | 18555 | 18526 | 16892 | 16695 | 19356 | 20394 | 19852 | 19379 | 18513 | 18203 | 21765 | 21694 | 22394 | 21827 | 19262 | 22591 | 22904
7528 | 7528 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 16 | 15225 | 17668 | 18467 | 18804 | 18694 | 16949 | 17073 | 19429 | 20450 | 20107 | 19256 | 18465 | 18595 | 21801 | 21773 | 22231 | 21271 | 19632 | 22218 | 22901
7529 | 7529 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 17 | 15885 | 18378 | 19076 | 19547 | 19210 | 17688 | 17896 | 20090 | 20891 | 20849 | 19796 | 19254 | 19383 | 22197 | 22555 | 22842 | 21739 | 20454 | 22844 | 23319
7530 | 7530 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 18 | 16491 | 19317 | 19870 | 20128 | 19905 | 18556 | 18818 | 21124 | 21358 | 21736 | 20744 | 20344 | 20445 | 22822 | 23373 | 23850 | 22605 | 21630 | 23916 | 24034
7531 | 7531 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 19 | 16224 | 19134 | 19692 | 19870 | 19842 | 18417 | 18811 | 21122 | 21256 | 21926 | 20831 | 20499 | 20774 | 23157 | 23631 | 24446 | 23043 | 22134 | 24385 | 24540
7532 | 7532 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 20 | 15772 | 18960 | 19322 | 19592 | 19568 | 18068 | 18590 | 21134 | 21268 | 21937 | 21111 | 20699 | 20892 | 23600 | 24153 | 24853 | 23745 | 22456 | 24943 | 25179
7533 | 7533 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 21 | 15395 | 18571 | 18889 | 19177 | 19274 | 17862 | 18433 | 20963 | 21196 | 22000 | 21383 | 21052 | 21234 | 24014 | 24677 | 25469 | 24548 | 23044 | 25439 | 25837
7534 | 7534 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 22 | 14889 | 17784 | 18189 | 18518 | 18628 | 17459 | 17989 | 20363 | 20792 | 21584 | 21232 | 21010 | 21097 | 23904 | 24651 | 25387 | 24717 | 23065 | 25258 | 25883
7535 | 7535 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 23 | 14307 | 16763 | 17234 | 17582 | 17751 | 16919 | 17394 | 19454 | 20110 | 20839 | 20815 | 20679 | 20692 | 23271 | 24061 | 24804 | 24475 | 22731 | 24587 | 25342
7536 | 7536 | 314 | 11 | 10 | Winter | 11 | 9 | Winter | 24 | 13615 | 15775 | 16347 | 16674 | 16876 | 16365 | 16843 | 18582 | 19306 | 20180 | 20129 | 20282 | 20296 | 22620 | 23435 | 24254 | 23860 | 22387 | 23833 | 24745
7537 | 7537 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 1 | 13170 | 15156 | 15733 | 15845 | 15797 | 15656 | 16433 | 18225 | 18806 | 19075 | 19490 | 19014 | 19791 | 22260 | 23157 | 23097 | 23038 | 21842 | 24085 | 24468
7538 | 7538 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 2 | 12799 | 14810 | 15355 | 15454 | 15356 | 15304 | 16194 | 17906 | 18421 | 18603 | 19028 | 18597 | 19511 | 21785 | 22642 | 22507 | 22480 | 21509 | 23637 | 23935
7539 | 7539 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 3 | 12682 | 14668 | 15235 | 15333 | 15178 | 15236 | 16250 | 17829 | 18366 | 18412 | 18822 | 18490 | 19474 | 21584 | 22368 | 22108 | 22100 | 21385 | 23332 | 23656
7540 | 7540 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 4 | 12581 | 14653 | 15182 | 15264 | 15031 | 15067 | 16247 | 17709 | 18114 | 18035 | 18383 | 18045 | 19180 | 20993 | 21736 | 21354 | 21335 | 20922 | 22702 | 22886
7541 | 7541 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 5 | 12613 | 14891 | 15342 | 15492 | 14973 | 15000 | 16483 | 17763 | 18017 | 17722 | 17960 | 17636 | 18997 | 20496 | 21185 | 20519 | 20549 | 20536 | 22144 | 22159
7542 | 7542 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 6 | 12775 | 15568 | 16073 | 16152 | 15288 | 15076 | 17175 | 18237 | 18436 | 17736 | 17659 | 17272 | 19275 | 20498 | 21000 | 20051 | 19903 | 20612 | 22031 | 21921
7543 | 7543 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 7 | 13084 | 16771 | 17408 | 17318 | 16242 | 15358 | 18514 | 19218 | 19487 | 18395 | 17852 | 17165 | 20318 | 21256 | 21582 | 20372 | 19719 | 21520 | 22368 | 22484
7544 | 7544 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 8 | 13635 | 17738 | 18317 | 18197 | 17560 | 15845 | 19577 | 20017 | 20343 | 19550 | 18545 | 17546 | 21261 | 21908 | 22292 | 21359 | 20240 | 22373 | 22743 | 23025
7545 | 7545 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 9 | 14231 | 18008 | 18509 | 18457 | 17919 | 16415 | 19783 | 20243 | 20533 | 19864 | 19122 | 18063 | 21355 | 21922 | 22501 | 21570 | 20688 | 22437 | 22754 | 22979
7546 | 7546 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 10 | 14486 | 17935 | 18379 | 18358 | 17882 | 16616 | 19728 | 20195 | 20397 | 19819 | 19533 | 18282 | 21511 | 21851 | 22625 | 21780 | 21346 | 22637 | 23008 | 22959
7547 | 7547 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 11 | 14574 | 18000 | 18454 | 18336 | 17818 | 16558 | 19586 | 20189 | 20323 | 19695 | 19535 | 18172 | 21799 | 21825 | 22990 | 22156 | 21847 | 22968 | 23530 | 22986
7548 | 7548 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 12 | 14690 | 17951 | 18436 | 18147 | 17805 | 16528 | 19433 | 19947 | 20202 | 19566 | 19435 | 18071 | 21924 | 21725 | 23002 | 22366 | 22070 | 23120 | 23592 | 22900
7549 | 7549 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 13 | 14568 | 17859 | 18287 | 17825 | 17602 | 16400 | 19260 | 19773 | 20014 | 19305 | 19184 | 17906 | 21845 | 21537 | 22721 | 22217 | 21920 | 23045 | 23517 | 22713
7550 | 7550 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 14 | 14377 | 17722 | 18226 | 17650 | 17490 | 16233 | 19176 | 19576 | 19898 | 19204 | 18994 | 17718 | 21625 | 21386 | 22348 | 21959 | 21583 | 22805 | 23131 | 22538
7551 | 7551 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 15 | 14592 | 17856 | 18420 | 17942 | 17537 | 16528 | 19321 | 19724 | 20040 | 19314 | 19086 | 18023 | 21361 | 21495 | 22193 | 21622 | 21250 | 22511 | 22829 | 22630
7552 | 7552 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 16 | 15188 | 18227 | 18855 | 18513 | 17684 | 17125 | 19623 | 20255 | 20342 | 19447 | 19337 | 18566 | 21170 | 21706 | 22163 | 21213 | 21013 | 22259 | 22944 | 22804
7553 | 7553 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 17 | 15800 | 18684 | 19430 | 18975 | 18139 | 17769 | 20089 | 20671 | 20956 | 19778 | 19968 | 19231 | 21643 | 22364 | 22632 | 21560 | 21498 | 22753 | 23220 | 23481
7554 | 7554 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 18 | 16709 | 19359 | 19925 | 19673 | 18898 | 18540 | 20928 | 21166 | 21537 | 20459 | 21025 | 20222 | 22586 | 23117 | 23593 | 22401 | 22754 | 23806 | 23919 | 24356
7555 | 7555 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 19 | 16618 | 19173 | 19668 | 19597 | 18586 | 18525 | 20906 | 21033 | 21456 | 20469 | 21100 | 20505 | 22878 | 23334 | 24152 | 22813 | 23235 | 24272 | 24419 | 24743
7556 | 7556 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 20 | 16292 | 18802 | 19372 | 19323 | 18490 | 18300 | 20898 | 21007 | 21408 | 20670 | 21223 | 20583 | 23280 | 23806 | 24534 | 23508 | 23786 | 24853 | 25076 | 25428
7557 | 7557 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 21 | 15911 | 18325 | 18911 | 18973 | 18251 | 18086 | 20659 | 20826 | 21327 | 20820 | 21517 | 20826 | 23522 | 24244 | 25076 | 24240 | 24577 | 25333 | 25714 | 26135
7558 | 7558 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 22 | 15317 | 17612 | 18239 | 18312 | 17785 | 17613 | 20026 | 20362 | 20960 | 20613 | 21375 | 20651 | 23193 | 24188 | 24972 | 24389 | 24736 | 25149 | 25765 | 26259
7559 | 7559 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 23 | 14592 | 16647 | 17288 | 17364 | 17163 | 17006 | 19099 | 19555 | 20175 | 20172 | 21022 | 20219 | 22447 | 23583 | 24392 | 24132 | 24501 | 24483 | 25239 | 25746
7560 | 7560 | 315 | 11 | 11 | Winter | 11 | 10 | Winter | 24 | 13920 | 15752 | 16343 | 16522 | 16275 | 16414 | 18187 | 18792 | 19426 | 19468 | 20610 | 19785 | 21616 | 22922 | 23795 | 23481 | 24161 | 23695 | 24621 | 25141
7561 | 7561 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 1 | 13703 | 15299 | 15619 | 15618 | 15892 | 16144 | 17896 | 18416 | 19025 | 18994 | 19230 | 19432 | 21759 | 22745 | 22776 | 22819 | 22231 | 24064 | 24470 | 25101
7562 | 7562 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 2 | 13464 | 14950 | 15256 | 15199 | 15470 | 15929 | 17609 | 18070 | 18647 | 18592 | 18801 | 19183 | 21390 | 22257 | 22214 | 22278 | 21716 | 23626 | 23945 | 24547
7563 | 7563 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 3 | 13399 | 14777 | 15082 | 14955 | 15272 | 15923 | 17477 | 17955 | 18547 | 18369 | 18649 | 19138 | 21155 | 21991 | 21814 | 21890 | 21440 | 23314 | 23656 | 24201
7564 | 7564 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 4 | 13460 | 14730 | 15034 | 14842 | 15128 | 15952 | 17409 | 17778 | 18299 | 18018 | 18305 | 18902 | 20736 | 21408 | 21105 | 21161 | 20821 | 22689 | 22894 | 23429
7565 | 7565 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 5 | 13757 | 14875 | 15263 | 14795 | 15064 | 16199 | 17497 | 17729 | 18227 | 17653 | 17877 | 18772 | 20432 | 20907 | 20311 | 20402 | 20081 | 22140 | 22166 | 22702
7566 | 7566 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 6 | 14556 | 15611 | 15970 | 15160 | 15185 | 16942 | 18054 | 18239 | 18585 | 17460 | 17492 | 19125 | 20582 | 20785 | 19898 | 19795 | 19363 | 22049 | 21941 | 22362
7567 | 7567 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 7 | 16064 | 16966 | 17177 | 16144 | 15682 | 18309 | 19109 | 19350 | 19636 | 17723 | 17530 | 20241 | 21148 | 21418 | 20273 | 19645 | 19194 | 22417 | 22520 | 22860
7568 | 7568 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 8 | 17154 | 17871 | 18060 | 17437 | 16513 | 19372 | 19955 | 20221 | 20466 | 18476 | 17956 | 21183 | 21650 | 22146 | 21273 | 20166 | 19510 | 22800 | 23065 | 23517
7569 | 7569 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 9 | 17305 | 18007 | 18260 | 17727 | 17155 | 19499 | 20121 | 20365 | 20658 | 19014 | 18385 | 21244 | 21673 | 22307 | 21438 | 20574 | 19793 | 22758 | 22968 | 23641
7570 | 7570 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 10 | 17284 | 17956 | 18240 | 17781 | 17502 | 19546 | 20180 | 20362 | 20497 | 19560 | 18852 | 21363 | 21833 | 22389 | 21603 | 21191 | 20315 | 22970 | 22910 | 23756
7571 | 7571 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 11 | 17210 | 18173 | 18415 | 17966 | 17535 | 19687 | 20480 | 20663 | 20321 | 19936 | 19199 | 21579 | 22242 | 22685 | 21912 | 21626 | 20706 | 23431 | 22876 | 24108
7572 | 7572 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 12 | 17178 | 18309 | 18412 | 18149 | 17535 | 19785 | 20511 | 20806 | 20002 | 20142 | 19439 | 21700 | 22289 | 22684 | 22111 | 21848 | 20962 | 23480 | 22778 | 24127
7573 | 7573 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 13 | 16906 | 18058 | 18013 | 17875 | 17176 | 19560 | 20295 | 20571 | 19455 | 19863 | 19203 | 21476 | 22054 | 22255 | 21816 | 21552 | 20707 | 23240 | 22427 | 23683
7574 | 7574 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 14 | 16933 | 18088 | 17917 | 17873 | 17122 | 19528 | 20148 | 20551 | 19365 | 19702 | 19068 | 21392 | 21827 | 22015 | 21689 | 21348 | 20530 | 22982 | 22385 | 23412
7575 | 7575 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 15 | 17169 | 18238 | 18138 | 17892 | 17327 | 19513 | 20108 | 20576 | 19780 | 19543 | 19085 | 21266 | 21684 | 22000 | 21490 | 21149 | 20508 | 22814 | 22601 | 23360
7576 | 7576 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 16 | 17505 | 18507 | 18519 | 17892 | 17656 | 19532 | 20290 | 20642 | 20305 | 19410 | 19218 | 21102 | 21857 | 22003 | 21113 | 20929 | 20576 | 22947 | 22792 | 23299
7577 | 7577 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 17 | 18053 | 19027 | 18925 | 18252 | 18279 | 19935 | 20630 | 21108 | 20849 | 19933 | 20016 | 21571 | 22116 | 22471 | 21453 | 21421 | 21414 | 23238 | 23479 | 23795
7578 | 7578 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 18 | 18868 | 19528 | 19589 | 18876 | 19258 | 20785 | 21129 | 21502 | 21506 | 20899 | 21038 | 22469 | 22705 | 23423 | 22284 | 22655 | 22644 | 23928 | 24351 | 24845
7579 | 7579 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 19 | 18706 | 19259 | 19470 | 18526 | 19105 | 20732 | 20942 | 21352 | 21636 | 20865 | 21173 | 22706 | 22991 | 23923 | 22645 | 23094 | 23011 | 24411 | 24733 | 25525
7580 | 7580 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 20 | 18511 | 18903 | 19135 | 18348 | 18724 | 20665 | 20830 | 21184 | 21554 | 20868 | 21203 | 23008 | 23355 | 24212 | 23249 | 23575 | 23454 | 25044 | 25389 | 26007
7581 | 7581 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 21 | 18145 | 18468 | 18802 | 18107 | 18577 | 20433 | 20626 | 21057 | 21550 | 21103 | 21396 | 23199 | 23723 | 24723 | 23963 | 24358 | 24044 | 25713 | 26132 | 26788
7582 | 7582 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 22 | 17309 | 17717 | 18085 | 17573 | 18054 | 19728 | 20074 | 20589 | 21036 | 20867 | 21169 | 22790 | 23536 | 24533 | 24046 | 24438 | 24051 | 25707 | 26207 | 26751
7583 | 7583 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 23 | 16284 | 16745 | 17099 | 16936 | 17500 | 18763 | 19216 | 19757 | 20268 | 20464 | 20661 | 22012 | 22892 | 23918 | 23758 | 24202 | 23675 | 25155 | 25677 | 26215
7584 | 7584 | 316 | 11 | 12 | Winter | 11 | 11 | Winter | 24 | 15269 | 15755 | 16194 | 16004 | 16881 | 17784 | 18378 | 18939 | 19562 | 20001 | 20122 | 21148 | 22194 | 23289 | 23072 | 23828 | 23204 | 24513 | 25056 | 25653
7585 | 7585 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 1 | 14359 | 14580 | 14911 | 15238 | 15662 | 17046 | 17573 | 18090 | 18187 | 18357 | 19018 | 20815 | 21542 | 21892 | 22037 | 21574 | 22027 | 23951 | 24607 | 24229
7586 | 7586 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 2 | 14031 | 14209 | 14482 | 14810 | 15246 | 16735 | 17200 | 17730 | 17754 | 17929 | 18704 | 20449 | 21074 | 21332 | 21493 | 21053 | 21588 | 23413 | 24043 | 23599
7587 | 7587 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 3 | 13869 | 14007 | 14229 | 14576 | 15097 | 16590 | 17087 | 17592 | 17518 | 17801 | 18609 | 20245 | 20885 | 20958 | 21122 | 20799 | 21403 | 23132 | 23693 | 23143
7588 | 7588 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 4 | 13846 | 13957 | 14124 | 14451 | 14960 | 16539 | 16943 | 17408 | 17213 | 17509 | 18358 | 19878 | 20344 | 20288 | 20430 | 20200 | 20890 | 22368 | 22916 | 22278
7589 | 7589 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 5 | 14073 | 14187 | 14094 | 14403 | 14821 | 16666 | 16948 | 17399 | 16954 | 17143 | 18252 | 19647 | 19899 | 19554 | 19718 | 19483 | 20476 | 21657 | 22208 | 21318
7590 | 7590 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 6 | 14768 | 14921 | 14506 | 14582 | 14824 | 17280 | 17531 | 17882 | 17087 | 16841 | 18633 | 19886 | 19982 | 19214 | 19171 | 18803 | 20499 | 21464 | 21888 | 20750
7591 | 7591 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 7 | 16011 | 16140 | 15533 | 15103 | 15201 | 18390 | 18697 | 19006 | 17825 | 16945 | 19754 | 20532 | 20802 | 19638 | 19065 | 18658 | 21347 | 22069 | 22389 | 21031
7592 | 7592 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 8 | 16978 | 16975 | 16807 | 15920 | 15662 | 19237 | 19590 | 19837 | 18993 | 17380 | 20807 | 21066 | 21474 | 20636 | 19579 | 18961 | 22347 | 22620 | 23010 | 21948
7593 | 7593 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 9 | 16904 | 16906 | 16833 | 16282 | 15824 | 19122 | 19473 | 19759 | 18971 | 17564 | 20701 | 20844 | 21177 | 20537 | 19726 | 18981 | 22195 | 22253 | 22859 | 21805
7594 | 7594 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 10 | 16733 | 16760 | 16746 | 16606 | 16075 | 19013 | 19303 | 19627 | 18925 | 17879 | 20544 | 20846 | 20915 | 20551 | 20190 | 19354 | 21921 | 22042 | 22834 | 21855
7595 | 7595 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 11 | 16706 | 16729 | 16737 | 16729 | 16154 | 19090 | 19391 | 19655 | 18971 | 18021 | 20486 | 21038 | 20618 | 20653 | 20420 | 19551 | 21654 | 21802 | 22985 | 22011
7596 | 7596 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 12 | 16703 | 16648 | 16839 | 16856 | 16297 | 19036 | 19440 | 19550 | 19059 | 18170 | 20404 | 20995 | 20412 | 20762 | 20553 | 19715 | 21570 | 21616 | 22913 | 22139
7597 | 7597 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 13 | 16863 | 16640 | 16920 | 16939 | 16422 | 19175 | 19555 | 19481 | 19123 | 18287 | 20320 | 21120 | 20435 | 20811 | 20611 | 19817 | 21457 | 21616 | 22823 | 22180
7598 | 7598 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 14 | 17015 | 16728 | 17111 | 17013 | 16526 | 19226 | 19725 | 19497 | 19249 | 18342 | 20355 | 21093 | 20607 | 20876 | 20596 | 19833 | 21500 | 21752 | 22736 | 22215
7599 | 7599 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 15 | 16964 | 16795 | 16986 | 16821 | 16485 | 19047 | 19603 | 19404 | 18959 | 18195 | 20165 | 20796 | 20690 | 20516 | 20233 | 19651 | 21494 | 21809 | 22530 | 21825
7600 | 7600 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 16 | 17131 | 17186 | 17003 | 16885 | 16771 | 19238 | 19682 | 19557 | 18700 | 18320 | 20183 | 20940 | 20899 | 20136 | 20002 | 19703 | 21580 | 21978 | 22456 | 21377
7601 | 7601 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 17 | 17855 | 17867 | 17655 | 17735 | 17884 | 19886 | 20452 | 20296 | 19236 | 19397 | 21013 | 21488 | 21842 | 20771 | 20780 | 20827 | 22467 | 22953 | 23236 | 22033
7602 | 7602 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 18 | 18624 | 18608 | 18341 | 18787 | 18874 | 20519 | 20954 | 20985 | 19962 | 20462 | 21942 | 22134 | 22676 | 21653 | 22088 | 22141 | 23690 | 23912 | 24370 | 23021
7603 | 7603 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 19 | 18439 | 18471 | 17966 | 18585 | 18785 | 20309 | 20765 | 21039 | 19894 | 20531 | 22166 | 22347 | 22833 | 21965 | 22491 | 22469 | 24217 | 24283 | 25051 | 23507
7604 | 7604 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 20 | 18002 | 18114 | 17744 | 18165 | 18562 | 20144 | 20538 | 20868 | 19963 | 20471 | 22372 | 22636 | 23202 | 22510 | 22912 | 22881 | 24655 | 24928 | 25510 | 24247
7605 | 7605 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 21 | 17518 | 17735 | 17434 | 17945 | 18332 | 19851 | 20299 | 20742 | 20024 | 20542 | 22467 | 22878 | 23565 | 23115 | 23606 | 23395 | 25133 | 25614 | 26253 | 25121
7606 | 7606 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 22 | 16757 | 17026 | 16889 | 17426 | 17853 | 19258 | 19780 | 20203 | 19732 | 20285 | 21978 | 22640 | 23425 | 23152 | 23669 | 23396 | 24869 | 25678 | 26233 | 25326
7607 | 7607 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 23 | 15772 | 16049 | 16247 | 16859 | 17188 | 18386 | 18931 | 19390 | 19245 | 19766 | 21106 | 21971 | 22796 | 22859 | 23422 | 23019 | 24099 | 25168 | 25710 | 25124
7608 | 7608 | 317 | 11 | 13 | Winter | 11 | 12 | Winter | 24 | 14876 | 15224 | 15380 | 16288 | 16496 | 17604 | 18162 | 18702 | 18497 | 19298 | 20180 | 21333 | 22127 | 22252 | 23113 | 22612 | 23188 | 24615 | 25236 | 24582
7609 | 7609 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 1 | 14434 | 14347 | 14971 | 15513 | 15857 | 17138 | 17625 | 17702 | 18047 | 18585 | 20277 | 21033 | 21907 | 21609 | 21294 | 21830 | 23717 | 24520 | 24185 | 23842
7610 | 7610 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 2 | 14099 | 13918 | 14549 | 15076 | 15585 | 16755 | 17257 | 17260 | 17670 | 18287 | 19838 | 20599 | 21458 | 21101 | 20796 | 21424 | 23156 | 23976 | 23571 | 23274
7611 | 7611 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 3 | 13934 | 13652 | 14308 | 14921 | 15488 | 16647 | 17133 | 17045 | 17464 | 18233 | 19640 | 20426 | 21216 | 20738 | 20548 | 21225 | 22866 | 23615 | 23105 | 22833
7612 | 7612 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 4 | 13908 | 13541 | 14187 | 14783 | 15473 | 16520 | 16977 | 16782 | 17192 | 18021 | 19333 | 19950 | 20712 | 20094 | 19984 | 20739 | 22262 | 22856 | 22245 | 22001
7613 | 7613 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 5 | 14051 | 13518 | 14149 | 14649 | 15702 | 16565 | 17024 | 16593 | 16898 | 17980 | 19141 | 19569 | 20280 | 19426 | 19289 | 20343 | 21681 | 22143 | 21274 | 21116
7614 | 7614 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 6 | 14781 | 13917 | 14341 | 14659 | 16415 | 17180 | 17562 | 16798 | 16794 | 18410 | 19436 | 19731 | 20241 | 18936 | 18643 | 20393 | 21599 | 21835 | 20709 | 20401
7615 | 7615 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 7 | 16146 | 14986 | 14907 | 15066 | 17746 | 18415 | 18766 | 17633 | 17135 | 19619 | 20264 | 20636 | 20950 | 18884 | 18531 | 21271 | 22205 | 22368 | 20999 | 20194
7616 | 7616 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 8 | 17083 | 16294 | 15781 | 15581 | 18884 | 19370 | 19659 | 18870 | 17931 | 20726 | 21050 | 21378 | 21688 | 19467 | 18912 | 22300 | 22763 | 23043 | 21968 | 20713
7617 | 7617 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 9 | 17274 | 16641 | 16483 | 16077 | 19139 | 19587 | 19925 | 19204 | 18537 | 20981 | 21209 | 21424 | 21907 | 19946 | 19261 | 22479 | 22811 | 23215 | 22143 | 21147
7618 | 7618 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 10 | 17264 | 16676 | 16909 | 16401 | 19105 | 19457 | 19825 | 19176 | 19112 | 20832 | 21459 | 21336 | 22024 | 20593 | 19814 | 22394 | 23126 | 23380 | 22384 | 21843
7619 | 7619 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 11 | 17316 | 16527 | 16851 | 16259 | 19027 | 19231 | 19504 | 18850 | 19325 | 20345 | 21775 | 21077 | 22155 | 20863 | 20055 | 22172 | 23310 | 23566 | 22584 | 22156
7620 | 7620 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 12 | 17292 | 16454 | 16784 | 16186 | 18885 | 19010 | 19106 | 18633 | 19380 | 19917 | 21751 | 20825 | 22015 | 20934 | 20155 | 22033 | 23047 | 23432 | 22658 | 22235
7621 | 7621 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 13 | 16986 | 16082 | 16402 | 15836 | 18423 | 18633 | 18539 | 18192 | 19053 | 19318 | 21515 | 20424 | 21533 | 20584 | 19848 | 21512 | 22708 | 22939 | 22292 | 21869
7622 | 7622 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 14 | 16998 | 16109 | 16307 | 15770 | 18322 | 18649 | 18409 | 18166 | 18882 | 19211 | 21286 | 20401 | 21285 | 20380 | 19672 | 21358 | 22407 | 22660 | 22135 | 21641
7623 | 7623 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 15 | 17022 | 16140 | 16298 | 15945 | 18301 | 18778 | 18594 | 18167 | 18614 | 19330 | 20873 | 20509 | 21152 | 20044 | 19517 | 21381 | 22007 | 22469 | 21767 | 21284
7624 | 7624 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 16 | 17303 | 16357 | 16570 | 16469 | 18537 | 19138 | 19053 | 18249 | 18518 | 19682 | 20974 | 20768 | 21181 | 19847 | 19597 | 21513 | 22220 | 22419 | 21344 | 21051
7625 | 7625 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 17 | 18093 | 17068 | 17492 | 17662 | 19283 | 20029 | 19921 | 18914 | 19315 | 20653 | 21597 | 21694 | 21923 | 20603 | 20701 | 22373 | 23115 | 23173 | 21981 | 21832
7626 | 7626 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 18 | 18725 | 17886 | 18674 | 18816 | 20286 | 20767 | 20813 | 19841 | 20393 | 21796 | 22170 | 22513 | 22948 | 21920 | 22029 | 23606 | 23976 | 24342 | 22996 | 23236
7627 | 7627 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 19 | 18462 | 17484 | 18447 | 18692 | 20289 | 20559 | 20831 | 19710 | 20289 | 21969 | 22303 | 22590 | 23385 | 22272 | 22315 | 24100 | 24468 | 25011 | 23474 | 23746
7628 | 7628 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 20 | 18096 | 17230 | 17999 | 18464 | 20181 | 20291 | 20614 | 19713 | 20207 | 22090 | 22672 | 22886 | 23598 | 22643 | 22704 | 24514 | 25284 | 25471 | 24223 | 24314
7629 | 7629 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 21 | 17617 | 16916 | 17751 | 18211 | 19915 | 19998 | 20428 | 19689 | 20319 | 22108 | 22961 | 23161 | 24011 | 23269 | 23185 | 24960 | 26063 | 26207 | 25093 | 25200
7630 | 7630 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 22 | 16850 | 16363 | 17199 | 17696 | 19164 | 19416 | 19829 | 19327 | 20035 | 21568 | 22597 | 22957 | 23794 | 23285 | 23145 | 24674 | 25949 | 26173 | 25288 | 25374
7631 | 7631 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 23 | 15869 | 15678 | 16591 | 17011 | 18091 | 18521 | 18958 | 18787 | 19591 | 20649 | 21814 | 22287 | 23137 | 22988 | 22728 | 23873 | 25335 | 25618 | 25063 | 25161
7632 | 7632 | 318 | 11 | 14 | Winter | 11 | 13 | Winter | 24 | 14977 | 14753 | 15950 | 16316 | 17051 | 17672 | 18187 | 18010 | 19188 | 19672 | 20936 | 21602 | 22590 | 22619 | 22267 | 22965 | 24560 | 25076 | 24473 | 24859
7633 | 7633 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 1 | 14246 | 14460 | 15336 | 15780 | 16715 | 17174 | 17302 | 17676 | 18116 | 19816 | 20799 | 21425 | 21657 | 20982 | 21596 | 23534 | 24465 | 24123 | 23842 | 22918
7634 | 7634 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 2 | 13871 | 14056 | 14906 | 15473 | 16265 | 16811 | 16883 | 17281 | 17666 | 19384 | 20397 | 20974 | 21123 | 20496 | 21193 | 22965 | 23910 | 23516 | 23264 | 22379
7635 | 7635 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 3 | 13665 | 13791 | 14718 | 15338 | 16105 | 16655 | 16631 | 17056 | 17561 | 19215 | 20231 | 20743 | 20746 | 20264 | 21006 | 22667 | 23636 | 23049 | 22825 | 22088
7636 | 7636 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 4 | 13624 | 13717 | 14629 | 15333 | 16065 | 16573 | 16459 | 16842 | 17307 | 19013 | 19879 | 20307 | 20149 | 19771 | 20584 | 22104 | 22925 | 22245 | 22032 | 21447
7637 | 7637 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 5 | 13851 | 13702 | 14518 | 15585 | 16197 | 16670 | 16342 | 16623 | 17000 | 18918 | 19620 | 19960 | 19479 | 19143 | 20245 | 21567 | 22315 | 21315 | 21174 | 20636
7638 | 7638 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 6 | 14572 | 13888 | 14545 | 16308 | 16821 | 17251 | 16631 | 16593 | 16725 | 19302 | 19805 | 19997 | 19201 | 18530 | 20318 | 21507 | 22138 | 20759 | 20453 | 19844
7639 | 7639 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 7 | 15805 | 14468 | 14968 | 17661 | 18124 | 18462 | 17521 | 17016 | 16898 | 20241 | 20714 | 20779 | 19697 | 18450 | 21221 | 22148 | 22689 | 21064 | 20248 | 19649
7640 | 7640 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 8 | 16703 | 15361 | 15511 | 18814 | 19187 | 19391 | 18786 | 17873 | 17423 | 21084 | 21752 | 21603 | 20768 | 18856 | 22273 | 22747 | 23471 | 22036 | 20776 | 20011
7641 | 7641 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 9 | 16936 | 16033 | 15982 | 19032 | 19339 | 19615 | 19090 | 18473 | 17936 | 21213 | 21780 | 21809 | 20975 | 19186 | 22434 | 22773 | 23383 | 22187 | 21181 | 20307
7642 | 7642 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 10 | 16857 | 16471 | 16350 | 18954 | 19267 | 19599 | 19167 | 18981 | 18200 | 21403 | 21833 | 21868 | 21125 | 19667 | 22294 | 23037 | 23301 | 22368 | 21811 | 20831
7643 | 7643 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 11 | 16714 | 16692 | 16504 | 18900 | 19147 | 19666 | 19258 | 19212 | 17968 | 21723 | 21892 | 22015 | 21296 | 19923 | 22088 | 23237 | 22991 | 22578 | 22143 | 21127
7644 | 7644 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 12 | 16439 | 16759 | 16580 | 18746 | 18927 | 19476 | 19267 | 19247 | 17763 | 21681 | 21849 | 21838 | 21320 | 20002 | 21928 | 22944 | 22644 | 22627 | 22202 | 21214
7645 | 7645 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 13 | 16115 | 16573 | 16426 | 18412 | 18755 | 19132 | 19055 | 19043 | 17491 | 21578 | 21697 | 21480 | 21089 | 19830 | 21543 | 22728 | 22347 | 22396 | 21971 | 21029
7646 | 7646 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 14 | 16015 | 16446 | 16328 | 18318 | 18658 | 18966 | 18990 | 18876 | 17385 | 21351 | 21652 | 21238 | 20952 | 19649 | 21382 | 22430 | 22362 | 22228 | 21733 | 20824
7647 | 7647 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 15 | 16181 | 16286 | 16334 | 18281 | 18572 | 18929 | 18743 | 18587 | 17506 | 20927 | 21593 | 21071 | 20581 | 19475 | 21386 | 21993 | 22645 | 21837 | 21353 | 20631
7648 | 7648 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 16 | 16817 | 16509 | 16805 | 18622 | 19099 | 19266 | 18682 | 18612 | 18055 | 21123 | 21712 | 21192 | 20332 | 19655 | 21600 | 22284 | 23111 | 21511 | 21209 | 20783
7649 | 7649 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 17 | 17526 | 17346 | 17893 | 19368 | 19970 | 20004 | 19195 | 19404 | 19268 | 21745 | 22428 | 21916 | 20932 | 20748 | 22437 | 23174 | 23881 | 22123 | 21980 | 21893
7650 | 7650 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 18 | 18282 | 18329 | 18825 | 20296 | 20663 | 20655 | 19835 | 20377 | 20483 | 22169 | 23048 | 22808 | 21731 | 21964 | 23587 | 23939 | 24734 | 23066 | 23298 | 23201
7651 | 7651 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 19 | 18124 | 18084 | 18674 | 20275 | 20446 | 20629 | 19654 | 20216 | 20496 | 22226 | 23026 | 23169 | 21972 | 22209 | 24033 | 24407 | 25168 | 23544 | 23811 | 23565
7652 | 7652 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 20 | 17780 | 17592 | 18409 | 20135 | 20449 | 20379 | 19581 | 20053 | 20384 | 22529 | 23331 | 23305 | 22440 | 22542 | 24403 | 25172 | 25918 | 24269 | 24371 | 24055
7653 | 7653 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 21 | 17396 | 17319 | 18123 | 19837 | 20279 | 20133 | 19476 | 20069 | 20380 | 22727 | 23611 | 23600 | 22958 | 22955 | 24804 | 25895 | 26725 | 25113 | 25236 | 24669
7654 | 7654 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 22 | 16647 | 16764 | 17572 | 19050 | 19532 | 19481 | 19050 | 19706 | 20042 | 22268 | 23380 | 23300 | 22923 | 22871 | 24472 | 25740 | 26795 | 25280 | 25389 | 24714
7655 | 7655 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 23 | 15659 | 16149 | 16866 | 17968 | 18570 | 18579 | 18466 | 19219 | 19492 | 21448 | 22660 | 22619 | 22593 | 22444 | 23666 | 25104 | 26213 | 25045 | 25178 | 24348
7656 | 7656 | 319 | 11 | 15 | Winter | 11 | 14 | Winter | 24 | 14760 | 15447 | 16128 | 16839 | 17485 | 17755 | 17632 | 18699 | 18935 | 20522 | 21873 | 21980 | 21907 | 21951 | 22733 | 24256 | 25510 | 24427 | 24850 | 23910
7657 | 7657 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 1 | 13683 | 14557 | 15272 | 16107 | 16794 | 16560 | 16986 | 17407 | 18019 | 19966 | 20722 | 20729 | 21061 | 20966 | 22922 | 23824 | 24472 | 23471 | 22617 | 22887
7658 | 7658 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 2 | 13301 | 14157 | 14979 | 15699 | 16408 | 16154 | 16605 | 17007 | 17754 | 19609 | 20252 | 20248 | 20580 | 20588 | 22390 | 23309 | 23887 | 22920 | 22097 | 22467
7659 | 7659 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 3 | 13037 | 13940 | 14844 | 15514 | 16266 | 15906 | 16390 | 16883 | 17685 | 19480 | 20063 | 19918 | 20250 | 20433 | 22114 | 23067 | 23556 | 22496 | 21818 | 22260
7660 | 7660 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 4 | 12951 | 13822 | 14821 | 15494 | 16167 | 15739 | 16193 | 16680 | 17543 | 19173 | 19655 | 19386 | 19671 | 20024 | 21560 | 22364 | 22802 | 21702 | 21157 | 21709
7661 | 7661 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 5 | 12967 | 13725 | 15094 | 15669 | 16288 | 15678 | 16045 | 16442 | 17573 | 19007 | 19300 | 18826 | 19100 | 19741 | 21084 | 21822 | 22034 | 20870 | 20366 | 21255
7662 | 7662 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 6 | 13371 | 13767 | 15836 | 16339 | 16859 | 16014 | 16091 | 16259 | 18063 | 19278 | 19264 | 18644 | 18663 | 19855 | 21075 | 21685 | 21562 | 20173 | 19581 | 21210
7663 | 7663 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 7 | 14488 | 14218 | 17224 | 17697 | 18090 | 16950 | 16597 | 16503 | 19328 | 20271 | 20052 | 19235 | 18694 | 20797 | 21777 | 22287 | 22090 | 19996 | 19402 | 22047
7664 | 7664 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 8 | 15796 | 14784 | 18388 | 18775 | 19300 | 18218 | 17478 | 17067 | 20510 | 21349 | 21041 | 20339 | 19312 | 21883 | 22383 | 23101 | 22949 | 20526 | 19762 | 23097
7665 | 7665 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 9 | 15994 | 15172 | 18509 | 18791 | 19372 | 18417 | 17980 | 17472 | 20630 | 21301 | 21245 | 20453 | 19675 | 21948 | 22312 | 22915 | 23040 | 20823 | 19949 | 23120
7666 | 7666 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 10 | 16108 | 15603 | 18484 | 18872 | 19385 | 18535 | 18536 | 17955 | 20642 | 21394 | 21316 | 20644 | 20304 | 21846 | 22623 | 22883 | 23167 | 21509 | 20534 | 23057
7667 | 7667 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 11 | 16177 | 15760 | 18427 | 19021 | 19355 | 18605 | 18748 | 18146 | 20628 | 21438 | 21356 | 20789 | 20574 | 21630 | 22804 | 22550 | 23262 | 21829 | 20821 | 22875
7668 | 7668 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 12 | 16287 | 15892 | 18369 | 19084 | 19390 | 18699 | 18868 | 18296 | 20541 | 21473 | 21336 | 20897 | 20711 | 21554 | 22593 | 22289 | 23257 | 21973 | 20994 | 22798
7669 | 7669 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 13 | 16359 | 16016 | 18296 | 19255 | 19500 | 18748 | 18924 | 18393 | 20444 | 21583 | 21301 | 20936 | 20757 | 21430 | 22653 | 22274 | 23209 | 22003 | 21069 | 22662
7670 | 7670 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 14 | 16335 | 15892 | 18183 | 19135 | 19474 | 18671 | 18741 | 18232 | 20257 | 21522 | 21146 | 20789 | 20528 | 21251 | 22340 | 22272 | 23003 | 21743 | 20841 | 22457
7671 | 7671 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 15 | 16191 | 15868 | 18129 | 18882 | 19487 | 18415 | 18434 | 18085 | 20053 | 21429 | 20929 | 20406 | 20137 | 21222 | 21869 | 22535 | 22734 | 21325 | 20610 | 22406
7672 | 7672 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 16 | 16291 | 16281 | 18417 | 19140 | 19710 | 18317 | 18398 | 18288 | 20119 | 21479 | 20884 | 20084 | 19937 | 21366 | 22092 | 22912 | 22572 | 21085 | 20664 | 22520
7673 | 7673 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 17 | 16810 | 17267 | 19056 | 19809 | 20355 | 18739 | 19088 | 19238 | 20804 | 22086 | 21611 | 20575 | 20571 | 22104 | 22878 | 23585 | 23330 | 21748 | 21673 | 23279
7674 | 7674 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 18 | 17395 | 18143 | 19930 | 20365 | 20994 | 19366 | 20019 | 20187 | 21591 | 22637 | 22443 | 21292 | 21737 | 23186 | 23579 | 24378 | 24395 | 23043 | 22937 | 24452
7675 | 7675 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 19 | 16971 | 17969 | 19879 | 20112 | 20743 | 19146 | 19805 | 20135 | 21690 | 22518 | 22567 | 21458 | 22025 | 23583 | 23998 | 24773 | 24804 | 23541 | 23300 | 24972
7676 | 7676 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 20 | 16663 | 17659 | 19700 | 20039 | 20512 | 19012 | 19565 | 19938 | 21734 | 22700 | 22636 | 21816 | 22306 | 23895 | 24697 | 25449 | 25375 | 24068 | 23770 | 25429
7677 | 7677 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 21 | 16322 | 17332 | 19366 | 19814 | 20282 | 18837 | 19496 | 19848 | 21660 | 22870 | 22872 | 22218 | 22835 | 24222 | 25345 | 26189 | 26114 | 24905 | 24364 | 25950
7678 | 7678 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 22 | 15769 | 16782 | 18564 | 19054 | 19685 | 18377 | 19086 | 19476 | 21066 | 22588 | 22595 | 22130 | 22790 | 23863 | 25168 | 26238 | 26129 | 25053 | 24413 | 25720
7679 | 7679 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 23 | 15063 | 16065 | 17461 | 18057 | 18739 | 17760 | 18563 | 18870 | 20108 | 21825 | 21979 | 21750 | 22462 | 23043 | 24515 | 25627 | 25669 | 24845 | 24048 | 24957
7680 | 7680 | 320 | 11 | 16 | Winter | 11 | 15 | Winter | 24 | 14145 | 15336 | 16334 | 16982 | 17792 | 16916 | 18030 | 18299 | 19111 | 21041 | 21267 | 21062 | 22081 | 22122 | 23661 | 24951 | 25036 | 24528 | 23628 | 24076
7681 | 7681 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 1 | 13544 | 14563 | 15606 | 16327 | 16574 | 16354 | 16885 | 17444 | 18897 | 19931 | 20067 | 20311 | 20285 | 22309 | 23265 | 23940 | 23848 | 22363 | 22663 | 24513
7682 | 7682 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 2 | 13169 | 14249 | 15192 | 15923 | 16144 | 15963 | 16465 | 17167 | 18484 | 19478 | 19589 | 19853 | 19814 | 21782 | 22753 | 23362 | 23216 | 21832 | 22229 | 23924
7683 | 7683 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 3 | 12930 | 14111 | 15003 | 15773 | 16002 | 15744 | 16344 | 17104 | 18343 | 19328 | 19409 | 19555 | 19624 | 21534 | 22537 | 23055 | 22895 | 21566 | 22028 | 23603
7684 | 7684 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 4 | 12854 | 14112 | 15005 | 15701 | 15899 | 15591 | 16187 | 17014 | 18185 | 19010 | 19003 | 19057 | 19164 | 21042 | 21910 | 22350 | 22132 | 20930 | 21497 | 22940
7685 | 7685 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 5 | 12856 | 14379 | 15188 | 15840 | 15919 | 15483 | 15986 | 17093 | 18170 | 18735 | 18703 | 18563 | 18597 | 20613 | 21409 | 21624 | 21414 | 20148 | 21039 | 22298
7686 | 7686 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 6 | 13070 | 15167 | 15892 | 16475 | 16392 | 15606 | 15892 | 17690 | 18661 | 18825 | 18847 | 18258 | 18071 | 20689 | 21352 | 21229 | 21073 | 19409 | 21026 | 22170
7687 | 7687 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 7 | 13663 | 16548 | 17278 | 17714 | 17526 | 16147 | 16182 | 18997 | 19677 | 19682 | 19872 | 18352 | 18036 | 21428 | 21987 | 21771 | 21719 | 19230 | 21858 | 22745
7688 | 7688 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 8 | 14514 | 17688 | 18366 | 18908 | 18563 | 17001 | 16747 | 20177 | 20525 | 20695 | 21063 | 18973 | 18441 | 22047 | 22801 | 22631 | 22793 | 19573 | 22894 | 23257
7689 | 7689 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 9 | 15241 | 18007 | 18555 | 19149 | 18923 | 17667 | 17330 | 20478 | 20724 | 21076 | 21286 | 19522 | 18842 | 22152 | 22799 | 22881 | 22989 | 19929 | 23085 | 23322
7690 | 7690 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 10 | 15707 | 17950 | 18576 | 19118 | 18893 | 18168 | 17755 | 20444 | 20914 | 21089 | 21308 | 20106 | 19340 | 22406 | 22715 | 22962 | 23079 | 20462 | 22971 | 23628
7691 | 7691 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 11 | 15984 | 17950 | 18771 | 19152 | 18906 | 18427 | 17993 | 20489 | 21260 | 21182 | 21310 | 20431 | 19635 | 22633 | 22437 | 23117 | 23136 | 20804 | 22848 | 23919
7692 | 7692 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 12 | 16114 | 17856 | 18808 | 19153 | 18845 | 18512 | 18105 | 20363 | 21273 | 21118 | 21267 | 20527 | 19767 | 22391 | 22148 | 23085 | 23127 | 20938 | 22726 | 23681
7693 | 7693 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 13 | 15974 | 17592 | 18773 | 19055 | 18612 | 18363 | 17995 | 20059 | 21215 | 20878 | 21054 | 20370 | 19640 | 22232 | 21914 | 22830 | 22891 | 20807 | 22389 | 23514
7694 | 7694 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 14 | 15753 | 17420 | 18608 | 18978 | 18466 | 18123 | 17774 | 19824 | 20908 | 20668 | 20863 | 20079 | 19367 | 21863 | 21849 | 22559 | 22647 | 20515 | 22119 | 23106
7695 | 7695 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 15 | 15601 | 17422 | 18431 | 19053 | 18447 | 17881 | 17691 | 19684 | 20520 | 20501 | 20582 | 19734 | 19211 | 21444 | 22158 | 22335 | 22324 | 20327 | 22111 | 22651
7696 | 7696 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 16 | 15802 | 17782 | 18718 | 19366 | 18697 | 17931 | 17975 | 19843 | 20716 | 20525 | 20475 | 19609 | 19365 | 21734 | 22590 | 22241 | 22118 | 20430 | 22273 | 22889
7697 | 7697 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 17 | 16526 | 18399 | 19376 | 20008 | 19442 | 18615 | 18912 | 20516 | 21227 | 21226 | 21174 | 20221 | 20338 | 22488 | 23232 | 22967 | 22853 | 21418 | 23012 | 23669
7698 | 7698 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 18 | 17521 | 19319 | 20036 | 20745 | 20168 | 19633 | 19916 | 21348 | 21677 | 22066 | 22125 | 21395 | 21565 | 23235 | 24072 | 24079 | 24114 | 22751 | 24242 | 24497
7699 | 7699 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 19 | 17224 | 19223 | 19741 | 20426 | 19932 | 19368 | 19801 | 21361 | 21629 | 22072 | 22405 | 21580 | 21711 | 23571 | 24389 | 24415 | 24764 | 23079 | 24729 | 25004
7700 | 7700 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 20 | 16727 | 19064 | 19679 | 20185 | 19739 | 19124 | 19605 | 21382 | 21877 | 22086 | 22655 | 21807 | 22016 | 24255 | 25056 | 24994 | 25363 | 23584 | 25233 | 25885
7701 | 7701 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 21 | 16401 | 18693 | 19394 | 19881 | 19467 | 18976 | 19434 | 21214 | 21941 | 22189 | 22965 | 22214 | 22323 | 24804 | 25704 | 25659 | 26177 | 24143 | 25728 | 26689
7702 | 7702 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 22 | 15877 | 17893 | 18618 | 19266 | 18906 | 18533 | 19026 | 20587 | 21452 | 21860 | 22643 | 22127 | 22224 | 24594 | 25724 | 25658 | 26170 | 24193 | 25503 | 26640
7703 | 7703 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 23 | 15248 | 16777 | 17594 | 18299 | 18062 | 17972 | 18382 | 19590 | 20577 | 21204 | 21883 | 21764 | 21763 | 23918 | 25090 | 25176 | 25567 | 23817 | 24723 | 26035
7704 | 7704 | 321 | 11 | 17 | Winter | 11 | 16 | Winter | 24 | 14560 | 15642 | 16490 | 17332 | 17150 | 17401 | 17774 | 18556 | 19645 | 20476 | 20934 | 21355 | 21279 | 23048 | 24396 | 24530 | 24725 | 23381 | 23836 | 25214
7705 | 7705 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 1 | 13704 | 14786 | 15797 | 16037 | 15961 | 16278 | 16866 | 18182 | 19058 | 19227 | 19870 | 19599 | 20310 | 22579 | 23317 | 23275 | 23478 | 22364 | 24195 | 24829
7706 | 7706 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 2 | 13334 | 14412 | 15418 | 15626 | 15543 | 15875 | 16607 | 17791 | 18730 | 18796 | 19414 | 19175 | 19957 | 22115 | 22779 | 22684 | 22870 | 21953 | 23634 | 24305
7707 | 7707 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 3 | 13126 | 14220 | 15249 | 15468 | 15396 | 15743 | 16540 | 17655 | 18614 | 18651 | 19161 | 19004 | 19828 | 21911 | 22494 | 22378 | 22502 | 21759 | 23330 | 24036
7708 | 7708 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 4 | 13032 | 14209 | 15193 | 15388 | 15297 | 15611 | 16485 | 17554 | 18386 | 18329 | 18669 | 18605 | 19482 | 21333 | 21839 | 21659 | 21660 | 21245 | 22683 | 23279
7709 | 7709 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 5 | 12927 | 14393 | 15340 | 15425 | 15428 | 15437 | 16604 | 17591 | 18285 | 18112 | 18102 | 18097 | 19239 | 20888 | 21158 | 20980 | 20660 | 20796 | 22043 | 22614
7710 | 7710 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 6 | 12995 | 15108 | 15972 | 15931 | 16021 | 15371 | 17256 | 18146 | 18662 | 18351 | 17626 | 17643 | 19431 | 20889 | 20810 | 20678 | 19737 | 20793 | 21912 | 22384
7711 | 7711 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 7 | 13431 | 16502 | 17214 | 17084 | 17308 | 15682 | 18607 | 19229 | 19714 | 19448 | 17633 | 17671 | 20396 | 21574 | 21382 | 21351 | 19490 | 21619 | 22474 | 22872
7712 | 7712 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 8 | 13985 | 17629 | 18389 | 18117 | 18620 | 16250 | 19799 | 20149 | 20796 | 20672 | 18381 | 18107 | 21482 | 22410 | 22250 | 22445 | 20088 | 22641 | 22999 | 23600
7713 | 7713 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 9 | 14556 | 17809 | 18644 | 18472 | 18903 | 16831 | 20110 | 20380 | 20939 | 20914 | 18914 | 18535 | 21730 | 22436 | 22521 | 22655 | 20540 | 22849 | 23079 | 23547
7714 | 7714 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 10 | 15019 | 17889 | 18696 | 18510 | 18941 | 17317 | 20140 | 20614 | 21057 | 21000 | 19347 | 19093 | 21654 | 22426 | 22672 | 22810 | 20867 | 22810 | 23459 | 23579
7715 | 7715 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 11 | 15349 | 18172 | 18839 | 18640 | 18975 | 17654 | 20284 | 21061 | 21260 | 21105 | 19636 | 19495 | 21603 | 22247 | 22929 | 22977 | 20761 | 22793 | 23854 | 23443
7716 | 7716 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 12 | 15490 | 18276 | 18904 | 18639 | 18975 | 17823 | 20216 | 21124 | 21312 | 21120 | 19717 | 19676 | 21539 | 22001 | 22938 | 23010 | 20581 | 22733 | 23666 | 23209
7717 | 7717 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 13 | 15629 | 18454 | 19020 | 18634 | 18995 | 17927 | 20126 | 21290 | 21434 | 21121 | 19626 | 19774 | 21428 | 21990 | 22897 | 23003 | 20366 | 22604 | 23709 | 23182
7718 | 7718 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 14 | 15476 | 18360 | 18988 | 18548 | 18911 | 17755 | 19942 | 21045 | 21352 | 20980 | 19453 | 19555 | 21227 | 21973 | 22673 | 22811 | 20191 | 22377 | 23346 | 23147
7719 | 7719 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 15 | 15496 | 18232 | 19089 | 18557 | 18778 | 17703 | 19833 | 20685 | 21323 | 20716 | 19223 | 19404 | 21254 | 22292 | 22463 | 22491 | 20205 | 22378 | 22904 | 23452
7720 | 7720 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 16 | 15686 | 18239 | 19155 | 18555 | 18623 | 17742 | 19743 | 20587 | 21170 | 20347 | 19030 | 19280 | 21173 | 22459 | 22101 | 22004 | 20231 | 22258 | 22861 | 23576
7721 | 7721 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 17 | 16469 | 18721 | 19627 | 19116 | 19098 | 18510 | 20239 | 20918 | 21579 | 20860 | 19519 | 20054 | 21701 | 22914 | 22656 | 22547 | 21015 | 22812 | 23463 | 24074
7722 | 7722 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 18 | 17270 | 19300 | 20301 | 19730 | 19924 | 19432 | 20956 | 21272 | 22071 | 21646 | 20293 | 21111 | 22706 | 23615 | 23635 | 23682 | 22164 | 23933 | 24182 | 24885
7723 | 7723 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 19 | 17101 | 19011 | 20003 | 19498 | 19920 | 19329 | 20969 | 21202 | 21886 | 21874 | 20267 | 21232 | 23052 | 23902 | 23964 | 24332 | 22490 | 24445 | 24698 | 25367
7724 | 7724 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 20 | 16751 | 18833 | 19643 | 19199 | 19686 | 19027 | 20871 | 21304 | 21947 | 21936 | 20388 | 21393 | 23289 | 24426 | 24410 | 24807 | 23026 | 24872 | 25513 | 26113
7725 | 7725 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 21 | 16411 | 18542 | 19330 | 18923 | 19535 | 18839 | 20676 | 21313 | 22022 | 22161 | 20666 | 21656 | 23558 | 25025 | 25031 | 25603 | 23783 | 25386 | 26336 | 26992
7726 | 7726 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 22 | 15855 | 17757 | 18679 | 18332 | 18877 | 18388 | 20000 | 20751 | 21679 | 21768 | 20648 | 21494 | 23177 | 24996 | 24988 | 25553 | 24042 | 25145 | 26274 | 27145
7727 | 7727 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 23 | 15151 | 16740 | 17721 | 17507 | 17916 | 17755 | 19008 | 19874 | 20895 | 21014 | 20371 | 21034 | 22343 | 24378 | 24531 | 24973 | 23940 | 24393 | 25702 | 26598
7728 | 7728 | 322 | 11 | 18 | Winter | 11 | 17 | Winter | 24 | 14412 | 15635 | 16730 | 16576 | 16804 | 17116 | 17941 | 18898 | 20081 | 20048 | 19845 | 20530 | 21401 | 23671 | 23871 | 24118 | 23491 | 23498 | 24903 | 25954
7729 | 7729 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 1 | 13637 | 14993 | 15510 | 15453 | 15877 | 16259 | 17518 | 18326 | 18929 | 19059 | 18262 | 19618 | 21495 | 22603 | 22657 | 22926 | 21323 | 23868 | 24557 | 24969
7730 | 7730 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 2 | 13340 | 14582 | 15063 | 14989 | 15429 | 15951 | 17084 | 17956 | 18489 | 18581 | 17811 | 19259 | 20988 | 22058 | 22054 | 22299 | 20795 | 23281 | 24009 | 24358
7731 | 7731 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 3 | 13203 | 14402 | 14893 | 14835 | 15212 | 15876 | 16953 | 17853 | 18349 | 18377 | 17648 | 19151 | 20764 | 21789 | 21761 | 21952 | 20501 | 22979 | 23737 | 24005
7732 | 7732 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 4 | 13256 | 14376 | 14859 | 14790 | 15045 | 15874 | 16924 | 17715 | 18138 | 17992 | 17239 | 18894 | 20370 | 21221 | 21124 | 21173 | 19823 | 22375 | 23004 | 23242
7733 | 7733 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 5 | 13534 | 14548 | 14929 | 14959 | 14833 | 16038 | 17032 | 17694 | 17948 | 17520 | 16703 | 18725 | 20011 | 20614 | 20512 | 20224 | 19008 | 21770 | 22358 | 22412
7734 | 7734 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 6 | 14335 | 15194 | 15486 | 15604 | 14743 | 16740 | 17669 | 18157 | 18133 | 17148 | 16245 | 19004 | 20156 | 20344 | 20279 | 19354 | 18269 | 21672 | 22158 | 21922
7735 | 7735 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 7 | 15722 | 16460 | 16695 | 16933 | 15148 | 18136 | 18849 | 19289 | 19065 | 17246 | 16344 | 20048 | 20952 | 20981 | 21013 | 19151 | 18059 | 22276 | 22683 | 22419
7736 | 7736 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 8 | 16851 | 17650 | 17747 | 18253 | 16096 | 19337 | 19826 | 20423 | 20119 | 18066 | 17235 | 21181 | 21627 | 21890 | 22135 | 19789 | 18748 | 22837 | 23427 | 23263
7737 | 7737 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 9 | 17207 | 17965 | 18121 | 18546 | 16689 | 19653 | 20077 | 20607 | 20531 | 18642 | 17869 | 21469 | 21773 | 22179 | 22369 | 20268 | 19278 | 22922 | 23397 | 23518
7738 | 7738 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 10 | 17316 | 18034 | 18163 | 18564 | 17085 | 19625 | 20230 | 20647 | 20683 | 18970 | 18340 | 21463 | 22160 | 22400 | 22595 | 20661 | 19970 | 23370 | 23506 | 23774
7739 | 7739 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 11 | 17374 | 18037 | 18132 | 18409 | 17245 | 19532 | 20407 | 20577 | 20838 | 18956 | 18604 | 21365 | 22448 | 22610 | 22715 | 20507 | 20550 | 23719 | 23328 | 24040
7740 | 7740 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 12 | 17336 | 18083 | 18126 | 18403 | 17292 | 19450 | 20453 | 20610 | 20817 | 19011 | 18840 | 21287 | 22239 | 22609 | 22748 | 20318 | 20808 | 23524 | 23086 | 24064
7741 | 7741 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 13 | 17250 | 18127 | 18071 | 18373 | 17164 | 19310 | 20560 | 20666 | 20745 | 18861 | 18826 | 21126 | 22258 | 22521 | 22688 | 20053 | 20794 | 23528 | 23025 | 23970
7742 | 7742 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 14 | 17169 | 18147 | 18049 | 18359 | 17097 | 19199 | 20399 | 20666 | 20636 | 18769 | 18821 | 20968 | 21988 | 22337 | 22530 | 19916 | 20731 | 23196 | 23016 | 23752
7743 | 7743 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 15 | 17194 | 18365 | 18214 | 18407 | 17005 | 19305 | 20272 | 20880 | 20515 | 18795 | 18901 | 21023 | 21603 | 22155 | 22237 | 19954 | 20551 | 22776 | 23340 | 23536
7744 | 7744 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 16 | 17245 | 18497 | 18286 | 18346 | 16974 | 19332 | 20274 | 20869 | 20257 | 18737 | 18968 | 20924 | 21582 | 21775 | 21729 | 19954 | 20405 | 22702 | 23436 | 23086
7745 | 7745 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 17 | 17676 | 18995 | 18867 | 18850 | 17568 | 19863 | 20637 | 21308 | 20786 | 19241 | 19690 | 21460 | 22161 | 22345 | 22293 | 20751 | 21070 | 23316 | 23930 | 23675
7746 | 7746 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 18 | 18476 | 19702 | 19462 | 19689 | 18279 | 20615 | 21027 | 21822 | 21498 | 19962 | 20352 | 22411 | 22778 | 23293 | 23402 | 21875 | 21891 | 24038 | 24736 | 24731
7747 | 7747 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 19 | 18421 | 19395 | 19200 | 19650 | 17877 | 20610 | 20918 | 21578 | 21466 | 19845 | 20197 | 22703 | 23080 | 23561 | 24003 | 22173 | 22123 | 24548 | 25201 | 25180
7748 | 7748 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 20 | 18208 | 19022 | 18911 | 19417 | 17669 | 20531 | 21010 | 21597 | 21357 | 19921 | 20349 | 22911 | 23669 | 23996 | 24467 | 22717 | 22630 | 25390 | 25983 | 25803
7749 | 7749 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 21 | 17820 | 18636 | 18570 | 19187 | 17449 | 20260 | 20913 | 21546 | 21351 | 20061 | 20658 | 23076 | 24127 | 24513 | 25165 | 23390 | 23338 | 26164 | 26817 | 26593
7750 | 7750 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 22 | 17020 | 17978 | 17977 | 18529 | 17129 | 19562 | 20311 | 21164 | 20978 | 20003 | 20576 | 22657 | 23893 | 24453 | 25095 | 23641 | 23515 | 26104 | 26981 | 26678
7751 | 7751 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 23 | 15911 | 16991 | 17105 | 17545 | 16659 | 18530 | 19375 | 20318 | 20296 | 19674 | 20086 | 21786 | 23201 | 23933 | 24475 | 23519 | 23141 | 25502 | 26412 | 26248
7752 | 7752 | 323 | 11 | 19 | Winter | 11 | 18 | Winter | 24 | 14780 | 15989 | 16145 | 16421 | 15967 | 17438 | 18366 | 19467 | 19542 | 19134 | 19451 | 20838 | 22316 | 23268 | 23611 | 23043 | 22573 | 24669 | 25755 | 25648
7753 | 7753 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 1 | 14331 | 15194 | 15475 | 15915 | 15413 | 17344 | 18172 | 18704 | 18762 | 18091 | 18868 | 21265 | 22286 | 22481 | 22864 | 21376 | 21908 | 24732 | 25187 | 24847
7754 | 7754 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 2 | 13953 | 14766 | 15020 | 15452 | 14956 | 16913 | 17800 | 18262 | 18302 | 17670 | 18480 | 20771 | 21809 | 21899 | 22254 | 20857 | 21422 | 24183 | 24586 | 24197
7755 | 7755 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 3 | 13773 | 14563 | 14853 | 15238 | 14787 | 16774 | 17704 | 18139 | 18182 | 17538 | 18385 | 20577 | 21627 | 21629 | 21927 | 20578 | 21235 | 23925 | 24244 | 23849
7756 | 7756 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 4 | 13753 | 14488 | 14773 | 15034 | 14559 | 16718 | 17551 | 17925 | 17925 | 17129 | 18128 | 20201 | 21102 | 21005 | 21151 | 19886 | 20717 | 23187 | 23460 | 23018
7757 | 7757 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 5 | 13956 | 14569 | 14968 | 14856 | 14315 | 16876 | 17594 | 17819 | 17797 | 16670 | 17916 | 19914 | 20731 | 20453 | 20252 | 19102 | 20185 | 22559 | 22639 | 22247
7758 | 7758 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 6 | 14654 | 15121 | 15610 | 14766 | 14123 | 17520 | 18078 | 18058 | 18103 | 16231 | 18033 | 20114 | 20776 | 20257 | 19406 | 18373 | 19964 | 22352 | 22132 | 21821
7759 | 7759 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 7 | 16075 | 16335 | 16970 | 15198 | 14428 | 18748 | 19261 | 19077 | 19280 | 16387 | 18857 | 20976 | 21522 | 21024 | 19230 | 18183 | 20579 | 22870 | 22622 | 22443
7760 | 7760 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 8 | 17227 | 17353 | 18293 | 16143 | 15465 | 19747 | 20433 | 20143 | 20560 | 17306 | 20006 | 21711 | 22431 | 22178 | 19891 | 18894 | 21604 | 23649 | 23447 | 23521
7761 | 7761 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 9 | 17382 | 17704 | 18577 | 16716 | 16207 | 19974 | 20618 | 20561 | 20806 | 17961 | 20382 | 21857 | 22472 | 22397 | 20358 | 19411 | 21830 | 23612 | 23684 | 23700
7762 | 7762 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 10 | 17478 | 17859 | 18720 | 17127 | 16672 | 20250 | 20800 | 20728 | 20823 | 18603 | 20692 | 22261 | 22551 | 22643 | 20770 | 20130 | 22024 | 23738 | 23973 | 23988
7763 | 7763 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 11 | 17575 | 17849 | 18584 | 17130 | 16917 | 20420 | 20740 | 20655 | 20614 | 18871 | 20783 | 22505 | 22304 | 22728 | 20582 | 20677 | 21923 | 23530 | 24210 | 24128
7764 | 7764 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 12 | 17645 | 17722 | 18424 | 16992 | 17105 | 20246 | 20528 | 20368 | 20569 | 18811 | 20660 | 22264 | 22010 | 22722 | 20357 | 20905 | 21807 | 23252 | 24191 | 24130
7765 | 7765 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 13 | 17821 | 17682 | 18403 | 16854 | 17144 | 20338 | 20559 | 20257 | 20565 | 18755 | 20662 | 22335 | 22005 | 22712 | 20142 | 20937 | 21807 | 23238 | 24149 | 24112
7766 | 7766 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 14 | 17750 | 17606 | 18332 | 16735 | 17123 | 20121 | 20486 | 20102 | 20460 | 18672 | 20635 | 22017 | 21978 | 22519 | 19968 | 20816 | 21791 | 23188 | 23896 | 23898
7767 | 7767 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 15 | 17714 | 17657 | 18253 | 16657 | 17187 | 19841 | 20521 | 20014 | 20409 | 18537 | 20515 | 21605 | 22277 | 22190 | 19967 | 20598 | 21867 | 23470 | 23638 | 23538
7768 | 7768 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 16 | 17866 | 17869 | 18325 | 16864 | 17488 | 19980 | 20643 | 20049 | 20306 | 18723 | 20570 | 21697 | 22537 | 21817 | 20094 | 20577 | 22012 | 23683 | 23316 | 23101
7769 | 7769 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 17 | 18360 | 18497 | 18897 | 17561 | 18228 | 20469 | 21210 | 20727 | 20839 | 19583 | 21400 | 22280 | 23005 | 22367 | 20876 | 21238 | 22885 | 24167 | 23888 | 23665
7770 | 7770 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 18 | 18953 | 19169 | 19818 | 18399 | 18964 | 21061 | 21930 | 21608 | 21604 | 20427 | 22375 | 22863 | 23667 | 23453 | 21981 | 22051 | 24066 | 24966 | 24941 | 24854
7771 | 7771 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 19 | 18668 | 18888 | 19747 | 17960 | 18648 | 20924 | 21639 | 21514 | 21762 | 20200 | 22323 | 23079 | 23892 | 23976 | 22224 | 22234 | 24238 | 25404 | 25373 | 25561
7772 | 7772 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 20 | 18497 | 18578 | 19471 | 17721 | 18359 | 20962 | 21597 | 21318 | 21773 | 20262 | 22437 | 23577 | 24381 | 24380 | 22703 | 22702 | 24760 | 26171 | 25971 | 26174
7773 | 7773 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 21 | 18184 | 18256 | 19234 | 17497 | 18290 | 20837 | 21494 | 21254 | 21896 | 20506 | 22630 | 23987 | 24891 | 25025 | 23351 | 23406 | 25360 | 27012 | 26783 | 27086
7774 | 7774 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 22 | 17372 | 17592 | 18502 | 17110 | 17861 | 20135 | 20996 | 20770 | 21424 | 20326 | 22299 | 23636 | 24793 | 24863 | 23527 | 23504 | 25271 | 27108 | 26823 | 27085
7775 | 7775 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 23 | 16331 | 16713 | 17503 | 16632 | 17186 | 19173 | 20121 | 20045 | 20611 | 19815 | 21584 | 22900 | 24124 | 24215 | 23372 | 23120 | 24669 | 26534 | 26390 | 26516
7776 | 7776 | 324 | 11 | 20 | Winter | 11 | 19 | Winter | 24 | 15210 | 15733 | 16348 | 15912 | 16362 | 18123 | 19219 | 19239 | 19598 | 19164 | 20748 | 21981 | 23373 | 23328 | 22874 | 22527 | 23877 | 25850 | 25765 | 25678
7777 | 7777 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 1 | 14624 | 14717 | 15440 | 15029 | 15422 | 17507 | 18039 | 18051 | 18655 | 18215 | 20316 | 21533 | 22333 | 22214 | 20882 | 21485 | 23804 | 24896 | 24584 | 24488
7778 | 7778 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 2 | 14227 | 14259 | 14980 | 14559 | 15078 | 17125 | 17591 | 17595 | 18209 | 17848 | 19876 | 21092 | 21827 | 21632 | 20379 | 21030 | 23236 | 24308 | 23951 | 23841
7779 | 7779 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 3 | 14049 | 14060 | 14753 | 14380 | 14960 | 17024 | 17475 | 17489 | 18014 | 17785 | 19704 | 20937 | 21571 | 21319 | 20112 | 20839 | 22932 | 23957 | 23597 | 23450
7780 | 7780 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 4 | 13989 | 14006 | 14582 | 14163 | 14937 | 16919 | 17324 | 17287 | 17648 | 17605 | 19314 | 20495 | 21044 | 20611 | 19470 | 20361 | 22231 | 23203 | 22806 | 22559
7781 | 7781 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 5 | 14165 | 14208 | 14418 | 13941 | 15021 | 17001 | 17271 | 17242 | 17262 | 17456 | 19062 | 20201 | 20506 | 19769 | 18721 | 19863 | 21610 | 22398 | 22030 | 21495
7782 | 7782 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 6 | 14781 | 14885 | 14376 | 13780 | 15562 | 17554 | 17604 | 17652 | 16941 | 17665 | 19242 | 20356 | 20301 | 19001 | 18048 | 19703 | 21357 | 21925 | 21629 | 20501
7783 | 7783 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 7 | 16026 | 16236 | 14828 | 14098 | 16751 | 18777 | 18672 | 18909 | 17099 | 18549 | 19952 | 21160 | 20978 | 18862 | 17876 | 20340 | 21696 | 22422 | 22239 | 20206
7784 | 7784 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 8 | 17229 | 17565 | 15805 | 15173 | 17965 | 19994 | 19783 | 20233 | 17955 | 19736 | 20789 | 22123 | 21914 | 19559 | 18639 | 21383 | 22363 | 23269 | 23340 | 20844
7785 | 7785 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 9 | 17522 | 17855 | 16371 | 15918 | 18320 | 20170 | 20199 | 20500 | 18515 | 20127 | 21127 | 22176 | 22163 | 20023 | 19156 | 21599 | 22669 | 23491 | 23502 | 21274
7786 | 7786 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 10 | 17444 | 17680 | 16457 | 16142 | 18307 | 19977 | 19984 | 20273 | 18770 | 20027 | 21233 | 22014 | 22171 | 20188 | 19627 | 21562 | 22855 | 23542 | 23546 | 21496
7787 | 7787 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 11 | 17343 | 17388 | 16264 | 16190 | 18288 | 19654 | 19624 | 19804 | 18668 | 19782 | 21277 | 21651 | 22244 | 19887 | 20068 | 21346 | 23001 | 23663 | 23580 | 21247
7788 | 7788 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 12 | 17335 | 17316 | 16212 | 16287 | 18324 | 19511 | 19396 | 19572 | 18521 | 19691 | 21090 | 21439 | 22292 | 19744 | 20378 | 21315 | 22830 | 23733 | 23670 | 21117
7789 | 7789 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 13 | 17186 | 17096 | 15879 | 16063 | 18157 | 19338 | 19079 | 19273 | 18141 | 19473 | 20837 | 21229 | 22061 | 19341 | 20219 | 21113 | 22567 | 23498 | 23461 | 20699
7790 | 7790 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 14 | 17259 | 17202 | 15938 | 16204 | 18286 | 19468 | 19140 | 19352 | 18093 | 19674 | 20726 | 21335 | 21963 | 19296 | 20224 | 21226 | 22386 | 23366 | 23374 | 20628
7791 | 7791 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 15 | 17502 | 17433 | 16205 | 16528 | 18401 | 19929 | 19508 | 19615 | 18061 | 20054 | 20845 | 21804 | 21892 | 19462 | 20171 | 21466 | 22422 | 23272 | 23174 | 20771
7792 | 7792 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 16 | 17912 | 17785 | 16712 | 17141 | 18742 | 20418 | 19937 | 19918 | 18288 | 20535 | 21299 | 22226 | 21802 | 19742 | 20297 | 21760 | 22818 | 23096 | 22882 | 21016
7793 | 7793 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 17 | 18506 | 18351 | 17396 | 17972 | 19576 | 20968 | 20588 | 20565 | 18967 | 21318 | 21954 | 22714 | 22391 | 20548 | 20983 | 22664 | 23492 | 23693 | 23476 | 21849
7794 | 7794 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 18 | 19328 | 19190 | 18127 | 18784 | 20376 | 21584 | 21308 | 21356 | 19900 | 22074 | 22376 | 23373 | 23329 | 21653 | 21795 | 23844 | 24159 | 24762 | 24677 | 23036
7795 | 7795 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 19 | 19016 | 19101 | 17668 | 18440 | 20107 | 21270 | 21176 | 21456 | 19720 | 21971 | 22507 | 23517 | 23521 | 21847 | 21941 | 23992 | 24639 | 25193 | 25385 | 23388
7796 | 7796 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 20 | 18609 | 18801 | 17397 | 18122 | 19951 | 21175 | 20921 | 21390 | 19704 | 21989 | 22747 | 23917 | 23857 | 22268 | 22374 | 24471 | 25214 | 25785 | 25987 | 24000
7797 | 7797 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 21 | 18212 | 18537 | 17133 | 17995 | 19735 | 20999 | 20773 | 21404 | 19761 | 22086 | 23021 | 24318 | 24314 | 22836 | 23018 | 25025 | 25950 | 26570 | 26883 | 24816
7798 | 7798 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 22 | 17474 | 17787 | 16714 | 17511 | 19106 | 20432 | 20229 | 20840 | 19585 | 21702 | 22740 | 24134 | 24146 | 22955 | 23076 | 24900 | 25944 | 26591 | 26871 | 25093
7799 | 7799 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 23 | 16498 | 16775 | 16219 | 16826 | 18239 | 19531 | 19469 | 19988 | 19239 | 20965 | 22016 | 23434 | 23619 | 22781 | 22680 | 24291 | 25398 | 26151 | 26316 | 25006
7800 | 7800 | 325 | 11 | 21 | Winter | 11 | 20 | Winter | 24 | 15472 | 15623 | 15492 | 16009 | 17237 | 18616 | 18648 | 18966 | 18655 | 20147 | 21196 | 22675 | 22913 | 22279 | 22084 | 23504 | 24661 | 25530 | 25481 | 24565
7801 | 7801 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 1 | 14329 | 14705 | 14649 | 15056 | 16410 | 17382 | 17439 | 18022 | 17313 | 19617 | 20617 | 21582 | 21709 | 20357 | 21037 | 23366 | 24173 | 24315 | 24265 | 22310
7802 | 7802 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 2 | 13909 | 14250 | 14184 | 14696 | 16006 | 16938 | 17004 | 17577 | 16882 | 19223 | 20171 | 21091 | 21166 | 19861 | 20581 | 22797 | 23584 | 23685 | 23617 | 21765
7803 | 7803 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 3 | 13698 | 13977 | 13955 | 14537 | 15835 | 16778 | 16847 | 17357 | 16765 | 19031 | 20002 | 20859 | 20898 | 19601 | 20395 | 22495 | 23305 | 23322 | 23215 | 21444
7804 | 7804 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 4 | 13648 | 13813 | 13756 | 14539 | 15727 | 16670 | 16707 | 17066 | 16425 | 18729 | 19622 | 20399 | 20355 | 19002 | 19953 | 21829 | 22575 | 22541 | 22340 | 20701
7805 | 7805 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 5 | 13743 | 13676 | 13549 | 14645 | 15883 | 16662 | 16728 | 16751 | 16032 | 18556 | 19344 | 19952 | 19886 | 18316 | 19509 | 21258 | 21877 | 21801 | 21298 | 19836
7806 | 7806 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 6 | 14335 | 13644 | 13385 | 15228 | 16470 | 17048 | 17230 | 16535 | 15676 | 18831 | 19533 | 19836 | 19792 | 17688 | 19382 | 21041 | 21655 | 21418 | 20306 | 19014
7807 | 7807 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 7 | 15562 | 14114 | 13702 | 16459 | 17513 | 18137 | 18556 | 16775 | 15886 | 19612 | 20279 | 20596 | 20628 | 17570 | 20061 | 21425 | 22144 | 22065 | 20028 | 18750
7808 | 7808 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 8 | 16610 | 15100 | 14785 | 17690 | 18584 | 19267 | 19891 | 17680 | 16885 | 20500 | 21168 | 21584 | 21826 | 18351 | 21116 | 22117 | 22842 | 23154 | 20660 | 19451
7809 | 7809 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 9 | 16978 | 15676 | 15547 | 18071 | 18975 | 19688 | 20175 | 18279 | 17590 | 20863 | 21245 | 21888 | 22087 | 18904 | 21365 | 22460 | 22825 | 23341 | 21102 | 19949
7810 | 7810 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 10 | 16970 | 15978 | 16005 | 18193 | 19137 | 19740 | 20238 | 18671 | 17961 | 21273 | 21354 | 22013 | 22235 | 19498 | 21453 | 22772 | 22818 | 23520 | 21451 | 20587
7811 | 7811 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 11 | 16927 | 16164 | 16456 | 18457 | 19319 | 19876 | 20288 | 18911 | 18064 | 21892 | 21547 | 22226 | 22356 | 20081 | 21382 | 23054 | 22598 | 23693 | 21350 | 21213
7812 | 7812 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 12 | 16897 | 16276 | 16755 | 18692 | 19258 | 19923 | 20351 | 19035 | 18069 | 22036 | 21604 | 22285 | 22447 | 20405 | 21365 | 22900 | 22399 | 23806 | 21244 | 21547
7813 | 7813 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 13 | 16871 | 16222 | 16808 | 18796 | 19266 | 19916 | 20372 | 18958 | 18006 | 22115 | 21562 | 22264 | 22457 | 20453 | 21368 | 22847 | 22254 | 23808 | 21032 | 21583
7814 | 7814 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 14 | 16875 | 16149 | 16807 | 18843 | 19151 | 19820 | 20287 | 18833 | 18057 | 21829 | 21513 | 22091 | 22307 | 20375 | 21398 | 22589 | 22206 | 23627 | 20875 | 21485
7815 | 7815 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 15 | 17117 | 16126 | 16808 | 18839 | 19215 | 19783 | 20110 | 18669 | 18305 | 21451 | 21416 | 21926 | 22032 | 20207 | 21522 | 22527 | 22366 | 23310 | 20900 | 21303
7816 | 7816 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 16 | 17295 | 16160 | 16925 | 18815 | 19370 | 19629 | 19800 | 18495 | 18614 | 21208 | 21306 | 21557 | 21525 | 20053 | 21535 | 22637 | 22473 | 22736 | 20855 | 21127
7817 | 7817 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 17 | 17881 | 16766 | 17684 | 19516 | 19943 | 20186 | 20338 | 18987 | 19403 | 21728 | 21849 | 22107 | 22064 | 20708 | 22408 | 23277 | 23290 | 23301 | 21659 | 21813
7818 | 7818 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 18 | 18425 | 17429 | 18490 | 20134 | 20482 | 20861 | 21050 | 19640 | 20035 | 22038 | 22344 | 22949 | 23098 | 21457 | 23529 | 23892 | 24127 | 24455 | 22804 | 22649
7819 | 7819 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 19 | 18123 | 16956 | 18123 | 19832 | 20312 | 20681 | 21095 | 19389 | 19742 | 22073 | 22405 | 23075 | 23555 | 21558 | 23640 | 24330 | 24563 | 25155 | 23157 | 22895
7820 | 7820 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 20 | 17786 | 16642 | 17741 | 19612 | 20121 | 20365 | 20924 | 19267 | 19708 | 22194 | 22754 | 23305 | 23844 | 21909 | 24053 | 24830 | 25351 | 25714 | 23733 | 23417
7821 | 7821 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 21 | 17418 | 16343 | 17570 | 19350 | 19905 | 20149 | 20852 | 19229 | 19843 | 22348 | 23018 | 23645 | 24384 | 22474 | 24538 | 25511 | 26118 | 26576 | 24523 | 24188
7822 | 7822 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 22 | 16755 | 15962 | 17096 | 18728 | 19305 | 19602 | 20276 | 19028 | 19622 | 22042 | 22905 | 23441 | 24192 | 22525 | 24419 | 25506 | 26314 | 26585 | 24827 | 24382
7823 | 7823 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 23 | 15854 | 15420 | 16378 | 17827 | 18340 | 18801 | 19371 | 18617 | 19066 | 21276 | 22229 | 22859 | 23502 | 22094 | 23784 | 24922 | 25812 | 26004 | 24731 | 24037
7824 | 7824 | 326 | 11 | 22 | Winter | 11 | 21 | Winter | 24 | 14879 | 14678 | 15518 | 16816 | 17362 | 17922 | 18287 | 17996 | 18415 | 20419 | 21420 | 22136 | 22594 | 21478 | 22981 | 24184 | 25077 | 25157 | 24285 | 23479
7825 | 7825 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 1 | 13896 | 13880 | 14573 | 15957 | 16621 | 16726 | 17352 | 16751 | 17447 | 19821 | 20266 | 20933 | 21474 | 20429 | 22792 | 23676 | 23958 | 23943 | 22048 | 22394
7826 | 7826 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 2 | 13481 | 13447 | 14229 | 15586 | 16211 | 16309 | 16929 | 16362 | 17122 | 19419 | 19790 | 20430 | 20927 | 20007 | 22267 | 23115 | 23331 | 23318 | 21527 | 21924
7827 | 7827 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 3 | 13241 | 13177 | 14049 | 15358 | 16059 | 16134 | 16698 | 16192 | 17017 | 19270 | 19621 | 20180 | 20624 | 19836 | 21965 | 22848 | 23055 | 22917 | 21202 | 21689
7828 | 7828 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 4 | 13196 | 12970 | 14048 | 15267 | 15945 | 16015 | 16441 | 15899 | 16892 | 18952 | 19229 | 19698 | 19967 | 19425 | 21331 | 22146 | 22296 | 22040 | 20453 | 21137
7829 | 7829 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 5 | 13426 | 12782 | 14169 | 15446 | 15996 | 16085 | 16193 | 15555 | 16808 | 18761 | 18931 | 19319 | 19214 | 19031 | 20815 | 21494 | 21644 | 21019 | 19592 | 20562
7830 | 7830 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 6 | 14129 | 12603 | 14773 | 16072 | 16527 | 16635 | 16057 | 15265 | 17098 | 19036 | 18962 | 19313 | 18519 | 18950 | 20652 | 21304 | 21267 | 20052 | 18782 | 20307
7831 | 7831 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 7 | 15479 | 12891 | 16007 | 17126 | 17635 | 17962 | 16336 | 15481 | 18009 | 19824 | 19947 | 20200 | 18427 | 19630 | 21055 | 21800 | 21902 | 19761 | 18497 | 20868
7832 | 7832 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 8 | 16796 | 14048 | 17293 | 18227 | 18768 | 19336 | 17292 | 16529 | 19263 | 20787 | 21243 | 21449 | 19168 | 20752 | 21780 | 22541 | 22985 | 20427 | 19233 | 21935
7833 | 7833 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 9 | 17094 | 14819 | 17691 | 18573 | 18942 | 19624 | 17899 | 17215 | 19675 | 20898 | 21399 | 21708 | 19670 | 21017 | 22132 | 22510 | 23101 | 20877 | 19736 | 22152
7834 | 7834 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 10 | 16943 | 15076 | 17605 | 18628 | 18773 | 19478 | 18074 | 17545 | 19678 | 20800 | 21235 | 21637 | 19757 | 20893 | 22241 | 22289 | 22818 | 21019 | 20172 | 22070
7835 | 7835 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 11 | 16925 | 15461 | 17798 | 19007 | 18815 | 19443 | 18228 | 17989 | 19942 | 20914 | 21279 | 21679 | 19522 | 20747 | 22441 | 21997 | 22453 | 20842 | 20726 | 21963
7836 | 7836 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 12 | 16921 | 15674 | 17946 | 19071 | 18773 | 19416 | 18261 | 18205 | 20092 | 20876 | 21220 | 21675 | 19301 | 20635 | 22206 | 21715 | 22117 | 20638 | 20972 | 21870
7837 | 7837 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 13 | 16422 | 15172 | 17496 | 18614 | 18188 | 18888 | 17635 | 17709 | 19653 | 20285 | 20745 | 21134 | 18554 | 20088 | 21603 | 21004 | 21513 | 19878 | 20460 | 21317
7838 | 7838 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 14 | 16384 | 15107 | 17492 | 18409 | 18170 | 18762 | 17467 | 17621 | 19648 | 20189 | 20593 | 20942 | 18406 | 20069 | 21300 | 20909 | 21382 | 19671 | 20310 | 21280
7839 | 7839 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 15 | 16744 | 15542 | 17925 | 18667 | 18600 | 19029 | 17739 | 17929 | 19954 | 20514 | 20707 | 21087 | 18877 | 20614 | 21661 | 21481 | 21728 | 20113 | 20544 | 21809
7840 | 7840 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 16 | 16850 | 15896 | 18146 | 18790 | 18887 | 18975 | 17810 | 18092 | 19964 | 20630 | 20640 | 20818 | 19088 | 20847 | 21993 | 21812 | 21848 | 20280 | 20577 | 22016
7841 | 7841 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 17 | 17514 | 16838 | 19025 | 19489 | 19715 | 19698 | 18476 | 18969 | 20797 | 21334 | 21454 | 21530 | 20037 | 21880 | 22796 | 22809 | 22783 | 21251 | 21429 | 23079
7842 | 7842 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 18 | 18355 | 17742 | 19707 | 20120 | 20342 | 20507 | 19198 | 19668 | 21546 | 21860 | 22690 | 22578 | 21148 | 23060 | 23468 | 23702 | 24470 | 22470 | 22328 | 24345
7843 | 7843 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 19 | 18239 | 17348 | 19373 | 19916 | 20016 | 20513 | 18896 | 19316 | 21362 | 21831 | 22875 | 22971 | 21274 | 23113 | 23864 | 24099 | 25104 | 22808 | 22561 | 24526
7844 | 7844 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 20 | 17922 | 16977 | 19166 | 19713 | 19964 | 20342 | 18760 | 19255 | 21332 | 22122 | 23175 | 23213 | 21636 | 23521 | 24346 | 24881 | 25831 | 23417 | 23125 | 25086
7845 | 7845 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 21 | 17637 | 16792 | 18873 | 19461 | 19719 | 20213 | 18653 | 19321 | 21341 | 22272 | 23473 | 23647 | 22113 | 23945 | 24969 | 25595 | 26630 | 24199 | 23899 | 25711
7846 | 7846 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 22 | 16916 | 16285 | 18215 | 18836 | 19227 | 19589 | 18391 | 19052 | 20937 | 22092 | 23097 | 23388 | 22208 | 23789 | 24926 | 25755 | 26551 | 24481 | 24076 | 25680
7847 | 7847 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 23 | 15887 | 15552 | 17284 | 17846 | 18360 | 18643 | 17934 | 18448 | 20154 | 21372 | 22301 | 22658 | 21998 | 23126 | 24312 | 25230 | 25910 | 24360 | 23709 | 25083
7848 | 7848 | 327 | 11 | 23 | Winter | 11 | 22 | Winter | 24 | 14758 | 14719 | 16300 | 16875 | 17411 | 17574 | 17324 | 17777 | 19318 | 20599 | 21294 | 21767 | 21504 | 22360 | 23608 | 24526 | 24982 | 23942 | 23196 | 24362
7849 | 7849 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 1 | 13833 | 13803 | 15443 | 16138 | 16254 | 16674 | 16189 | 16838 | 18746 | 19445 | 20591 | 20697 | 19703 | 22145 | 23104 | 23419 | 24319 | 21766 | 22138 | 24352
7850 | 7850 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 2 | 13425 | 13461 | 15067 | 15708 | 15780 | 16238 | 15777 | 16493 | 18397 | 18965 | 20005 | 20190 | 19251 | 21643 | 22563 | 22804 | 23647 | 21253 | 21673 | 23787
7851 | 7851 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 3 | 13160 | 13304 | 14870 | 15582 | 15664 | 16047 | 15656 | 16436 | 18221 | 18892 | 19736 | 19932 | 19021 | 21390 | 22335 | 22572 | 23194 | 20958 | 21472 | 23457
7852 | 7852 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 4 | 12981 | 13278 | 14774 | 15464 | 15561 | 15798 | 15370 | 16328 | 17959 | 18553 | 19273 | 19336 | 18448 | 20791 | 21667 | 21843 | 22390 | 20212 | 20913 | 22685
7853 | 7853 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 5 | 12845 | 13392 | 14955 | 15526 | 15628 | 15590 | 15065 | 16293 | 17844 | 18338 | 18897 | 18648 | 17804 | 20313 | 21045 | 21216 | 21583 | 19352 | 20328 | 21994
7854 | 7854 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 6 | 12819 | 13992 | 15574 | 16070 | 16097 | 15487 | 14809 | 16637 | 18198 | 18450 | 18782 | 18045 | 17232 | 20206 | 20903 | 20883 | 21052 | 18559 | 20076 | 21668
7855 | 7855 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 7 | 13286 | 15278 | 16689 | 17225 | 17361 | 15835 | 15098 | 17639 | 19043 | 19535 | 19492 | 18049 | 17146 | 20669 | 21454 | 21550 | 21472 | 18304 | 20654 | 21968
7856 | 7856 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 8 | 14245 | 16523 | 17765 | 18328 | 18757 | 16725 | 16117 | 18877 | 19952 | 20822 | 20575 | 18771 | 17947 | 21377 | 22173 | 22615 | 22434 | 19002 | 21672 | 22578
7857 | 7857 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 9 | 14830 | 16939 | 18135 | 18527 | 19043 | 17343 | 16833 | 19333 | 20344 | 21011 | 20954 | 19300 | 18534 | 21745 | 22174 | 22734 | 22679 | 19516 | 21900 | 22932
7858 | 7858 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 10 | 15149 | 16998 | 18300 | 18461 | 19046 | 17586 | 17215 | 19378 | 20760 | 20868 | 21022 | 19592 | 19138 | 22058 | 22163 | 22658 | 23000 | 20162 | 22031 | 23302
7859 | 7859 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 11 | 15321 | 17047 | 18488 | 18289 | 19063 | 17434 | 17320 | 19281 | 21342 | 20488 | 20853 | 19405 | 19699 | 22299 | 21921 | 22343 | 23363 | 20768 | 21979 | 23607
7860 | 7860 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 12 | 15427 | 17167 | 18504 | 18171 | 19083 | 17339 | 17384 | 19264 | 21478 | 20228 | 20689 | 19263 | 20013 | 22142 | 21717 | 22106 | 23500 | 21093 | 21963 | 23458
7861 | 7861 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 13 | 15321 | 17177 | 18494 | 18024 | 19117 | 17135 | 17299 | 19227 | 21501 | 20143 | 20571 | 19021 | 20006 | 22036 | 21509 | 22003 | 23472 | 21080 | 21909 | 23354
7862 | 7862 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 14 | 15268 | 17282 | 18433 | 18111 | 19110 | 17112 | 17358 | 19341 | 21248 | 20149 | 20499 | 18955 | 19950 | 21846 | 21521 | 21950 | 23272 | 21034 | 21974 | 23128
7863 | 7863 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 15 | 15229 | 17440 | 18440 | 18300 | 18934 | 17190 | 17490 | 19490 | 20872 | 20133 | 20430 | 19005 | 19763 | 21794 | 21673 | 21879 | 22856 | 20844 | 22080 | 23033
7864 | 7864 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 16 | 15289 | 17613 | 18494 | 18599 | 18901 | 17321 | 17728 | 19604 | 20665 | 20189 | 20294 | 19040 | 19625 | 21951 | 21814 | 21817 | 22313 | 20678 | 22087 | 23123
7865 | 7865 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 17 | 15877 | 18373 | 19107 | 19348 | 19559 | 17940 | 18568 | 20402 | 21174 | 20978 | 21029 | 19792 | 20258 | 22579 | 22623 | 22552 | 22912 | 21341 | 22968 | 23761
7866 | 7866 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 18 | 16526 | 19039 | 19824 | 20058 | 20628 | 18777 | 19401 | 21248 | 21482 | 22300 | 21987 | 20767 | 20984 | 23143 | 23405 | 24129 | 23878 | 22175 | 24162 | 24406
7867 | 7867 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 19 | 16036 | 18700 | 19601 | 19696 | 20578 | 18456 | 19017 | 21016 | 21441 | 22406 | 21992 | 20815 | 21018 | 23477 | 23753 | 24719 | 24161 | 22390 | 24324 | 24911
7868 | 7868 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 20 | 15720 | 18424 | 19333 | 19563 | 20401 | 18244 | 18877 | 20892 | 21485 | 22584 | 22068 | 21053 | 21324 | 23869 | 24450 | 25382 | 24756 | 22906 | 24851 | 25511
7869 | 7869 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 21 | 15385 | 18090 | 19019 | 19241 | 20188 | 18059 | 18855 | 20798 | 21525 | 22741 | 22346 | 21404 | 21802 | 24393 | 25075 | 26099 | 25543 | 23635 | 25446 | 26285
7870 | 7870 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 22 | 14990 | 17402 | 18355 | 18697 | 19485 | 17745 | 18521 | 20325 | 21147 | 22287 | 22195 | 21433 | 21794 | 24305 | 25187 | 25979 | 25706 | 23801 | 25404 | 26351
7871 | 7871 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 23 | 14455 | 16492 | 17379 | 17839 | 18486 | 17295 | 17920 | 19533 | 20358 | 21495 | 21691 | 21207 | 21363 | 23687 | 24680 | 25357 | 25369 | 23457 | 24832 | 25828
7872 | 7872 | 328 | 11 | 24 | Winter | 11 | 23 | Winter | 24 | 13764 | 15467 | 16362 | 16867 | 17287 | 16634 | 17194 | 18658 | 19515 | 20454 | 20934 | 20687 | 20776 | 22948 | 23937 | 24400 | 24714 | 22904 | 24090 | 25140
7873 | 7873 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 1 | 12956 | 14566 | 15566 | 15653 | 16452 | 15523 | 16199 | 17940 | 18835 | 19708 | 19962 | 18918 | 19691 | 22361 | 22745 | 23679 | 23693 | 21781 | 23994 | 24630
7874 | 7874 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 2 | 12506 | 14157 | 15131 | 15143 | 15919 | 15100 | 15847 | 17564 | 18405 | 19155 | 19399 | 18462 | 19263 | 21821 | 22129 | 22997 | 23014 | 21295 | 23409 | 24031
7875 | 7875 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 3 | 12302 | 13966 | 14994 | 15049 | 15716 | 14968 | 15783 | 17432 | 18352 | 18914 | 19157 | 18292 | 19164 | 21645 | 21946 | 22598 | 22663 | 21127 | 23125 | 23777
7876 | 7876 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 4 | 12119 | 13915 | 14931 | 14998 | 15603 | 14751 | 15756 | 17257 | 18106 | 18583 | 18699 | 17810 | 18826 | 21061 | 21299 | 21868 | 21887 | 20623 | 22394 | 23015
7877 | 7877 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 5 | 11911 | 14075 | 14987 | 15080 | 15596 | 14457 | 15744 | 17193 | 17973 | 18268 | 18192 | 17218 | 18456 | 20487 | 20710 | 21096 | 20988 | 20042 | 21698 | 22222
7878 | 7878 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 6 | 11720 | 14722 | 15559 | 15599 | 15983 | 14268 | 16183 | 17630 | 18321 | 18285 | 17865 | 16729 | 18440 | 20422 | 20446 | 20621 | 20142 | 19821 | 21389 | 21933
7879 | 7879 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 7 | 12001 | 15852 | 16697 | 16863 | 17044 | 14561 | 17212 | 18523 | 19190 | 19040 | 17990 | 16677 | 19157 | 21011 | 21131 | 21049 | 19853 | 20388 | 21662 | 22335
7880 | 7880 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 8 | 13144 | 16986 | 17815 | 18269 | 18227 | 15629 | 18504 | 19510 | 20134 | 20193 | 18738 | 17522 | 20273 | 21766 | 22240 | 22035 | 20457 | 21431 | 22322 | 22978
7881 | 7881 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 9 | 13910 | 17310 | 17997 | 18523 | 18575 | 16318 | 18938 | 19897 | 20265 | 20551 | 19385 | 18103 | 20537 | 21769 | 22347 | 22262 | 20996 | 21643 | 22654 | 22905
7882 | 7882 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 10 | 14160 | 17406 | 17899 | 18385 | 18480 | 16691 | 18985 | 20146 | 20057 | 20647 | 19839 | 18554 | 20475 | 21615 | 22123 | 22434 | 21392 | 21628 | 22872 | 22792
7883 | 7883 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 11 | 14277 | 17668 | 17860 | 18269 | 18242 | 17025 | 19148 | 20576 | 19633 | 20800 | 20034 | 18966 | 20242 | 21225 | 21661 | 22655 | 21295 | 21432 | 23042 | 22443
7884 | 7884 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 12 | 14289 | 17674 | 17749 | 18135 | 17995 | 17154 | 19214 | 20548 | 19245 | 20753 | 20060 | 19116 | 20047 | 20855 | 21255 | 22631 | 21040 | 21252 | 22728 | 22091
7885 | 7885 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 13 | 13939 | 17420 | 17368 | 17881 | 17629 | 16856 | 18971 | 20276 | 18753 | 20445 | 19773 | 18816 | 19700 | 20348 | 20852 | 22310 | 20529 | 20899 | 22313 | 21574
7886 | 7886 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 14 | 13934 | 17307 | 17369 | 17856 | 17565 | 16819 | 18986 | 20007 | 18760 | 20272 | 19592 | 18736 | 19735 | 20301 | 20741 | 22080 | 20327 | 20901 | 22021 | 21502
7887 | 7887 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 15 | 14281 | 17415 | 17623 | 17931 | 17760 | 16952 | 19115 | 19887 | 19159 | 20138 | 19617 | 18779 | 20077 | 20665 | 20885 | 21893 | 20625 | 21215 | 22141 | 21850
7888 | 7888 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 16 | 14829 | 17579 | 18037 | 18199 | 18012 | 17237 | 19253 | 19941 | 19651 | 19979 | 19594 | 18915 | 20378 | 21075 | 21094 | 21621 | 20828 | 21478 | 22490 | 22213
7889 | 7889 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 17 | 15881 | 18345 | 18916 | 19087 | 18933 | 18168 | 20125 | 20681 | 20552 | 20752 | 20479 | 19763 | 21438 | 22092 | 22037 | 22436 | 21901 | 22559 | 23343 | 23271
7890 | 7890 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 18 | 16892 | 19064 | 19633 | 20246 | 19732 | 18946 | 20858 | 21095 | 21293 | 21521 | 21494 | 20547 | 22594 | 22944 | 23690 | 23465 | 23417 | 23839 | 24077 | 24230
7891 | 7891 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 19 | 16509 | 18819 | 19272 | 20177 | 19434 | 18547 | 20601 | 21006 | 21217 | 21443 | 21690 | 20534 | 22603 | 23249 | 24258 | 23721 | 23964 | 24023 | 24581 | 24721
7892 | 7892 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 20 | 16096 | 18531 | 19092 | 19968 | 19188 | 18367 | 20429 | 20983 | 21386 | 21417 | 21823 | 20765 | 22940 | 23876 | 24871 | 24275 | 24427 | 24549 | 25188 | 25575
7893 | 7893 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 21 | 15906 | 18223 | 18764 | 19745 | 19004 | 18326 | 20307 | 20966 | 21444 | 21615 | 22193 | 21194 | 23303 | 24456 | 25551 | 25042 | 25285 | 25163 | 25987 | 26431
7894 | 7894 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 22 | 15365 | 17556 | 18208 | 19034 | 18528 | 17961 | 19802 | 20539 | 21188 | 21416 | 22212 | 21145 | 23093 | 24542 | 25410 | 25195 | 25610 | 25117 | 26058 | 26695
7895 | 7895 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 23 | 14669 | 16597 | 17349 | 18043 | 17799 | 17354 | 19003 | 19732 | 20466 | 20899 | 21858 | 20707 | 22451 | 24030 | 24786 | 24858 | 25369 | 24569 | 25561 | 26260
7896 | 7896 | 329 | 11 | 25 | Winter | 11 | 24 | Winter | 24 | 13804 | 15550 | 16338 | 16799 | 16834 | 16577 | 18081 | 18819 | 19643 | 20106 | 21186 | 20072 | 21648 | 23263 | 23807 | 24155 | 24815 | 23807 | 24856 | 25552
7897 | 7897 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 1 | 13160 | 15079 | 15474 | 16275 | 16353 | 15896 | 17605 | 18433 | 18746 | 19480 | 19404 | 19322 | 21624 | 22384 | 23387 | 23467 | 22603 | 24007 | 24666 | 24708
7898 | 7898 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 2 | 12846 | 14683 | 14973 | 15759 | 15848 | 15540 | 17231 | 18033 | 18305 | 18941 | 18861 | 18940 | 21140 | 21806 | 22743 | 22827 | 22005 | 23445 | 24100 | 24068
7899 | 7899 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 3 | 12661 | 14488 | 14837 | 15501 | 15590 | 15444 | 17081 | 17936 | 18197 | 18723 | 18595 | 18821 | 20901 | 21601 | 22323 | 22451 | 21616 | 23122 | 23805 | 23784
7900 | 7900 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 4 | 12659 | 14397 | 14772 | 15388 | 15390 | 15405 | 16912 | 17723 | 17956 | 18295 | 18148 | 18515 | 20372 | 20993 | 21623 | 21683 | 20930 | 22392 | 23033 | 22987
7901 | 7901 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 5 | 12782 | 14506 | 14905 | 15431 | 15326 | 15464 | 16941 | 17681 | 17817 | 17913 | 17615 | 18234 | 19965 | 20493 | 20929 | 20854 | 20012 | 21743 | 22275 | 22261
7902 | 7902 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 6 | 13393 | 15057 | 15437 | 15851 | 15411 | 15920 | 17420 | 18091 | 18037 | 17645 | 17097 | 18284 | 19923 | 20283 | 20503 | 20038 | 19110 | 21448 | 21982 | 21816
7903 | 7903 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 7 | 14690 | 16237 | 16755 | 16939 | 15841 | 17014 | 18407 | 19031 | 19170 | 17872 | 17046 | 19077 | 20426 | 21026 | 20974 | 19793 | 18806 | 21755 | 22406 | 22414
7904 | 7904 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 8 | 15946 | 17330 | 18140 | 18104 | 16688 | 18279 | 19400 | 19990 | 20503 | 18614 | 17760 | 20202 | 21196 | 22122 | 21949 | 20374 | 19390 | 22387 | 23029 | 23447
7905 | 7905 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 9 | 16357 | 17566 | 18433 | 18464 | 17437 | 18740 | 19823 | 20172 | 20690 | 19339 | 18268 | 20517 | 21580 | 22254 | 22196 | 20976 | 19764 | 22734 | 22982 | 23551
7906 | 7906 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 10 | 16475 | 17533 | 18337 | 18506 | 17935 | 18758 | 20024 | 20095 | 20702 | 19721 | 18706 | 20573 | 21858 | 22144 | 22482 | 21491 | 20331 | 23068 | 22989 | 23479
7907 | 7907 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 11 | 16510 | 17227 | 17924 | 18223 | 17999 | 18488 | 19973 | 19620 | 20578 | 19365 | 18652 | 20255 | 21882 | 21600 | 22617 | 21313 | 20455 | 23154 | 22565 | 22993
7908 | 7908 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 12 | 16612 | 17017 | 17678 | 18030 | 18051 | 18364 | 19733 | 19270 | 20458 | 19127 | 18654 | 20076 | 21573 | 21212 | 22630 | 21065 | 20452 | 22871 | 22232 | 22620
7909 | 7909 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 13 | 16470 | 16704 | 17475 | 17773 | 17873 | 18139 | 19475 | 18884 | 20283 | 18834 | 18534 | 19829 | 21270 | 20912 | 22405 | 20655 | 20217 | 22556 | 21816 | 22307
7910 | 7910 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 14 | 16474 | 16720 | 17480 | 17705 | 17733 | 18192 | 19260 | 18883 | 20180 | 18704 | 18453 | 19856 | 21014 | 20809 | 22181 | 20444 | 20056 | 22267 | 21744 | 22171
7911 | 7911 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 15 | 16503 | 16874 | 17485 | 17669 | 17634 | 18319 | 19166 | 19044 | 19884 | 18782 | 18510 | 19964 | 20955 | 20729 | 21771 | 20503 | 20101 | 22159 | 21860 | 22057
7912 | 7912 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 16 | 16785 | 17400 | 17901 | 17900 | 17765 | 18680 | 19441 | 19518 | 19900 | 19038 | 18812 | 20246 | 21344 | 20922 | 21482 | 20677 | 20341 | 22481 | 22203 | 22185
7913 | 7913 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 17 | 17751 | 18401 | 18934 | 18871 | 18644 | 19752 | 20396 | 20478 | 20799 | 20143 | 19835 | 21365 | 22235 | 21933 | 22352 | 21822 | 21466 | 23385 | 23304 | 23200
7914 | 7914 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 18 | 18399 | 19243 | 20189 | 19657 | 19685 | 20683 | 21025 | 21230 | 21975 | 21333 | 20977 | 22483 | 22878 | 23559 | 23354 | 23341 | 22708 | 24130 | 24267 | 24928
7915 | 7915 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 19 | 18070 | 18854 | 20106 | 19338 | 19594 | 20427 | 20917 | 21103 | 22011 | 21459 | 20984 | 22443 | 23159 | 24079 | 23573 | 23861 | 22983 | 24631 | 24763 | 25622
7916 | 7916 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 20 | 17748 | 18648 | 19871 | 19066 | 19327 | 20227 | 20840 | 21192 | 22095 | 21501 | 21191 | 22710 | 23483 | 24639 | 24087 | 24285 | 23488 | 25232 | 25604 | 26372
7917 | 7917 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 21 | 17434 | 18304 | 19622 | 18846 | 19223 | 20064 | 20759 | 21164 | 22191 | 21777 | 21402 | 23005 | 23967 | 25256 | 24793 | 25098 | 24090 | 26019 | 26458 | 27247
7918 | 7918 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 22 | 16752 | 17687 | 18875 | 18352 | 18911 | 19504 | 20262 | 20848 | 21696 | 21724 | 21229 | 22742 | 23839 | 25063 | 24903 | 25396 | 24186 | 26072 | 26707 | 27207
7919 | 7919 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 23 | 15805 | 16749 | 17800 | 17565 | 18278 | 18623 | 19362 | 20041 | 20829 | 21287 | 20740 | 22031 | 23181 | 24345 | 24480 | 25094 | 23819 | 25496 | 26213 | 26592
7920 | 7920 | 330 | 11 | 26 | Winter | 11 | 25 | Winter | 24 | 14769 | 15731 | 16535 | 16582 | 17455 | 17682 | 18423 | 19176 | 19747 | 20607 | 20091 | 21211 | 22411 | 23359 | 23772 | 24529 | 23240 | 24785 | 25514 | 25667
7921 | 7921 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 1 | 13713 | 14483 | 15540 | 15663 | 15762 | 16689 | 17539 | 17786 | 18814 | 18494 | 18559 | 20643 | 21654 | 22470 | 22660 | 21911 | 21471 | 24118 | 24207 | 24798
7922 | 7922 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 2 | 13322 | 13994 | 15028 | 15128 | 15246 | 16304 | 17124 | 17324 | 18267 | 17969 | 18157 | 20172 | 21152 | 21841 | 22031 | 21322 | 21040 | 23540 | 23571 | 24105
7923 | 7923 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 3 | 13098 | 13798 | 14748 | 14869 | 14972 | 16134 | 17021 | 17237 | 18025 | 17724 | 18070 | 19948 | 20952 | 21427 | 21660 | 20934 | 20849 | 23253 | 23270 | 23610
7924 | 7924 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 4 | 13047 | 13751 | 14677 | 14695 | 14771 | 16017 | 16872 | 17060 | 17746 | 17360 | 17820 | 19503 | 20426 | 20805 | 20956 | 20294 | 20395 | 22513 | 22495 | 22789
7925 | 7925 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 5 | 13252 | 13902 | 14748 | 14675 | 14501 | 16095 | 16893 | 17018 | 17561 | 16901 | 17693 | 19182 | 19954 | 20183 | 20187 | 19422 | 20035 | 21782 | 21790 | 21948
7926 | 7926 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 6 | 13891 | 14469 | 15212 | 14792 | 14280 | 16632 | 17378 | 17327 | 17650 | 16464 | 17935 | 19231 | 19952 | 19827 | 19430 | 18562 | 20025 | 21518 | 21366 | 21368
7927 | 7927 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 7 | 15079 | 15813 | 16348 | 15265 | 14553 | 17679 | 18379 | 18564 | 18499 | 16485 | 19006 | 19820 | 20613 | 20356 | 19234 | 18289 | 20806 | 21968 | 21984 | 21756
7928 | 7928 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 8 | 16189 | 17191 | 17538 | 16120 | 15413 | 18719 | 19404 | 19921 | 19655 | 17254 | 20460 | 20653 | 21393 | 21382 | 19851 | 18891 | 22076 | 22638 | 23017 | 22702
7929 | 7929 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 9 | 16334 | 17286 | 17709 | 16688 | 15778 | 18935 | 19406 | 19952 | 19867 | 17599 | 20740 | 20863 | 21254 | 21445 | 20272 | 19078 | 22230 | 22404 | 22927 | 22717
7930 | 7930 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 10 | 16009 | 16750 | 17289 | 16602 | 15746 | 18646 | 18845 | 19324 | 19446 | 17552 | 20461 | 20652 | 20759 | 21248 | 20306 | 19165 | 22086 | 21927 | 22385 | 22559
7931 | 7931 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 11 | 15948 | 16351 | 17037 | 16380 | 15744 | 18599 | 18388 | 18771 | 19028 | 17496 | 20177 | 20627 | 20254 | 21350 | 20096 | 19252 | 21920 | 21476 | 21868 | 22719
7932 | 7932 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 12 | 15819 | 16093 | 16816 | 16210 | 15776 | 18316 | 17983 | 18327 | 18681 | 17416 | 19936 | 20271 | 19836 | 21305 | 19808 | 19204 | 21692 | 21085 | 21464 | 22697
7933 | 7933 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 13 | 15951 | 16210 | 16876 | 16267 | 16015 | 18365 | 17900 | 18353 | 18688 | 17585 | 19888 | 20279 | 19750 | 21395 | 19707 | 19278 | 21557 | 20987 | 21466 | 22794
7934 | 7934 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 14 | 16111 | 16479 | 17074 | 16435 | 16196 | 18442 | 18183 | 18595 | 18802 | 17798 | 20069 | 20280 | 19941 | 21413 | 19735 | 19363 | 21610 | 21150 | 21566 | 22782
7935 | 7935 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 15 | 16257 | 16668 | 17231 | 16714 | 16403 | 18582 | 18571 | 18800 | 18864 | 18104 | 20282 | 20366 | 20212 | 21148 | 19934 | 19543 | 21694 | 21405 | 21591 | 22485
7936 | 7936 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 16 | 16642 | 17288 | 17678 | 17264 | 16914 | 19105 | 19299 | 19372 | 19126 | 18681 | 20666 | 20899 | 20732 | 21021 | 20263 | 19935 | 21890 | 21893 | 21861 | 22298
7937 | 7937 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 17 | 17576 | 18296 | 18618 | 18222 | 18000 | 20031 | 20213 | 20383 | 20146 | 19636 | 21609 | 21813 | 21833 | 21898 | 21417 | 21074 | 22845 | 23006 | 22896 | 23180
7938 | 7938 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 18 | 18377 | 19396 | 19224 | 19241 | 18994 | 20501 | 20774 | 21514 | 21071 | 20485 | 22564 | 22382 | 22622 | 22830 | 22871 | 22268 | 24174 | 23917 | 24575 | 24225
7939 | 7939 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 19 | 18128 | 19275 | 18855 | 19119 | 18697 | 20342 | 20577 | 21494 | 20941 | 20399 | 22426 | 22582 | 22866 | 22975 | 23329 | 22508 | 24376 | 24379 | 25243 | 24545
7940 | 7940 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 20 | 17844 | 19037 | 18571 | 18867 | 18624 | 20244 | 20637 | 21538 | 20864 | 20553 | 22509 | 22872 | 23456 | 23455 | 23727 | 23037 | 24723 | 25246 | 26003 | 25220
7941 | 7941 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 21 | 17502 | 18753 | 18289 | 18696 | 18429 | 20075 | 20501 | 21513 | 20937 | 20656 | 22640 | 23228 | 23938 | 24054 | 24457 | 23570 | 25186 | 26043 | 26842 | 26083
7942 | 7942 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 22 | 16804 | 17985 | 17753 | 18329 | 17980 | 19509 | 20101 | 20925 | 20653 | 20421 | 22134 | 23014 | 23946 | 24097 | 24691 | 23618 | 24905 | 26254 | 26786 | 26284
7943 | 7943 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 23 | 15814 | 16918 | 16977 | 17706 | 17348 | 18614 | 19294 | 20038 | 20072 | 19934 | 21267 | 22338 | 23373 | 23682 | 24406 | 23255 | 24088 | 25787 | 26199 | 25969
7944 | 7944 | 331 | 11 | 27 | Winter | 11 | 26 | Winter | 24 | 14750 | 15659 | 15979 | 16881 | 16537 | 17652 | 18404 | 18934 | 19247 | 19293 | 20255 | 21551 | 22583 | 22959 | 23834 | 22660 | 23109 | 25072 | 25277 | 25321
7945 | 7945 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 1 | 14503 | 15359 | 15716 | 15921 | 16030 | 17416 | 17678 | 18666 | 18882 | 18519 | 20302 | 21450 | 21922 | 22544 | 21956 | 21624 | 23531 | 24445 | 25087 | 24789
7946 | 7946 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 2 | 14103 | 14858 | 15173 | 15386 | 15617 | 16988 | 17204 | 18114 | 18338 | 18131 | 19827 | 20961 | 21361 | 21922 | 21368 | 21194 | 23007 | 23805 | 24386 | 24100
7947 | 7947 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 3 | 13945 | 14617 | 14944 | 15139 | 15542 | 16913 | 17156 | 17916 | 18174 | 18104 | 19681 | 20831 | 21208 | 21627 | 21046 | 21054 | 22694 | 23558 | 23938 | 23727
7948 | 7948 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 4 | 13853 | 14511 | 14758 | 14918 | 15456 | 16765 | 16995 | 17670 | 17808 | 17883 | 19330 | 20346 | 20651 | 20950 | 20409 | 20604 | 22090 | 22775 | 23109 | 22875
7949 | 7949 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 5 | 13955 | 14547 | 14731 | 14643 | 15545 | 16806 | 16990 | 17532 | 17482 | 17786 | 19029 | 19926 | 20209 | 20216 | 19557 | 20242 | 21470 | 22063 | 22245 | 21917
7950 | 7950 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 6 | 14501 | 15023 | 14878 | 14445 | 16069 | 17340 | 17372 | 17714 | 17305 | 18088 | 19145 | 20003 | 20083 | 19521 | 18733 | 20254 | 21235 | 21656 | 21669 | 21000
7951 | 7951 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 7 | 15698 | 16157 | 15366 | 14740 | 17297 | 18385 | 18663 | 18640 | 17603 | 19202 | 19952 | 20729 | 20900 | 19357 | 18486 | 21046 | 21774 | 22279 | 22053 | 20683
7952 | 7952 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 8 | 16831 | 17343 | 16239 | 15603 | 18799 | 19425 | 20042 | 19847 | 18418 | 20686 | 21109 | 21565 | 22039 | 19999 | 19087 | 22345 | 22779 | 23313 | 22989 | 21265
7953 | 7953 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 9 | 17078 | 17692 | 17004 | 16163 | 19320 | 19620 | 20277 | 20263 | 19158 | 21170 | 21544 | 21638 | 22179 | 20620 | 19487 | 22683 | 23071 | 23418 | 23204 | 21845
7954 | 7954 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 10 | 17036 | 17758 | 17417 | 16593 | 19501 | 19541 | 20135 | 20301 | 19522 | 21371 | 21768 | 21589 | 22052 | 21123 | 20041 | 22994 | 23591 | 23353 | 23524 | 22395
7955 | 7955 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 11 | 16865 | 17674 | 17345 | 16766 | 19438 | 19211 | 19699 | 20044 | 19312 | 21178 | 21688 | 21211 | 21609 | 21027 | 20250 | 22962 | 24098 | 22954 | 23806 | 22343
7956 | 7956 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 12 | 16707 | 17591 | 17315 | 16922 | 19401 | 18941 | 19387 | 19810 | 19115 | 21053 | 21479 | 20885 | 21277 | 20826 | 20285 | 22830 | 24194 | 22628 | 23861 | 22149
7957 | 7957 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 13 | 16518 | 17479 | 17219 | 16987 | 19212 | 18709 | 19265 | 19642 | 18927 | 20850 | 21266 | 20618 | 21102 | 20554 | 20191 | 22512 | 24050 | 22456 | 23773 | 21864
7958 | 7958 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 14 | 16637 | 17512 | 17216 | 17034 | 19259 | 18814 | 19329 | 19627 | 18939 | 20842 | 21102 | 20680 | 21090 | 20450 | 20143 | 22430 | 23726 | 22421 | 23625 | 21734
7959 | 7959 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 15 | 16932 | 17568 | 17394 | 17205 | 19419 | 19079 | 19409 | 19662 | 19226 | 20916 | 21104 | 20926 | 21116 | 20622 | 20289 | 22484 | 23420 | 22413 | 23294 | 21890
7960 | 7960 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 16 | 17472 | 17783 | 17695 | 17546 | 19662 | 19533 | 19709 | 19767 | 19578 | 21002 | 21563 | 21286 | 21297 | 20770 | 20494 | 22509 | 23534 | 22491 | 22918 | 22008
7961 | 7961 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 17 | 18161 | 18455 | 18388 | 18326 | 20308 | 20214 | 20486 | 20479 | 20330 | 21711 | 22459 | 22083 | 22035 | 21625 | 21339 | 23173 | 24229 | 23241 | 23527 | 22883
7962 | 7962 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 18 | 18820 | 19073 | 19413 | 19241 | 21162 | 20889 | 21698 | 21291 | 21183 | 22745 | 23101 | 22773 | 23510 | 22980 | 22458 | 24410 | 24799 | 24855 | 24503 | 24329
7963 | 7963 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 19 | 18393 | 18725 | 19283 | 18925 | 20923 | 20685 | 21655 | 21103 | 21223 | 22564 | 23056 | 22948 | 23948 | 23409 | 22682 | 24596 | 24942 | 25542 | 24843 | 24905
7964 | 7964 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 20 | 18179 | 18369 | 18964 | 18787 | 20663 | 20647 | 21601 | 20903 | 21199 | 22540 | 23166 | 23412 | 24431 | 23716 | 23124 | 24875 | 25503 | 26253 | 25470 | 25398
7965 | 7965 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 21 | 17796 | 18057 | 18757 | 18563 | 20477 | 20449 | 21508 | 20880 | 21355 | 22596 | 23400 | 23789 | 24943 | 24368 | 23618 | 25309 | 26153 | 27084 | 26336 | 26318
7966 | 7966 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 22 | 17116 | 17511 | 18377 | 18096 | 19750 | 20003 | 20880 | 20536 | 21219 | 22070 | 23097 | 23731 | 24676 | 24578 | 23644 | 25022 | 26107 | 27027 | 26545 | 26701
7967 | 7967 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 23 | 16197 | 16701 | 17708 | 17428 | 18712 | 19144 | 19928 | 19887 | 20763 | 21156 | 22463 | 23104 | 23954 | 24246 | 23246 | 24165 | 25640 | 26407 | 26207 | 26451
7968 | 7968 | 332 | 11 | 28 | Winter | 11 | 27 | Winter | 24 | 15178 | 15681 | 16853 | 16614 | 17569 | 18208 | 18773 | 19033 | 20069 | 20128 | 21602 | 22304 | 22952 | 23657 | 22646 | 23188 | 24853 | 25467 | 25549 | 25917
7969 | 7969 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 1 | 14242 | 14987 | 15514 | 15699 | 16794 | 17031 | 18054 | 18242 | 18288 | 19662 | 20920 | 21175 | 22288 | 21429 | 21206 | 23120 | 24333 | 24823 | 24569 | 23382
7970 | 7970 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 2 | 13753 | 14475 | 14988 | 15280 | 16366 | 16551 | 17511 | 17705 | 17765 | 19214 | 20505 | 20631 | 21681 | 20862 | 20792 | 22607 | 23831 | 24136 | 23888 | 22761
7971 | 7971 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 3 | 13584 | 14204 | 14714 | 15169 | 16198 | 16486 | 17295 | 17523 | 17558 | 19084 | 20358 | 20503 | 21320 | 20548 | 20653 | 22302 | 23512 | 23683 | 23507 | 22382
7972 | 7972 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 4 | 13522 | 14029 | 14509 | 15094 | 16088 | 16364 | 17104 | 17216 | 17219 | 18801 | 19966 | 20021 | 20741 | 19961 | 20242 | 21730 | 22844 | 22870 | 22671 | 21644
7973 | 7973 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 5 | 13681 | 14043 | 14279 | 15231 | 16113 | 16430 | 17060 | 16994 | 16828 | 18600 | 19687 | 19693 | 20196 | 19189 | 19945 | 21177 | 22220 | 22060 | 21755 | 20691
7974 | 7974 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 6 | 14249 | 14200 | 14112 | 15788 | 16594 | 16865 | 17330 | 16917 | 16446 | 18792 | 19842 | 19673 | 19909 | 18421 | 19996 | 20983 | 21935 | 21516 | 20855 | 19746
7975 | 7975 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 7 | 15579 | 14667 | 14398 | 16990 | 17767 | 18143 | 18290 | 17256 | 16503 | 19629 | 20678 | 20526 | 20481 | 18176 | 20776 | 21511 | 22401 | 21882 | 20508 | 19386
7976 | 7976 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 8 | 16979 | 15568 | 15277 | 18470 | 19088 | 19552 | 19512 | 18098 | 17288 | 20840 | 21821 | 21709 | 21529 | 18796 | 22095 | 22533 | 23426 | 22829 | 21095 | 19966
7977 | 7977 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 9 | 17269 | 16332 | 15859 | 18994 | 19491 | 19802 | 19953 | 18875 | 17863 | 21314 | 21987 | 21880 | 21808 | 19218 | 22456 | 22845 | 23505 | 23061 | 21688 | 20358
7978 | 7978 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 10 | 17288 | 16828 | 16371 | 19271 | 19697 | 19727 | 20061 | 19329 | 18361 | 21589 | 22021 | 21820 | 22153 | 19829 | 22827 | 23440 | 23825 | 23449 | 22301 | 21018
7979 | 7979 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 11 | 17051 | 16841 | 16624 | 19254 | 19674 | 19354 | 19853 | 19149 | 18453 | 21534 | 21804 | 21395 | 22406 | 20068 | 22829 | 23961 | 24151 | 23758 | 22285 | 21299
7980 | 7980 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 12 | 16948 | 16856 | 16841 | 19288 | 19605 | 19097 | 19669 | 19025 | 18540 | 21349 | 21601 | 21074 | 22473 | 20134 | 22725 | 24081 | 24250 | 23846 | 22124 | 21375
7981 | 7981 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 13 | 16963 | 16825 | 16959 | 19182 | 19513 | 19029 | 19554 | 18923 | 18619 | 21182 | 21439 | 20962 | 22446 | 20086 | 22452 | 24005 | 24192 | 23800 | 21884 | 21316
7982 | 7982 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 14 | 16985 | 16718 | 16901 | 19104 | 19362 | 18996 | 19443 | 18796 | 18556 | 20925 | 21334 | 20869 | 22247 | 19938 | 22269 | 23589 | 23971 | 23550 | 21651 | 21146
7983 | 7983 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 15 | 17155 | 16939 | 17129 | 19259 | 19498 | 19150 | 19548 | 19046 | 18778 | 21000 | 21502 | 20973 | 22011 | 20151 | 22391 | 23352 | 23848 | 23285 | 21870 | 21344
7984 | 7984 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 16 | 17359 | 17075 | 17306 | 19247 | 19768 | 19302 | 19505 | 19118 | 18878 | 21291 | 21559 | 20991 | 21530 | 20197 | 22253 | 23290 | 23501 | 22745 | 21818 | 21366
7985 | 7985 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 17 | 18075 | 17735 | 18042 | 19902 | 20627 | 20051 | 20180 | 19893 | 19581 | 22145 | 22366 | 21694 | 22090 | 21006 | 22881 | 23964 | 24139 | 23321 | 22667 | 22201
7986 | 7986 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 18 | 19159 | 18732 | 18914 | 20875 | 21218 | 21259 | 20956 | 20885 | 20534 | 22743 | 23061 | 23119 | 22930 | 22091 | 24102 | 24516 | 24876 | 24273 | 24110 | 23368
7987 | 7987 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 19 | 19043 | 18556 | 18557 | 20620 | 20940 | 21166 | 20708 | 20870 | 20412 | 22603 | 23176 | 23484 | 23038 | 22253 | 24239 | 24632 | 25316 | 24586 | 24659 | 23639
7988 | 7988 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 20 | 18745 | 18214 | 18392 | 20315 | 20760 | 21083 | 20439 | 20744 | 20440 | 22630 | 23477 | 23865 | 23366 | 22644 | 24484 | 25134 | 25903 | 25203 | 25141 | 24174
7989 | 7989 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 21 | 18441 | 17987 | 18144 | 20106 | 20562 | 20932 | 20344 | 20806 | 20464 | 22779 | 23755 | 24273 | 23879 | 23085 | 24873 | 25735 | 26615 | 26047 | 26048 | 24825
7990 | 7990 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 22 | 17664 | 17566 | 17647 | 19376 | 19947 | 20249 | 19936 | 20616 | 20185 | 22410 | 23520 | 23943 | 23873 | 23066 | 24545 | 25655 | 26685 | 26240 | 26409 | 24942
7991 | 7991 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 23 | 16567 | 16906 | 16969 | 18324 | 19110 | 19276 | 19256 | 20115 | 19645 | 21760 | 22811 | 23184 | 23408 | 22659 | 23691 | 25168 | 26121 | 25901 | 26177 | 24608
7992 | 7992 | 333 | 11 | 29 | Winter | 11 | 28 | Winter | 24 | 15303 | 16040 | 16133 | 17161 | 18077 | 18089 | 18366 | 19369 | 18967 | 20900 | 21876 | 22159 | 22674 | 22049 | 22711 | 24376 | 25281 | 25229 | 25641 | 24039
7993 | 7993 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 1 | 14409 | 14609 | 15111 | 16240 | 17119 | 17236 | 17464 | 17546 | 17678 | 20070 | 21149 | 21355 | 21695 | 20521 | 22472 | 23707 | 24673 | 24117 | 22980 | 22317
7994 | 7994 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 2 | 13932 | 14086 | 14690 | 15807 | 16695 | 16695 | 16932 | 17028 | 17286 | 19684 | 20710 | 20757 | 21084 | 20102 | 21959 | 23198 | 24139 | 23427 | 22340 | 21855
7995 | 7995 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 3 | 13695 | 13783 | 14549 | 15601 | 16543 | 16450 | 16723 | 16795 | 17260 | 19534 | 20556 | 20432 | 20805 | 19986 | 21671 | 22894 | 23843 | 23061 | 21973 | 21694
7996 | 7996 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 4 | 13601 | 13581 | 14478 | 15513 | 16396 | 16299 | 16468 | 16510 | 17076 | 19219 | 20218 | 19917 | 20189 | 19599 | 21136 | 22256 | 23209 | 22228 | 21239 | 21184
7997 | 7997 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 5 | 13658 | 13360 | 14611 | 15540 | 16474 | 16277 | 16284 | 16159 | 17049 | 18991 | 19997 | 19451 | 19541 | 19336 | 20612 | 21663 | 22603 | 21324 | 20282 | 20770
7998 | 7998 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 6 | 14167 | 13203 | 15183 | 16059 | 16997 | 16594 | 16286 | 15874 | 17421 | 19224 | 20101 | 19261 | 18935 | 19408 | 20444 | 21414 | 22294 | 20431 | 19334 | 20710
7999 | 7999 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 7 | 15303 | 13495 | 16422 | 17261 | 18096 | 17593 | 16702 | 15983 | 18561 | 20129 | 21026 | 19916 | 18809 | 20234 | 21023 | 21921 | 22969 | 20119 | 18988 | 21462
8000 | 8000 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 8 | 16453 | 14383 | 17880 | 18609 | 19378 | 18821 | 17568 | 16804 | 20040 | 21310 | 22424 | 20987 | 19468 | 21542 | 22063 | 22951 | 24230 | 20700 | 19564 | 22744
8001 | 8001 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 9 | 16837 | 15018 | 18452 | 19020 | 19668 | 19291 | 18383 | 17422 | 20598 | 21534 | 22656 | 21329 | 20159 | 21965 | 22417 | 23091 | 24407 | 21335 | 19992 | 23124
8002 | 8002 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 10 | 16805 | 15449 | 18688 | 19168 | 19522 | 19385 | 18833 | 17932 | 20696 | 21593 | 22562 | 21508 | 20551 | 22178 | 22857 | 23253 | 24400 | 21791 | 20497 | 23370
8003 | 8003 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 11 | 16691 | 15877 | 18883 | 19368 | 19315 | 19479 | 18992 | 18398 | 20476 | 21775 | 22495 | 21689 | 20402 | 22112 | 23312 | 23514 | 24401 | 21707 | 20709 | 23337
8004 | 8004 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 12 | 16492 | 16084 | 18938 | 19338 | 19047 | 19369 | 18962 | 18605 | 20227 | 21698 | 22342 | 21600 | 20060 | 21856 | 23280 | 23473 | 24249 | 21393 | 20638 | 23098
8005 | 8005 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 13 | 16147 | 15952 | 18592 | 19009 | 18655 | 19041 | 18653 | 18468 | 19794 | 21342 | 22063 | 21262 | 19553 | 21283 | 22898 | 23102 | 23980 | 20853 | 20274 | 22515
8006 | 8006 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 14 | 16139 | 15932 | 18537 | 18881 | 18659 | 18951 | 18540 | 18398 | 19754 | 21243 | 21969 | 21100 | 19417 | 21151 | 22533 | 22913 | 23811 | 20667 | 20151 | 22361
8007 | 8007 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 15 | 16257 | 16028 | 18528 | 18862 | 18849 | 18839 | 18546 | 18366 | 19894 | 21119 | 21905 | 20864 | 19656 | 21259 | 22288 | 22783 | 23741 | 20871 | 20336 | 22452
8008 | 8008 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 16 | 16573 | 16311 | 18612 | 19205 | 19242 | 18837 | 18628 | 18468 | 20074 | 21130 | 21928 | 20655 | 19901 | 21368 | 22476 | 22691 | 23655 | 21059 | 20598 | 22541
8009 | 8009 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 17 | 17500 | 17249 | 19476 | 20263 | 20236 | 19691 | 19561 | 19306 | 21037 | 22059 | 22740 | 21505 | 21008 | 22298 | 23444 | 23617 | 24514 | 22210 | 21731 | 23489
8010 | 8010 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 18 | 18161 | 18079 | 20397 | 20821 | 21092 | 20388 | 20432 | 20093 | 22125 | 22570 | 23768 | 22369 | 22407 | 23570 | 24053 | 24405 | 25666 | 23732 | 22959 | 24837
8011 | 8011 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 19 | 17786 | 17700 | 20108 | 20488 | 20951 | 20095 | 20361 | 19886 | 21870 | 22586 | 23861 | 22378 | 22745 | 23661 | 24126 | 24796 | 26076 | 24270 | 23233 | 25020
8012 | 8012 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 20 | 17418 | 17508 | 19786 | 20296 | 20885 | 19792 | 20185 | 19882 | 21799 | 22812 | 24134 | 22635 | 22988 | 23884 | 24595 | 25365 | 26712 | 24757 | 23793 | 25353
8013 | 8013 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 21 | 17073 | 17238 | 19552 | 20057 | 20689 | 19631 | 20162 | 19829 | 21784 | 22978 | 24345 | 23044 | 23552 | 24222 | 25136 | 26024 | 27349 | 25634 | 24417 | 25855
8014 | 8014 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 22 | 16531 | 16760 | 18826 | 19434 | 20148 | 19203 | 19937 | 19517 | 21229 | 22717 | 24005 | 22984 | 23724 | 23883 | 25045 | 26078 | 27287 | 25991 | 24546 | 25621
8015 | 8015 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 23 | 15756 | 16108 | 17779 | 18608 | 19236 | 18509 | 19420 | 18971 | 20327 | 22003 | 23245 | 22522 | 23400 | 23041 | 24563 | 25530 | 26689 | 25772 | 24237 | 24844
8016 | 8016 | 334 | 11 | 30 | Winter | 11 | 29 | Winter | 24 | 14744 | 15254 | 16596 | 17561 | 18151 | 17586 | 18639 | 18256 | 19280 | 21060 | 22219 | 21770 | 22804 | 22056 | 23771 | 24684 | 25730 | 25233 | 23671 | 23899
8017 | 8017 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 1 | 14151 | 14621 | 16014 | 16932 | 17527 | 17087 | 17278 | 17434 | 18914 | 20722 | 20011 | 21110 | 20798 | 22057 | 23351 | 24346 | 23497 | 22866 | 22256 | 24065
8018 | 8018 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 2 | 13671 | 14228 | 15613 | 16543 | 17122 | 16595 | 16799 | 17103 | 18495 | 20354 | 19557 | 20545 | 20236 | 21579 | 22874 | 23841 | 22898 | 22251 | 21815 | 23547
8019 | 8019 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 3 | 13394 | 14090 | 15415 | 16376 | 16986 | 16405 | 16596 | 17074 | 18349 | 20270 | 19396 | 20294 | 19960 | 21323 | 22614 | 23584 | 22615 | 21911 | 21668 | 23235
8020 | 8020 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 4 | 13235 | 14030 | 15344 | 16266 | 16901 | 16192 | 16358 | 16958 | 18141 | 20015 | 18990 | 19751 | 19425 | 20834 | 22015 | 22983 | 21894 | 21193 | 21164 | 22594
8021 | 8021 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 5 | 13263 | 14173 | 15389 | 16371 | 16970 | 16062 | 16063 | 16981 | 17994 | 19882 | 18732 | 19196 | 18719 | 20364 | 21472 | 22425 | 21342 | 20259 | 20761 | 21939
8022 | 8022 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 6 | 13419 | 14722 | 15885 | 16880 | 17391 | 16074 | 15798 | 17365 | 18260 | 20023 | 18783 | 18669 | 18003 | 20249 | 21272 | 22133 | 21065 | 19333 | 20708 | 21650
8023 | 8023 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 7 | 13922 | 15972 | 17113 | 17993 | 18630 | 16515 | 15940 | 18529 | 19175 | 20986 | 19610 | 18649 | 17825 | 20881 | 21831 | 22852 | 21585 | 19012 | 21473 | 22151
8024 | 8024 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 8 | 14795 | 17408 | 18458 | 19274 | 20158 | 17338 | 16742 | 20007 | 20431 | 22373 | 20823 | 19330 | 18459 | 21947 | 22882 | 24131 | 22611 | 19587 | 22746 | 23128
8025 | 8025 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 9 | 15600 | 17967 | 18868 | 19552 | 20442 | 18132 | 17348 | 20548 | 20946 | 22597 | 21162 | 20054 | 18944 | 22320 | 23048 | 24322 | 22885 | 20022 | 23145 | 23465
8026 | 8026 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 10 | 16175 | 18285 | 19069 | 19593 | 20457 | 18609 | 17871 | 20847 | 21379 | 22491 | 21299 | 20577 | 19535 | 22869 | 23326 | 24448 | 23129 | 20643 | 23511 | 24070
8027 | 8027 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 11 | 16472 | 18445 | 19206 | 19629 | 20498 | 18614 | 18156 | 20894 | 21856 | 22170 | 21208 | 20555 | 19842 | 23430 | 23701 | 24582 | 23220 | 20968 | 23595 | 24688
8028 | 8028 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 12 | 16658 | 18568 | 19229 | 19581 | 20548 | 18548 | 18296 | 20849 | 22001 | 21886 | 21050 | 20417 | 19961 | 23577 | 23831 | 24637 | 23431 | 21081 | 23534 | 24844
8029 | 8029 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 13 | 16691 | 18493 | 19153 | 19467 | 20575 | 18435 | 18336 | 20659 | 21957 | 21751 | 20905 | 20240 | 19924 | 23545 | 23809 | 24690 | 23377 | 21066 | 23299 | 24802
8030 | 8030 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 14 | 16555 | 18413 | 19029 | 19410 | 20487 | 18312 | 18255 | 20545 | 21659 | 21655 | 20767 | 20068 | 19770 | 23167 | 23602 | 24481 | 23209 | 20921 | 23123 | 24385
8031 | 8031 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 15 | 16495 | 18427 | 19060 | 19462 | 20421 | 18427 | 18355 | 20553 | 21322 | 21765 | 20700 | 20169 | 19837 | 22803 | 23347 | 24275 | 23008 | 20980 | 23087 | 23989
8032 | 8032 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 16 | 16503 | 18402 | 19264 | 19596 | 20409 | 18510 | 18478 | 20477 | 21316 | 21848 | 20620 | 20164 | 19875 | 22753 | 23009 | 23932 | 22689 | 20987 | 22920 | 23896
8033 | 8033 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 17 | 17106 | 19057 | 20112 | 20303 | 21063 | 19279 | 19157 | 21142 | 22020 | 22526 | 21316 | 20988 | 20693 | 23435 | 23646 | 24521 | 23155 | 21831 | 23586 | 24601
8034 | 8034 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 18 | 17981 | 19959 | 20703 | 21054 | 21935 | 20221 | 19998 | 22067 | 22369 | 23594 | 22312 | 22221 | 21718 | 23920 | 24307 | 25549 | 24161 | 22958 | 24832 | 25153
8035 | 8035 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 19 | 17779 | 19641 | 20347 | 20872 | 21693 | 20129 | 19761 | 21756 | 22146 | 23605 | 22206 | 22489 | 21819 | 23939 | 24646 | 25920 | 24457 | 23226 | 25013 | 25297
8036 | 8036 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 20 | 17417 | 19305 | 20124 | 20762 | 21637 | 19905 | 19714 | 21629 | 22107 | 23789 | 22271 | 22642 | 22175 | 24351 | 25168 | 26520 | 24885 | 23783 | 25338 | 25879
8037 | 8037 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 21 | 17173 | 19082 | 19864 | 20535 | 21434 | 19833 | 19609 | 21565 | 22169 | 23916 | 22508 | 23119 | 22545 | 24839 | 25786 | 27116 | 25557 | 24405 | 25846 | 26589
8038 | 8038 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 22 | 16721 | 18317 | 19197 | 19944 | 20793 | 19551 | 19240 | 20959 | 21749 | 23518 | 22220 | 23200 | 22472 | 24690 | 25784 | 26992 | 25528 | 24485 | 25586 | 26577
8039 | 8039 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 23 | 16061 | 17230 | 18322 | 18978 | 19825 | 18964 | 18622 | 19979 | 21061 | 22689 | 21583 | 22824 | 22049 | 24173 | 25202 | 26372 | 25036 | 24153 | 24782 | 26146
8040 | 8040 | 335 | 12 | 1 | Winter | 11 | 30 | Winter | 24 | 15200 | 16049 | 17262 | 17891 | 18632 | 18173 | 17897 | 18921 | 20173 | 21678 | 20704 | 22205 | 21428 | 23367 | 24347 | 25403 | 24202 | 23578 | 23830 | 25382
8041 | 8041 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 1 | 14109 | 15397 | 16597 | 17258 | 16298 | 16821 | 17044 | 18531 | 19680 | 19403 | 19828 | 20262 | 20210 | 22907 | 23957 | 23121 | 23167 | 22131 | 23964 | 25003
8042 | 8042 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 2 | 13640 | 14986 | 16197 | 16866 | 15854 | 16329 | 16696 | 18140 | 19352 | 18967 | 19337 | 19729 | 19823 | 22443 | 23458 | 22542 | 22596 | 21683 | 23432 | 24493
8043 | 8043 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 3 | 13341 | 14750 | 15981 | 16708 | 15674 | 16090 | 16636 | 18000 | 19222 | 18811 | 19198 | 19453 | 19710 | 22161 | 23180 | 22249 | 22343 | 21511 | 23093 | 24148
8044 | 8044 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 4 | 13161 | 14689 | 15893 | 16647 | 15541 | 15881 | 16556 | 17847 | 18993 | 18484 | 18879 | 18979 | 19379 | 21623 | 22628 | 21569 | 21738 | 21028 | 22463 | 23449
8045 | 8045 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 5 | 12960 | 14760 | 16010 | 16728 | 15615 | 15624 | 16622 | 17754 | 18836 | 18312 | 18445 | 18331 | 19167 | 21134 | 22119 | 21045 | 20957 | 20644 | 21824 | 22760
8046 | 8046 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 6 | 12786 | 15258 | 16531 | 17155 | 16064 | 15405 | 17075 | 18036 | 19089 | 18463 | 18023 | 17701 | 19294 | 20995 | 21880 | 20813 | 20172 | 20615 | 21546 | 22425
8047 | 8047 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 7 | 13063 | 16483 | 17639 | 18379 | 17115 | 15569 | 18270 | 18976 | 20015 | 19351 | 18210 | 17581 | 20151 | 21586 | 22620 | 21351 | 20143 | 21367 | 22041 | 22853
8048 | 8048 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 8 | 13948 | 17846 | 18960 | 19903 | 18419 | 16401 | 19794 | 20259 | 21217 | 20622 | 19217 | 18270 | 21497 | 22701 | 23940 | 22428 | 21038 | 22675 | 23036 | 23869
8049 | 8049 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 9 | 14548 | 18266 | 19241 | 20153 | 18811 | 17001 | 20331 | 20768 | 21395 | 20975 | 19908 | 18768 | 21900 | 22876 | 24137 | 22702 | 21554 | 23066 | 23383 | 23970
8050 | 8050 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 10 | 15007 | 18406 | 19253 | 20041 | 18896 | 17475 | 20583 | 21017 | 21418 | 21053 | 20239 | 19289 | 22188 | 23110 | 24215 | 22881 | 21935 | 23386 | 23940 | 24239
8051 | 8051 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 11 | 15382 | 18529 | 19272 | 19807 | 18844 | 17728 | 20591 | 21096 | 21343 | 20894 | 20287 | 19515 | 22201 | 23430 | 24296 | 22897 | 22050 | 23415 | 24507 | 24595
8052 | 8052 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 12 | 15636 | 18529 | 19222 | 19631 | 18767 | 17852 | 20531 | 20918 | 21143 | 20689 | 20143 | 19575 | 22119 | 23517 | 24308 | 23048 | 21935 | 23318 | 24626 | 24689
8053 | 8053 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 13 | 15747 | 18481 | 19129 | 19573 | 18664 | 17910 | 20354 | 20725 | 20918 | 20553 | 19901 | 19574 | 21875 | 23498 | 24364 | 23022 | 21651 | 23083 | 24582 | 24666
8054 | 8054 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 14 | 15812 | 18509 | 19181 | 19636 | 18670 | 17939 | 20353 | 20585 | 20912 | 20530 | 19726 | 19563 | 21825 | 23399 | 24265 | 22993 | 21424 | 23012 | 24273 | 24542
8055 | 8055 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 15 | 15927 | 18559 | 19249 | 19798 | 18661 | 18058 | 20384 | 20562 | 20988 | 20489 | 19695 | 19665 | 21843 | 23170 | 24083 | 22825 | 21366 | 22999 | 23896 | 24295
8056 | 8056 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 16 | 16060 | 18698 | 19372 | 19984 | 18686 | 18176 | 20302 | 20799 | 21040 | 20409 | 19697 | 19704 | 21689 | 22825 | 23733 | 22503 | 21301 | 22815 | 23785 | 23922
8057 | 8057 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 17 | 16775 | 19542 | 20082 | 20742 | 19372 | 18863 | 20965 | 21650 | 21842 | 21099 | 20584 | 20518 | 22335 | 23459 | 24324 | 22969 | 22244 | 23480 | 24493 | 24593
8058 | 8058 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 18 | 17570 | 20166 | 20865 | 21739 | 20234 | 19728 | 21876 | 22202 | 22431 | 22047 | 21576 | 21488 | 23478 | 24098 | 25341 | 23969 | 23457 | 24726 | 25059 | 25317
8059 | 8059 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 19 | 17194 | 19803 | 20684 | 21485 | 19947 | 19489 | 21557 | 21947 | 22396 | 21870 | 21524 | 21541 | 23531 | 24402 | 25682 | 24245 | 23636 | 24925 | 25223 | 25773
8060 | 8060 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 20 | 16979 | 19526 | 20534 | 21399 | 19593 | 19404 | 21394 | 21838 | 22541 | 21835 | 21474 | 21824 | 23712 | 24862 | 26226 | 24632 | 24014 | 25255 | 25782 | 26417
8061 | 8061 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 21 | 16741 | 19255 | 20284 | 21180 | 19427 | 19264 | 21285 | 21839 | 22660 | 21988 | 21734 | 22127 | 24022 | 25412 | 26783 | 25271 | 24710 | 25758 | 26499 | 27222
8062 | 8062 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 22 | 16236 | 18570 | 19661 | 20535 | 18853 | 18845 | 20631 | 21378 | 22339 | 21637 | 21632 | 22000 | 23619 | 25355 | 26619 | 25202 | 24843 | 25477 | 26473 | 27331
8063 | 8063 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 23 | 15559 | 17701 | 18696 | 19566 | 18019 | 18228 | 19651 | 20659 | 21541 | 21000 | 21239 | 21580 | 22747 | 24777 | 26007 | 24723 | 24560 | 24694 | 26056 | 26824
8064 | 8064 | 336 | 12 | 2 | Winter | 12 | 1 | Winter | 24 | 14704 | 16654 | 17609 | 18402 | 16974 | 17499 | 18592 | 19784 | 20597 | 20141 | 20552 | 20971 | 21757 | 23946 | 25059 | 23910 | 23907 | 23762 | 25317 | 26037
8065 | 8065 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 1 | 14003 | 15987 | 16946 | 16017 | 16129 | 16662 | 18127 | 19213 | 20102 | 19273 | 19511 | 19791 | 21628 | 23502 | 22750 | 22851 | 22340 | 23863 | 24925 | 25682
8066 | 8066 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 2 | 13620 | 15551 | 16535 | 15538 | 15649 | 16287 | 17715 | 18858 | 19739 | 18789 | 19137 | 19400 | 21163 | 23009 | 22171 | 22267 | 21858 | 23316 | 24401 | 25121
8067 | 8067 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 3 | 13478 | 15315 | 16359 | 15346 | 15503 | 16212 | 17568 | 18729 | 19655 | 18680 | 19041 | 19312 | 20916 | 22753 | 21897 | 22035 | 21635 | 22982 | 24063 | 24797
8068 | 8068 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 4 | 13425 | 15236 | 16302 | 15222 | 15384 | 16143 | 17445 | 18543 | 19458 | 18415 | 18757 | 19025 | 20473 | 22245 | 21256 | 21451 | 21103 | 22362 | 23371 | 24127
8069 | 8069 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 5 | 13566 | 15335 | 16379 | 15305 | 15255 | 16217 | 17380 | 18434 | 19385 | 18039 | 18430 | 18856 | 20055 | 21771 | 20761 | 20696 | 20519 | 21722 | 22674 | 23465
8070 | 8070 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 6 | 14115 | 15848 | 16837 | 15792 | 15241 | 16697 | 17716 | 18753 | 19602 | 17688 | 18220 | 19046 | 19988 | 21579 | 20570 | 19944 | 19978 | 21456 | 22341 | 23094
8071 | 8071 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 7 | 15340 | 16978 | 18087 | 16850 | 15762 | 17903 | 18714 | 19722 | 20605 | 17929 | 18391 | 19940 | 20647 | 22343 | 21130 | 19927 | 19909 | 21954 | 22766 | 23752
8072 | 8072 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 8 | 16798 | 18296 | 19606 | 18141 | 16811 | 19409 | 20027 | 20954 | 22045 | 18947 | 18978 | 21305 | 21759 | 23661 | 22209 | 20815 | 20507 | 22949 | 23765 | 25024
8073 | 8073 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 9 | 17335 | 18578 | 19833 | 18526 | 17510 | 19903 | 20511 | 21161 | 22276 | 19646 | 19586 | 21730 | 22153 | 23835 | 22460 | 21352 | 21164 | 23264 | 23840 | 25172
8074 | 8074 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 10 | 17649 | 18629 | 19761 | 18641 | 17846 | 20176 | 20769 | 21208 | 22151 | 19993 | 20020 | 22036 | 22672 | 23931 | 22657 | 21750 | 21800 | 23839 | 24134 | 25288
8075 | 8075 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 11 | 17770 | 18709 | 19578 | 18621 | 17977 | 20221 | 20867 | 21155 | 21804 | 20055 | 20103 | 22045 | 23192 | 24024 | 22684 | 21866 | 22291 | 24419 | 24508 | 25403
8076 | 8076 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 12 | 17847 | 18688 | 19436 | 18550 | 17930 | 20187 | 20712 | 20954 | 21475 | 19913 | 20010 | 21938 | 23281 | 24035 | 22833 | 21730 | 22486 | 24538 | 24603 | 25424
8077 | 8077 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 13 | 17784 | 18602 | 19395 | 18481 | 17794 | 20023 | 20532 | 20759 | 21362 | 19670 | 19864 | 21711 | 23262 | 24095 | 22804 | 21464 | 22531 | 24492 | 24584 | 25493
8078 | 8078 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 14 | 17765 | 18624 | 19429 | 18460 | 17647 | 19992 | 20370 | 20727 | 21338 | 19466 | 19768 | 21633 | 22955 | 23965 | 22743 | 21208 | 22334 | 24149 | 24423 | 25340
8079 | 8079 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 15 | 17824 | 18724 | 19629 | 18478 | 17663 | 20065 | 20395 | 20833 | 21498 | 19477 | 19903 | 21684 | 22640 | 23830 | 22618 | 21179 | 22155 | 23814 | 24215 | 25175
8080 | 8080 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 16 | 17796 | 18856 | 19836 | 18526 | 17768 | 20006 | 20628 | 20910 | 21598 | 19501 | 20084 | 21554 | 22590 | 23506 | 22319 | 21130 | 21962 | 23716 | 23852 | 24796
8081 | 8081 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 17 | 18444 | 19555 | 20586 | 19197 | 18617 | 20674 | 21482 | 21700 | 22268 | 20378 | 21066 | 22183 | 23262 | 24094 | 22782 | 22061 | 22775 | 24424 | 24519 | 25400
8082 | 8082 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 18 | 19347 | 20362 | 21553 | 20055 | 19423 | 21612 | 22062 | 22305 | 23322 | 21323 | 22161 | 23283 | 23739 | 25094 | 23767 | 23270 | 23943 | 25001 | 25255 | 26483
8083 | 8083 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 19 | 19032 | 20158 | 21269 | 19731 | 19118 | 21279 | 21771 | 22212 | 23278 | 21182 | 22317 | 23277 | 23706 | 25383 | 23994 | 23411 | 24355 | 25155 | 25687 | 26906
8084 | 8084 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 20 | 18691 | 19964 | 21164 | 19362 | 18836 | 21104 | 21620 | 22295 | 23384 | 21056 | 22375 | 23412 | 24061 | 25887 | 24346 | 23763 | 24609 | 25724 | 26345 | 27570
8085 | 8085 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 21 | 18448 | 19666 | 20906 | 19134 | 18661 | 20944 | 21539 | 22300 | 23409 | 21214 | 22501 | 23624 | 24467 | 26360 | 24914 | 24389 | 25057 | 26399 | 27117 | 28275
8086 | 8086 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 22 | 17679 | 19042 | 20258 | 18555 | 18286 | 20273 | 21039 | 21929 | 22960 | 21078 | 22173 | 23192 | 24279 | 26176 | 24830 | 24510 | 24903 | 26377 | 27230 | 28223
8087 | 8087 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 23 | 16599 | 18013 | 19223 | 17688 | 17696 | 19227 | 20243 | 21073 | 22106 | 20615 | 21582 | 22276 | 23744 | 25500 | 24289 | 24196 | 24487 | 25912 | 26683 | 27629
8088 | 8088 | 337 | 12 | 3 | Winter | 12 | 2 | Winter | 24 | 15428 | 16890 | 18000 | 16627 | 16826 | 18112 | 19304 | 20088 | 21085 | 19890 | 20892 | 21271 | 22940 | 24510 | 23438 | 23533 | 23868 | 25132 | 25864 | 26696
8089 | 8089 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 1 | 14681 | 16096 | 15494 | 15690 | 16169 | 17444 | 18545 | 19445 | 18695 | 18821 | 20121 | 20986 | 22362 | 22101 | 22301 | 21949 | 22989 | 24614 | 25416 | 24302
8090 | 8090 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 2 | 14247 | 15671 | 15000 | 15161 | 15751 | 17001 | 18160 | 19045 | 18238 | 18443 | 19818 | 20518 | 21883 | 21536 | 21727 | 21456 | 22592 | 24089 | 24862 | 23671
8091 | 8091 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 3 | 14023 | 15469 | 14793 | 14972 | 15615 | 16832 | 18013 | 18924 | 18101 | 18346 | 19789 | 20308 | 21634 | 21306 | 21534 | 21254 | 22456 | 23782 | 24562 | 23374
8092 | 8092 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 4 | 13972 | 15412 | 14673 | 14853 | 15501 | 16722 | 17844 | 18772 | 17830 | 18101 | 19665 | 19925 | 21140 | 20711 | 20985 | 20748 | 22111 | 23091 | 23899 | 22608
8093 | 8093 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 5 | 14056 | 15518 | 14800 | 14763 | 15487 | 16724 | 17823 | 18785 | 17732 | 17869 | 19688 | 19584 | 20718 | 20291 | 20293 | 20205 | 21827 | 22435 | 23257 | 21989
8094 | 8094 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 6 | 14556 | 16002 | 15326 | 14786 | 15593 | 17114 | 18210 | 19099 | 17966 | 17726 | 20060 | 19594 | 20638 | 20153 | 19582 | 19694 | 21932 | 22120 | 22890 | 21665
8095 | 8095 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 7 | 15770 | 17288 | 16427 | 15336 | 15933 | 18163 | 19249 | 20182 | 18901 | 17962 | 21282 | 20314 | 21266 | 20752 | 19600 | 19643 | 23025 | 22569 | 23552 | 22159
8096 | 8096 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 8 | 17151 | 18840 | 17760 | 16409 | 16613 | 19554 | 20549 | 21706 | 20208 | 18634 | 22760 | 21488 | 22411 | 21870 | 20524 | 20257 | 24424 | 23600 | 24853 | 23231
8097 | 8097 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 9 | 17478 | 19007 | 18114 | 17048 | 17223 | 19993 | 20756 | 21901 | 20498 | 19254 | 22923 | 21811 | 22544 | 22070 | 21014 | 20834 | 24517 | 23634 | 24928 | 23401
8098 | 8098 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 10 | 16993 | 18394 | 17685 | 16854 | 17019 | 19713 | 20292 | 21291 | 19952 | 19214 | 22420 | 21676 | 22152 | 21620 | 20769 | 20830 | 24036 | 23282 | 24411 | 22978
8099 | 8099 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 11 | 16910 | 18178 | 17656 | 17016 | 16959 | 19859 | 20334 | 21076 | 19584 | 19448 | 22209 | 21954 | 22252 | 21411 | 20652 | 21097 | 23841 | 23427 | 24299 | 22797
8100 | 8100 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 12 | 16797 | 18057 | 17629 | 17063 | 16855 | 19825 | 20271 | 20921 | 19248 | 19528 | 21922 | 21924 | 22197 | 21413 | 20373 | 21170 | 23548 | 23380 | 24174 | 22815
8101 | 8101 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 13 | 16918 | 18276 | 17846 | 17222 | 16973 | 19978 | 20424 | 21155 | 19278 | 19755 | 21858 | 22055 | 22335 | 21548 | 20271 | 21369 | 23459 | 23511 | 24410 | 22957
8102 | 8102 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 14 | 17228 | 18597 | 18089 | 17344 | 17227 | 20082 | 20644 | 21383 | 19509 | 19899 | 21886 | 22051 | 22488 | 21777 | 20306 | 21466 | 23442 | 23638 | 24543 | 23170
8103 | 8103 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 15 | 17510 | 18841 | 18144 | 17394 | 17571 | 20099 | 20704 | 21501 | 19695 | 19944 | 21835 | 21935 | 22483 | 21829 | 20451 | 21475 | 23367 | 23600 | 24551 | 23198
8104 | 8104 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 16 | 17800 | 19068 | 18201 | 17475 | 17988 | 20268 | 20691 | 21493 | 19814 | 19970 | 21848 | 22034 | 22327 | 21706 | 20572 | 21444 | 23332 | 23396 | 24338 | 23019
8105 | 8105 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 17 | 18799 | 19906 | 18932 | 18383 | 19030 | 21152 | 21491 | 22163 | 20674 | 20908 | 22690 | 22883 | 23129 | 22338 | 21672 | 22438 | 24301 | 24235 | 25113 | 23674
8106 | 8106 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 18 | 19463 | 20804 | 19664 | 19075 | 20145 | 21622 | 21961 | 23013 | 21642 | 21759 | 23762 | 23342 | 23790 | 23314 | 22875 | 23610 | 25518 | 24988 | 26199 | 24739
8107 | 8107 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 19 | 19106 | 20536 | 19333 | 18762 | 20131 | 21334 | 21851 | 22932 | 21420 | 21860 | 23918 | 23273 | 24053 | 23512 | 22997 | 24018 | 25933 | 25446 | 26646 | 25080
8108 | 8108 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 20 | 18810 | 20400 | 18921 | 18450 | 19931 | 21137 | 21863 | 22963 | 21311 | 21835 | 24224 | 23557 | 24453 | 23796 | 23293 | 24238 | 26502 | 26068 | 27295 | 25526
8109 | 8109 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 21 | 18528 | 20161 | 18694 | 18286 | 19756 | 21021 | 21824 | 22942 | 21385 | 21912 | 24338 | 23914 | 24939 | 24326 | 23892 | 24693 | 26941 | 26857 | 28012 | 26275
8110 | 8110 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 22 | 17862 | 19504 | 18102 | 17909 | 19208 | 20479 | 21396 | 22453 | 21002 | 21554 | 23804 | 23691 | 24861 | 24213 | 23996 | 24537 | 26584 | 26964 | 27971 | 26298
8111 | 8111 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 23 | 16940 | 18458 | 17233 | 17299 | 18448 | 19677 | 20538 | 21562 | 20289 | 20977 | 22738 | 23094 | 24226 | 23648 | 23662 | 24080 | 25642 | 26402 | 27364 | 25824
8112 | 8112 | 338 | 12 | 4 | Winter | 12 | 3 | Winter | 24 | 15864 | 17252 | 16156 | 16403 | 17648 | 18714 | 19519 | 20489 | 19390 | 20287 | 21535 | 22266 | 23361 | 22797 | 22997 | 23447 | 24469 | 25581 | 26443 | 25032
8113 | 8113 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 1 | 15082 | 14713 | 15180 | 15685 | 16899 | 17891 | 18799 | 17955 | 18374 | 19497 | 21359 | 21633 | 22787 | 21667 | 21445 | 22543 | 24556 | 25102 | 24028 | 23807
8114 | 8114 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 2 | 14649 | 14218 | 14663 | 15265 | 16601 | 17514 | 18416 | 17509 | 17891 | 19234 | 20904 | 21204 | 22327 | 21128 | 20979 | 22188 | 24000 | 24569 | 23419 | 23215
8115 | 8115 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 3 | 14412 | 13963 | 14449 | 15088 | 16539 | 17348 | 18286 | 17339 | 17766 | 19218 | 20754 | 20990 | 22114 | 20946 | 20786 | 22068 | 23741 | 24271 | 23117 | 22981
8116 | 8116 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 4 | 14329 | 13858 | 14331 | 14960 | 16580 | 17204 | 18169 | 17103 | 17539 | 19148 | 20440 | 20552 | 21662 | 20440 | 20303 | 21749 | 23152 | 23627 | 22353 | 22319
8117 | 8117 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 5 | 14453 | 13994 | 14246 | 14964 | 16777 | 17216 | 18224 | 17077 | 17255 | 19219 | 20239 | 20192 | 21260 | 19793 | 19794 | 21480 | 22670 | 22995 | 21737 | 21479
8118 | 8118 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 6 | 14957 | 14532 | 14293 | 15086 | 17393 | 17650 | 18603 | 17396 | 16978 | 19652 | 20405 | 20174 | 21130 | 19132 | 19315 | 21600 | 22567 | 22639 | 21416 | 20630
8119 | 8119 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 7 | 16130 | 15672 | 14883 | 15470 | 18882 | 18756 | 19756 | 18436 | 17311 | 20936 | 21155 | 20883 | 21960 | 19203 | 19306 | 22728 | 23002 | 23322 | 21924 | 20578
8120 | 8120 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 8 | 17459 | 16949 | 15948 | 16136 | 20441 | 20057 | 21279 | 19783 | 18397 | 22433 | 22200 | 22046 | 23324 | 20123 | 19899 | 24127 | 23818 | 24608 | 22974 | 21457
8121 | 8121 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 9 | 17766 | 17343 | 16634 | 16807 | 20658 | 20307 | 21523 | 20157 | 19145 | 22652 | 22488 | 22230 | 23486 | 20665 | 20536 | 24244 | 24018 | 24725 | 23184 | 21965
8122 | 8122 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 10 | 17728 | 17388 | 16927 | 17200 | 20583 | 20309 | 21390 | 20247 | 19490 | 22633 | 22686 | 22318 | 23420 | 20896 | 21009 | 24254 | 24295 | 24695 | 23245 | 22236
8123 | 8123 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 11 | 17956 | 17580 | 17304 | 17617 | 20545 | 20548 | 21382 | 20449 | 19907 | 22630 | 22947 | 22629 | 23485 | 20984 | 21484 | 24276 | 24638 | 24797 | 23276 | 22362
8124 | 8124 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 12 | 18165 | 17793 | 17593 | 17972 | 20511 | 20722 | 21462 | 20646 | 20160 | 22577 | 22959 | 22807 | 23572 | 20939 | 21796 | 24217 | 24654 | 24912 | 23527 | 22320
8125 | 8125 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 13 | 18214 | 17894 | 17638 | 18126 | 20361 | 20762 | 21576 | 20763 | 20175 | 22400 | 22914 | 22836 | 23672 | 20727 | 21884 | 24018 | 24591 | 25014 | 23553 | 22088
8126 | 8126 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 14 | 18296 | 17963 | 17578 | 18169 | 20263 | 20798 | 21620 | 20762 | 20009 | 22239 | 22766 | 22804 | 23628 | 20573 | 21791 | 23811 | 24372 | 24950 | 23570 | 21903
8127 | 8127 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 15 | 18248 | 17814 | 17428 | 18128 | 20126 | 20660 | 21539 | 20485 | 19737 | 21973 | 22525 | 22572 | 23466 | 20503 | 21580 | 23507 | 24092 | 24740 | 23378 | 21811
8128 | 8128 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 16 | 18254 | 17754 | 17397 | 18203 | 20172 | 20536 | 21423 | 20180 | 19473 | 21847 | 22612 | 22274 | 23167 | 20483 | 21404 | 23320 | 24146 | 24381 | 23052 | 21765
8129 | 8129 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 17 | 18840 | 18288 | 18118 | 18921 | 20935 | 21158 | 21907 | 20656 | 20123 | 22478 | 23264 | 22875 | 23726 | 21382 | 22198 | 24087 | 24758 | 24960 | 23508 | 22690
8130 | 8130 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 18 | 19535 | 18960 | 18753 | 19844 | 21929 | 21629 | 22710 | 21336 | 20804 | 23450 | 23831 | 23439 | 24648 | 22518 | 23314 | 25220 | 25469 | 26008 | 24517 | 23899
8131 | 8131 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 19 | 19313 | 18564 | 18381 | 19761 | 21795 | 21466 | 22561 | 21015 | 20585 | 23506 | 23745 | 23598 | 24864 | 22559 | 23653 | 25569 | 25777 | 26410 | 24823 | 24068
8132 | 8132 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 20 | 19055 | 18144 | 18023 | 19519 | 21837 | 21409 | 22525 | 20813 | 20355 | 23724 | 24003 | 23900 | 25276 | 22783 | 23817 | 26097 | 26386 | 27038 | 25250 | 24452
8133 | 8133 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 21 | 18721 | 17855 | 17789 | 19281 | 21583 | 21262 | 22391 | 20759 | 20407 | 23718 | 24256 | 24260 | 25655 | 23274 | 24188 | 26464 | 27058 | 27704 | 25962 | 25163
8134 | 8134 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 22 | 18102 | 17265 | 17408 | 18732 | 20842 | 20793 | 21869 | 20331 | 20239 | 23167 | 23980 | 24138 | 25456 | 23354 | 24019 | 26110 | 27023 | 27658 | 26006 | 25385
8135 | 8135 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 23 | 17092 | 16388 | 16784 | 17990 | 19646 | 19910 | 20948 | 19617 | 19791 | 22088 | 23252 | 23466 | 24769 | 23008 | 23560 | 25156 | 26431 | 27050 | 25529 | 25120
8136 | 8136 | 339 | 12 | 5 | Winter | 12 | 4 | Winter | 24 | 15960 | 15321 | 15869 | 17170 | 18309 | 18861 | 19841 | 18669 | 19039 | 20886 | 22254 | 22580 | 23774 | 22340 | 22922 | 23972 | 25481 | 26122 | 24729 | 24493
8137 | 8137 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 1 | 15346 | 14522 | 15367 | 16602 | 17984 | 18264 | 17476 | 17830 | 18181 | 20817 | 21899 | 22155 | 21511 | 21038 | 22214 | 24200 | 25290 | 23877 | 23687 | 22921
8138 | 8138 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 2 | 14939 | 14013 | 14927 | 16279 | 17518 | 17865 | 17022 | 17336 | 17816 | 20378 | 21454 | 21705 | 20981 | 20577 | 21861 | 23648 | 24776 | 23269 | 23094 | 22416
8139 | 8139 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 3 | 14704 | 13743 | 14706 | 16169 | 17343 | 17706 | 16828 | 17180 | 17692 | 20232 | 21265 | 21493 | 20740 | 20376 | 21732 | 23374 | 24505 | 22948 | 22835 | 22171
8140 | 8140 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 4 | 14650 | 13618 | 14590 | 16220 | 17261 | 17616 | 16646 | 17006 | 17490 | 19988 | 20899 | 21105 | 20212 | 19940 | 21451 | 22824 | 23856 | 22215 | 22189 | 21613
8141 | 8141 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 5 | 14770 | 13528 | 14611 | 16438 | 17373 | 17717 | 16678 | 16795 | 17318 | 19868 | 20643 | 20790 | 19861 | 19484 | 21229 | 22388 | 23217 | 21624 | 21370 | 20998
8142 | 8142 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 6 | 15279 | 13593 | 14764 | 17092 | 17894 | 18142 | 17078 | 16613 | 17242 | 20113 | 20753 | 20756 | 19801 | 19056 | 21391 | 22330 | 22922 | 21329 | 20538 | 20421
8143 | 8143 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 7 | 16626 | 14206 | 15184 | 18604 | 18972 | 19334 | 18184 | 17032 | 17563 | 20942 | 21626 | 21668 | 20483 | 19088 | 22554 | 22804 | 23632 | 21855 | 20502 | 20367
8144 | 8144 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 8 | 18116 | 15248 | 15834 | 20125 | 20181 | 20819 | 19537 | 18121 | 18195 | 22008 | 22817 | 23027 | 21587 | 19667 | 23940 | 23614 | 24622 | 22897 | 21356 | 20923
8145 | 8145 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 9 | 18287 | 15915 | 16488 | 20305 | 20503 | 21045 | 19883 | 18861 | 18849 | 22298 | 23068 | 23189 | 21796 | 20290 | 24045 | 23795 | 24642 | 23075 | 21841 | 21519
8146 | 8146 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 10 | 17964 | 16044 | 16695 | 20044 | 20330 | 20714 | 19775 | 19009 | 19086 | 22290 | 22979 | 22925 | 21626 | 20566 | 23859 | 23877 | 24429 | 22950 | 21918 | 21827
8147 | 8147 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 11 | 17828 | 16291 | 17000 | 19895 | 20300 | 20588 | 19852 | 19301 | 19394 | 22420 | 23026 | 22864 | 21484 | 20919 | 23761 | 24095 | 24091 | 22863 | 21924 | 22207
8148 | 8148 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 12 | 17830 | 16441 | 17210 | 19730 | 20193 | 20518 | 19890 | 19411 | 19593 | 22275 | 22978 | 22805 | 21591 | 21078 | 23548 | 23964 | 23860 | 22956 | 21727 | 22360
8149 | 8149 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 13 | 17976 | 16522 | 17399 | 19620 | 20208 | 20657 | 20031 | 19460 | 19752 | 22262 | 22986 | 22941 | 21653 | 21202 | 23382 | 23934 | 23647 | 23006 | 21529 | 22462
8150 | 8150 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 14 | 18565 | 16912 | 17889 | 19981 | 20633 | 21145 | 20470 | 19752 | 20165 | 22556 | 23224 | 23350 | 22145 | 21548 | 23612 | 24165 | 24001 | 23453 | 21777 | 22779
8151 | 8151 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 15 | 18578 | 16772 | 17862 | 19847 | 20539 | 21082 | 20209 | 19479 | 19992 | 22319 | 23133 | 23174 | 21972 | 21337 | 23306 | 23869 | 24296 | 23258 | 21681 | 22548
8152 | 8152 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 16 | 18629 | 16745 | 17951 | 19912 | 20691 | 20994 | 19928 | 19237 | 19860 | 22387 | 22999 | 22878 | 21684 | 21151 | 23107 | 23916 | 24443 | 22920 | 21615 | 22342
8153 | 8153 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 17 | 19279 | 17474 | 18685 | 20696 | 21411 | 21507 | 20421 | 19901 | 20612 | 23033 | 23740 | 23440 | 22120 | 21945 | 23875 | 24533 | 25282 | 23379 | 22543 | 23164
8154 | 8154 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 18 | 20137 | 18115 | 19610 | 21725 | 22093 | 22358 | 21104 | 20587 | 21420 | 23571 | 24321 | 24344 | 23023 | 23052 | 25003 | 25263 | 26094 | 24406 | 23772 | 24334
8155 | 8155 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 19 | 19834 | 17729 | 19512 | 21578 | 21848 | 22198 | 20754 | 20324 | 21442 | 23414 | 24305 | 24505 | 23133 | 23361 | 25331 | 25546 | 26326 | 24718 | 23946 | 24743
8156 | 8156 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 20 | 19704 | 17394 | 19286 | 21639 | 21695 | 22168 | 20541 | 20067 | 21377 | 23626 | 24514 | 24879 | 23376 | 23521 | 25864 | 26164 | 26994 | 25179 | 24366 | 25024
8157 | 8157 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 21 | 19450 | 17191 | 19058 | 21392 | 21534 | 22015 | 20443 | 20069 | 21378 | 23816 | 24767 | 25204 | 23819 | 23870 | 26215 | 26815 | 27687 | 25899 | 25093 | 25549
8158 | 8158 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 22 | 18767 | 16775 | 18470 | 20618 | 20902 | 21430 | 19948 | 19825 | 20963 | 23470 | 24499 | 24925 | 23653 | 23650 | 25815 | 26738 | 27718 | 25904 | 25286 | 25442
8159 | 8159 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 23 | 17713 | 16130 | 17702 | 19397 | 19949 | 20473 | 19186 | 19325 | 20359 | 22707 | 23748 | 24193 | 23060 | 23170 | 24844 | 26114 | 27056 | 25410 | 25014 | 25023
8160 | 8160 | 340 | 12 | 6 | Winter | 12 | 5 | Winter | 24 | 16515 | 15208 | 16860 | 18059 | 18814 | 19338 | 18209 | 18549 | 19658 | 21709 | 22764 | 23189 | 22208 | 22530 | 23659 | 25162 | 26151 | 24604 | 24390 | 24419
8161 | 8161 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 1 | 14039 | 14611 | 16184 | 17604 | 18123 | 16870 | 17276 | 17664 | 18900 | 21244 | 21723 | 20785 | 21119 | 21685 | 23722 | 24816 | 25154 | 23418 | 22696 | 23539
8162 | 8162 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 2 | 13555 | 14174 | 15863 | 17134 | 17718 | 16422 | 16782 | 17299 | 18642 | 20833 | 21212 | 20284 | 20601 | 21353 | 23196 | 24327 | 24514 | 22831 | 22212 | 23172
8163 | 8163 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 3 | 13271 | 13939 | 15756 | 16971 | 17541 | 16252 | 16656 | 17213 | 18610 | 20719 | 21034 | 20066 | 20417 | 21235 | 22927 | 24073 | 24153 | 22569 | 21960 | 23009
8164 | 8164 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 4 | 13191 | 13818 | 15801 | 16907 | 17409 | 16098 | 16517 | 17051 | 18577 | 20421 | 20651 | 19599 | 19966 | 20977 | 22413 | 23448 | 23454 | 21932 | 21396 | 22630
8165 | 8165 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 5 | 13342 | 13846 | 16025 | 17032 | 17467 | 16162 | 16353 | 16923 | 18706 | 20236 | 20374 | 19320 | 19387 | 20795 | 22014 | 22843 | 22805 | 21129 | 20786 | 22300
8166 | 8166 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 6 | 13896 | 13994 | 16692 | 17573 | 17983 | 16589 | 16229 | 16904 | 19199 | 20408 | 20492 | 19337 | 18792 | 20982 | 21987 | 22574 | 22498 | 20305 | 20204 | 22355
8167 | 8167 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 7 | 15040 | 14389 | 18201 | 18657 | 19202 | 17690 | 16679 | 17252 | 20519 | 21314 | 21464 | 20055 | 18902 | 22143 | 22465 | 23283 | 23156 | 20254 | 20122 | 23447
8168 | 8168 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 8 | 16300 | 15059 | 19702 | 19900 | 20518 | 19026 | 17771 | 17898 | 22017 | 22519 | 22810 | 21211 | 19839 | 23544 | 23325 | 24318 | 24463 | 21125 | 20691 | 24821
8169 | 8169 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 9 | 16646 | 15688 | 19871 | 20177 | 20787 | 19326 | 18475 | 18535 | 22233 | 22750 | 23087 | 21444 | 20369 | 23667 | 23505 | 24359 | 24779 | 21607 | 21285 | 24907
8170 | 8170 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 10 | 16396 | 15750 | 19432 | 19786 | 20496 | 18995 | 18381 | 18534 | 21912 | 22399 | 22741 | 21159 | 20300 | 23366 | 23471 | 24038 | 24652 | 21569 | 21482 | 24629
8171 | 8171 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 11 | 16381 | 15843 | 19047 | 19472 | 20367 | 18754 | 18326 | 18497 | 21697 | 22047 | 22433 | 20920 | 20171 | 23165 | 23580 | 23610 | 24711 | 21470 | 21760 | 24449
8172 | 8172 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 12 | 16387 | 16052 | 18877 | 19316 | 20260 | 18777 | 18419 | 18648 | 21444 | 21981 | 22312 | 20966 | 19919 | 22932 | 23420 | 23309 | 24584 | 21248 | 21891 | 24213
8173 | 8173 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 13 | 16565 | 16263 | 18778 | 19324 | 20314 | 18897 | 18453 | 18775 | 21348 | 21954 | 22229 | 21064 | 19787 | 22814 | 23436 | 23130 | 24564 | 21097 | 22040 | 24079
8174 | 8174 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 14 | 17086 | 16812 | 19213 | 19824 | 20635 | 19429 | 18851 | 19279 | 21642 | 22309 | 22537 | 21556 | 20084 | 23065 | 23684 | 23480 | 24727 | 21361 | 22371 | 24302
8175 | 8175 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 15 | 17015 | 16949 | 19270 | 19964 | 20721 | 19409 | 18830 | 19379 | 21462 | 22489 | 22512 | 21480 | 20089 | 22846 | 23479 | 23866 | 24462 | 21350 | 22224 | 24061
8176 | 8176 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 16 | 16965 | 17163 | 19476 | 20276 | 20798 | 19328 | 18791 | 19476 | 21358 | 22571 | 22459 | 21242 | 20077 | 22670 | 23552 | 24050 | 24130 | 21299 | 22032 | 23864
8177 | 8177 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 17 | 17558 | 17973 | 20340 | 21081 | 21657 | 19911 | 19538 | 20306 | 22057 | 23378 | 23246 | 21732 | 21032 | 23496 | 24226 | 24946 | 24930 | 22289 | 22914 | 24721
8178 | 8178 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 18 | 18267 | 18967 | 21425 | 21864 | 22297 | 20679 | 20281 | 21159 | 23092 | 23972 | 24298 | 22647 | 22205 | 24669 | 24995 | 25817 | 26264 | 23584 | 24158 | 25962
8179 | 8179 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 19 | 17856 | 18836 | 21247 | 21585 | 22030 | 20299 | 19976 | 21129 | 23100 | 23864 | 24569 | 22683 | 22192 | 24948 | 25228 | 26005 | 26853 | 23750 | 24556 | 26338
8180 | 8180 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 20 | 17467 | 18588 | 21281 | 21388 | 21929 | 20053 | 19669 | 21007 | 23295 | 23983 | 24877 | 22848 | 22390 | 25440 | 25802 | 26631 | 27440 | 24163 | 24837 | 26938
8181 | 8181 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 21 | 17180 | 18335 | 21003 | 21157 | 21716 | 19888 | 19589 | 20924 | 23240 | 24130 | 25295 | 23178 | 22823 | 25729 | 26388 | 27268 | 28281 | 24859 | 25341 | 27399
8182 | 8182 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 22 | 16578 | 17757 | 20217 | 20506 | 21119 | 19363 | 19303 | 20475 | 22631 | 23820 | 24909 | 22968 | 22852 | 25307 | 26285 | 27275 | 28149 | 25046 | 25234 | 27080
8183 | 8183 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 23 | 15697 | 16980 | 18976 | 19531 | 20173 | 18563 | 18763 | 19833 | 21530 | 23030 | 24056 | 22354 | 22489 | 24331 | 25647 | 26605 | 27454 | 24770 | 24821 | 26158
8184 | 8184 | 341 | 12 | 7 | Winter | 12 | 6 | Winter | 24 | 14654 | 16116 | 17615 | 18378 | 19022 | 17552 | 17952 | 19091 | 20316 | 22035 | 22979 | 21483 | 21815 | 23141 | 24698 | 25690 | 26476 | 24139 | 24218 | 25003
8185 | 8185 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 1 | 13882 | 15603 | 17328 | 17871 | 18039 | 16826 | 17312 | 18573 | 20284 | 21172 | 22428 | 20604 | 20631 | 23329 | 24482 | 24855 | 25910 | 22628 | 23495 | 25359
8186 | 8186 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 2 | 13407 | 15295 | 16877 | 17475 | 17568 | 16351 | 16966 | 18335 | 19871 | 20716 | 22015 | 20118 | 20203 | 22830 | 24012 | 24237 | 25379 | 22149 | 23134 | 24813
8187 | 8187 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 3 | 13156 | 15174 | 16702 | 17314 | 17416 | 16209 | 16872 | 18342 | 19787 | 20572 | 21888 | 19959 | 20023 | 22590 | 23785 | 23896 | 25129 | 21910 | 22984 | 24514
8188 | 8188 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 4 | 13023 | 15205 | 16643 | 17198 | 17301 | 16092 | 16733 | 18351 | 19600 | 20258 | 21541 | 19570 | 19621 | 22118 | 23197 | 23221 | 24468 | 21355 | 22608 | 23892
8189 | 8189 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 5 | 12919 | 15421 | 16768 | 17267 | 17402 | 15943 | 16627 | 18509 | 19533 | 20043 | 21310 | 19058 | 19211 | 21765 | 22634 | 22612 | 23824 | 20758 | 22281 | 23353
8190 | 8190 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 6 | 12949 | 16080 | 17293 | 17787 | 17908 | 15837 | 16640 | 19040 | 19810 | 20228 | 21415 | 18523 | 18797 | 21764 | 22388 | 22316 | 23532 | 20168 | 22317 | 23177
8191 | 8191 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 7 | 13541 | 17607 | 18427 | 19042 | 19118 | 16323 | 17043 | 20420 | 20683 | 21276 | 22383 | 18709 | 18847 | 22296 | 23148 | 23010 | 24282 | 20109 | 23420 | 23573
8192 | 8192 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 8 | 14604 | 19112 | 19714 | 20361 | 20575 | 17446 | 17723 | 21921 | 21793 | 22674 | 23836 | 19698 | 19474 | 23193 | 24220 | 24345 | 25617 | 20690 | 24805 | 24382
8193 | 8193 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 9 | 15247 | 19281 | 20001 | 20607 | 20900 | 18136 | 18369 | 22115 | 22049 | 22970 | 24087 | 20237 | 20116 | 23384 | 24277 | 24667 | 25808 | 21283 | 24892 | 24533
8194 | 8194 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 10 | 15153 | 18781 | 19511 | 20122 | 20459 | 17948 | 18271 | 21553 | 21701 | 22505 | 23609 | 20075 | 20202 | 23260 | 23873 | 24446 | 25391 | 21397 | 24535 | 24463
8195 | 8195 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 11 | 15181 | 18400 | 19161 | 19759 | 20195 | 17841 | 18176 | 20994 | 21435 | 22090 | 23161 | 19930 | 20451 | 23359 | 23442 | 24494 | 25001 | 21675 | 24359 | 24619
8196 | 8196 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 12 | 15246 | 18064 | 18788 | 19435 | 19988 | 17632 | 18001 | 20430 | 21199 | 21574 | 22707 | 19640 | 20514 | 23135 | 23075 | 24322 | 24558 | 21744 | 24061 | 24403
8197 | 8197 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 13 | 15296 | 17857 | 18694 | 19320 | 19876 | 17533 | 17985 | 20105 | 21113 | 21322 | 22401 | 19464 | 20641 | 23107 | 22851 | 24256 | 24235 | 21849 | 23883 | 24363
8198 | 8198 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 14 | 15721 | 18236 | 19147 | 19645 | 20193 | 17866 | 18421 | 20421 | 21503 | 21557 | 22610 | 19732 | 20980 | 23326 | 23167 | 24384 | 24410 | 22144 | 24068 | 24545
8199 | 8199 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 15 | 15817 | 18434 | 19437 | 20008 | 20299 | 18012 | 18692 | 20598 | 21615 | 21718 | 22656 | 19850 | 20927 | 23226 | 23652 | 24228 | 24380 | 22095 | 23925 | 24412
8200 | 8200 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 16 | 16004 | 18807 | 19879 | 20411 | 20519 | 18201 | 19022 | 20918 | 22005 | 21921 | 22658 | 19956 | 20870 | 23413 | 23940 | 24006 | 24293 | 22002 | 23826 | 24562
8201 | 8201 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 17 | 16855 | 19803 | 20847 | 21465 | 21335 | 19159 | 20070 | 21866 | 22786 | 22945 | 23483 | 20963 | 21778 | 24136 | 24880 | 24865 | 25235 | 22936 | 24720 | 25300
8202 | 8202 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 18 | 17506 | 20947 | 21753 | 22231 | 22383 | 20049 | 21057 | 23033 | 23346 | 24119 | 24633 | 22046 | 22890 | 24845 | 25690 | 26161 | 26520 | 24144 | 25927 | 26091
8203 | 8203 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 19 | 17102 | 20746 | 21455 | 21936 | 22407 | 19729 | 21004 | 22997 | 23123 | 24311 | 24751 | 21964 | 23145 | 25026 | 25834 | 26713 | 26973 | 24542 | 26298 | 26414
8204 | 8204 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 20 | 16778 | 20771 | 21229 | 21802 | 22395 | 19402 | 20854 | 23148 | 23270 | 24536 | 24997 | 22101 | 23268 | 25553 | 26420 | 27275 | 27595 | 24829 | 26910 | 27115
8205 | 8205 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 21 | 16554 | 20502 | 20969 | 21553 | 22383 | 19276 | 20726 | 23036 | 23355 | 24867 | 25258 | 22448 | 23543 | 26075 | 27000 | 28080 | 28284 | 25325 | 27368 | 27863
8206 | 8206 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 22 | 16131 | 19685 | 20272 | 20909 | 21701 | 18940 | 20222 | 22370 | 22951 | 24414 | 24999 | 22412 | 23285 | 25917 | 26962 | 27897 | 28289 | 25191 | 27037 | 27850
8207 | 8207 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 23 | 15460 | 18419 | 19252 | 19906 | 20614 | 18339 | 19519 | 21184 | 22129 | 23500 | 24208 | 21999 | 22784 | 25245 | 26262 | 27181 | 27651 | 24759 | 26102 | 27264
8208 | 8208 | 342 | 12 | 8 | Winter | 12 | 7 | Winter | 24 | 14530 | 17048 | 18072 | 18730 | 19373 | 17499 | 18748 | 19930 | 21092 | 22417 | 23192 | 21294 | 22124 | 24284 | 25328 | 26173 | 26682 | 24135 | 24931 | 26328
8209 | 8209 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 1 | 13924 | 16551 | 17365 | 17523 | 18555 | 16688 | 18007 | 19608 | 20587 | 21638 | 22327 | 19998 | 21257 | 23879 | 24295 | 25413 | 25918 | 23233 | 25089 | 26012
8210 | 8210 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 2 | 13487 | 16075 | 16935 | 17027 | 18153 | 16294 | 17724 | 19175 | 20200 | 21210 | 21795 | 19572 | 20931 | 23409 | 23674 | 24879 | 25274 | 22855 | 24519 | 25499
8211 | 8211 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 3 | 13249 | 15846 | 16727 | 16826 | 18036 | 16142 | 17677 | 19038 | 20094 | 21062 | 21533 | 19408 | 20839 | 23196 | 23347 | 24633 | 25073 | 22704 | 24223 | 25220
8212 | 8212 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 4 | 13130 | 15774 | 16623 | 16727 | 17954 | 16012 | 17704 | 18885 | 19860 | 20778 | 21144 | 19058 | 20625 | 22663 | 22729 | 24011 | 24411 | 22343 | 23614 | 24529
8213 | 8213 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 5 | 13163 | 15928 | 16721 | 16866 | 18026 | 15957 | 17927 | 18890 | 19731 | 20659 | 20769 | 18717 | 20498 | 22162 | 22179 | 23417 | 23731 | 22042 | 23100 | 23829
8214 | 8214 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 6 | 13299 | 16480 | 17272 | 17440 | 18494 | 16028 | 18541 | 19258 | 19970 | 20885 | 20495 | 18395 | 20728 | 21992 | 21952 | 23186 | 23143 | 22111 | 22949 | 23457
8215 | 8215 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 7 | 13713 | 17666 | 18552 | 18692 | 19790 | 16473 | 19988 | 20224 | 20951 | 21947 | 20696 | 18518 | 21943 | 22807 | 22690 | 23978 | 23035 | 23232 | 23364 | 24111
8216 | 8216 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 8 | 14378 | 18953 | 19870 | 20132 | 21351 | 17143 | 21496 | 21372 | 22192 | 23434 | 21348 | 19132 | 23346 | 23883 | 24007 | 25291 | 23486 | 24584 | 24124 | 25082
8217 | 8217 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 9 | 15052 | 19300 | 20177 | 20504 | 21696 | 17854 | 21769 | 21733 | 22489 | 23785 | 21873 | 19820 | 23532 | 23989 | 24375 | 25518 | 23911 | 24711 | 24326 | 25117
8218 | 8218 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 10 | 15184 | 18980 | 19924 | 20284 | 21356 | 18017 | 21480 | 21631 | 22171 | 23593 | 22129 | 20034 | 23285 | 23718 | 24284 | 25231 | 24200 | 24489 | 24386 | 24884
8219 | 8219 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 11 | 15416 | 18958 | 19929 | 20362 | 21155 | 18376 | 21400 | 21778 | 21899 | 23658 | 22298 | 20433 | 23245 | 23430 | 24476 | 24991 | 24446 | 24461 | 24691 | 24635
8220 | 8220 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 12 | 15573 | 18865 | 19907 | 20279 | 20941 | 18581 | 21233 | 21661 | 21581 | 23631 | 22254 | 20624 | 23077 | 23174 | 24419 | 24668 | 24415 | 24279 | 24607 | 24391
8221 | 8221 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 13 | 15655 | 18835 | 19876 | 20186 | 20659 | 18706 | 21062 | 21615 | 21346 | 23508 | 22122 | 20721 | 22876 | 22916 | 24320 | 24310 | 24153 | 24069 | 24534 | 24132
8222 | 8222 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 14 | 15587 | 18733 | 19626 | 19883 | 20359 | 18561 | 20791 | 21363 | 21063 | 23121 | 21840 | 20501 | 22531 | 22683 | 23899 | 23922 | 23931 | 23702 | 24165 | 23871
8223 | 8223 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 15 | 15668 | 18730 | 19661 | 19724 | 20266 | 18447 | 20562 | 21157 | 21248 | 22718 | 21580 | 20287 | 22236 | 22979 | 23555 | 23730 | 23398 | 23366 | 23839 | 24152
8224 | 8224 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 16 | 16186 | 19161 | 20060 | 20002 | 20532 | 18698 | 20776 | 21505 | 21725 | 22558 | 21506 | 20385 | 22308 | 23431 | 23492 | 23794 | 23105 | 23414 | 24132 | 24575
8225 | 8225 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 17 | 17325 | 20234 | 21205 | 21015 | 21614 | 19789 | 21746 | 22477 | 22966 | 23363 | 22387 | 21476 | 23375 | 24558 | 24541 | 24923 | 23950 | 24512 | 25065 | 25718
8226 | 8226 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 18 | 18358 | 21075 | 21902 | 22067 | 22627 | 20644 | 22735 | 23061 | 23711 | 24255 | 23642 | 22530 | 24478 | 25342 | 25820 | 26194 | 25411 | 25719 | 25858 | 26610
8227 | 8227 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 19 | 18232 | 20791 | 21620 | 22087 | 22419 | 20604 | 22701 | 22810 | 23564 | 24312 | 23728 | 22751 | 24728 | 25462 | 26359 | 26634 | 25907 | 26121 | 26202 | 26881
8228 | 8228 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 20 | 17946 | 20497 | 21420 | 22013 | 22275 | 20400 | 22783 | 22851 | 23575 | 24432 | 23664 | 22779 | 25144 | 25956 | 26841 | 27185 | 26162 | 26696 | 26864 | 27564
8229 | 8229 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 21 | 17683 | 20221 | 21128 | 21970 | 22088 | 20225 | 22611 | 22858 | 23625 | 24593 | 23864 | 22984 | 25370 | 26467 | 27584 | 27839 | 26776 | 27139 | 27604 | 28317
8230 | 8230 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 22 | 17106 | 19499 | 20467 | 21278 | 21546 | 19695 | 21911 | 22400 | 23261 | 24285 | 23584 | 22695 | 24913 | 26398 | 27388 | 27818 | 26730 | 26804 | 27594 | 28412
8231 | 8231 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 23 | 16303 | 18455 | 19463 | 20184 | 20572 | 18999 | 20732 | 21554 | 22399 | 23506 | 23073 | 22167 | 23911 | 25677 | 26648 | 27166 | 26516 | 25867 | 27013 | 27770
8232 | 8232 | 343 | 12 | 9 | Winter | 12 | 8 | Winter | 24 | 15406 | 17280 | 18265 | 18939 | 19372 | 18198 | 19444 | 20492 | 21375 | 22473 | 22336 | 21497 | 22693 | 24739 | 25639 | 26201 | 25869 | 24693 | 26078 | 26876
8233 | 8233 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 1 | 14838 | 16676 | 17159 | 18196 | 18744 | 17551 | 19153 | 20020 | 20375 | 21722 | 21150 | 20772 | 22767 | 23799 | 24985 | 25562 | 24274 | 24943 | 25877 | 25994
8234 | 8234 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 2 | 14517 | 16244 | 16668 | 17775 | 18215 | 17261 | 18720 | 19617 | 19898 | 21218 | 20663 | 20468 | 22271 | 23201 | 24472 | 24937 | 23710 | 24382 | 25364 | 25344
8235 | 8235 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 3 | 14370 | 16019 | 16454 | 17612 | 17965 | 17196 | 18578 | 19464 | 19717 | 20986 | 20458 | 20392 | 22052 | 22895 | 24242 | 24744 | 23585 | 24089 | 25091 | 24957
8236 | 8236 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 4 | 14386 | 15923 | 16355 | 17521 | 17797 | 17220 | 18444 | 19251 | 19444 | 20642 | 20080 | 20208 | 21614 | 22301 | 23647 | 24093 | 22986 | 23471 | 24391 | 24195
8237 | 8237 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 5 | 14603 | 15994 | 16491 | 17605 | 17728 | 17444 | 18474 | 19176 | 19311 | 20322 | 19695 | 20114 | 21316 | 21785 | 23079 | 23429 | 22321 | 22953 | 23679 | 23481
8238 | 8238 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 6 | 15307 | 16565 | 17120 | 18132 | 17855 | 18105 | 18917 | 19505 | 19622 | 20141 | 19333 | 20425 | 21406 | 21627 | 22910 | 22892 | 21665 | 22835 | 23331 | 23136
8239 | 8239 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 7 | 16833 | 17836 | 18386 | 19433 | 18279 | 19546 | 19928 | 20531 | 20736 | 20383 | 19416 | 21668 | 21981 | 22377 | 23709 | 22788 | 21597 | 23240 | 23967 | 23781
8240 | 8240 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 8 | 18331 | 19209 | 19857 | 21027 | 19024 | 21071 | 21143 | 21858 | 22187 | 21085 | 20045 | 23115 | 22892 | 23737 | 25065 | 23258 | 22113 | 24045 | 24979 | 25092
8241 | 8241 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 9 | 18525 | 19508 | 20219 | 21369 | 19625 | 21319 | 21495 | 22195 | 22554 | 21637 | 20664 | 23299 | 23128 | 24100 | 25288 | 23680 | 22577 | 24236 | 25007 | 25428
8242 | 8242 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 10 | 18417 | 19431 | 20168 | 21309 | 19962 | 21191 | 21539 | 22197 | 22547 | 22056 | 21142 | 23224 | 23294 | 24174 | 25167 | 24136 | 23079 | 24463 | 24946 | 25528
8243 | 8243 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 11 | 18314 | 19404 | 20203 | 21311 | 20021 | 21063 | 21618 | 22227 | 22607 | 22177 | 21410 | 23132 | 23490 | 24314 | 24878 | 24329 | 23404 | 24719 | 24654 | 25696
8244 | 8244 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 12 | 18249 | 19377 | 20121 | 21301 | 19981 | 20902 | 21499 | 22196 | 22520 | 22131 | 21524 | 22952 | 23382 | 24249 | 24552 | 24284 | 23512 | 24619 | 24413 | 25653
8245 | 8245 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 13 | 18103 | 19349 | 20036 | 21175 | 19879 | 20743 | 21463 | 22171 | 22452 | 22008 | 21598 | 22767 | 23331 | 24159 | 24202 | 24038 | 23467 | 24554 | 24158 | 25570
8246 | 8246 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 14 | 17943 | 19144 | 19777 | 20892 | 19706 | 20519 | 21261 | 21890 | 22125 | 21766 | 21364 | 22470 | 23037 | 23777 | 23851 | 23860 | 23296 | 24221 | 23931 | 25167
8247 | 8247 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 15 | 17750 | 19100 | 19550 | 20541 | 19464 | 20227 | 20993 | 21736 | 21753 | 21422 | 21155 | 22077 | 22655 | 23351 | 23577 | 23223 | 22792 | 23810 | 24119 | 24713
8248 | 8248 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 16 | 18113 | 19491 | 19834 | 20609 | 19562 | 20450 | 21316 | 21918 | 21784 | 21329 | 21270 | 22139 | 22964 | 23273 | 23622 | 22913 | 22714 | 24077 | 24505 | 24580
8249 | 8249 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 17 | 19181 | 20598 | 20808 | 21520 | 20448 | 21391 | 22253 | 22929 | 22768 | 22151 | 22336 | 23149 | 23839 | 24271 | 24700 | 23705 | 23832 | 24966 | 25610 | 25589
8250 | 8250 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 18 | 20240 | 21312 | 21841 | 22410 | 21660 | 22415 | 22870 | 23504 | 23724 | 23352 | 23394 | 24207 | 24532 | 25530 | 25950 | 25175 | 25088 | 25749 | 26484 | 26930
8251 | 8251 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 19 | 20048 | 21011 | 21834 | 22173 | 21542 | 22370 | 22582 | 23307 | 23874 | 23346 | 23406 | 24408 | 24677 | 26016 | 26344 | 25639 | 25284 | 26085 | 26743 | 27549
8252 | 8252 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 20 | 20032 | 20764 | 21724 | 22003 | 21104 | 22427 | 22565 | 23250 | 23992 | 23196 | 23294 | 24771 | 25112 | 26443 | 26844 | 25865 | 25536 | 26734 | 27419 | 28128
8253 | 8253 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 21 | 19744 | 20441 | 21649 | 21780 | 20889 | 22212 | 22494 | 23214 | 24222 | 23300 | 23398 | 24928 | 25558 | 27117 | 27430 | 26438 | 25987 | 27449 | 28155 | 29039
8254 | 8254 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 22 | 18927 | 19763 | 20936 | 21214 | 20322 | 21480 | 21980 | 22785 | 23716 | 22972 | 23082 | 24432 | 25365 | 26884 | 27386 | 26363 | 25858 | 27424 | 28241 | 28941
8255 | 8255 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 23 | 17681 | 18756 | 19840 | 20270 | 19622 | 20298 | 21120 | 21942 | 22808 | 22456 | 22462 | 23426 | 24675 | 26146 | 26743 | 26159 | 25505 | 26863 | 27616 | 28292
8256 | 8256 | 344 | 12 | 10 | Winter | 12 | 9 | Winter | 24 | 16320 | 17538 | 18561 | 19053 | 18733 | 18977 | 20018 | 20878 | 21702 | 21703 | 21673 | 22198 | 23704 | 25112 | 25756 | 25510 | 24814 | 25911 | 26729 | 27308
8257 | 8257 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 1 | 15789 | 16318 | 17683 | 18268 | 17866 | 18501 | 19361 | 19678 | 20856 | 20495 | 20923 | 22059 | 23254 | 24314 | 24999 | 23813 | 24047 | 25540 | 25712 | 26534
8258 | 8258 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 2 | 15336 | 15829 | 17267 | 17728 | 17402 | 18064 | 18954 | 19207 | 20449 | 20032 | 20539 | 21585 | 22810 | 23823 | 24388 | 23258 | 23551 | 25028 | 25058 | 25974
8259 | 8259 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 3 | 15113 | 15593 | 17104 | 17475 | 17204 | 17922 | 18811 | 19037 | 20324 | 19863 | 20458 | 21400 | 22633 | 23626 | 24224 | 23155 | 23552 | 24776 | 24694 | 25712
8260 | 8260 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 4 | 15040 | 15523 | 17039 | 17330 | 17021 | 17823 | 18642 | 18833 | 20095 | 19552 | 20236 | 21030 | 22143 | 23093 | 23624 | 22594 | 23115 | 24099 | 23949 | 25009
8261 | 8261 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 5 | 15177 | 15681 | 17140 | 17277 | 16886 | 17889 | 18620 | 18758 | 20025 | 19227 | 20113 | 20795 | 21683 | 22582 | 23007 | 21956 | 22721 | 23411 | 23241 | 24298
8262 | 8262 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 6 | 15726 | 16301 | 17684 | 17415 | 16864 | 18358 | 18992 | 19137 | 20328 | 18909 | 20324 | 20931 | 21568 | 22448 | 22494 | 21306 | 22616 | 23063 | 22883 | 23977
8263 | 8263 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 7 | 16927 | 17606 | 19031 | 17865 | 17243 | 19429 | 20088 | 20327 | 21440 | 19057 | 21322 | 21579 | 22423 | 23295 | 22434 | 21260 | 23384 | 23734 | 23536 | 24721
8264 | 8264 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 8 | 18227 | 19073 | 20602 | 18580 | 17854 | 20644 | 21409 | 21796 | 22951 | 19692 | 22685 | 22514 | 23518 | 24646 | 22896 | 21760 | 24663 | 24723 | 24836 | 26023
8265 | 8265 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 9 | 18562 | 19429 | 20970 | 19209 | 18457 | 21003 | 21787 | 22201 | 23318 | 20359 | 23033 | 22804 | 23662 | 24900 | 23352 | 22263 | 24950 | 24791 | 25182 | 26239
8266 | 8266 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 10 | 18396 | 19379 | 20907 | 19544 | 18867 | 21011 | 21767 | 22189 | 23299 | 20830 | 22967 | 22959 | 23565 | 24770 | 23800 | 22764 | 24907 | 24720 | 25285 | 26130
8267 | 8267 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 11 | 18390 | 19501 | 21001 | 19698 | 19152 | 21153 | 21876 | 22335 | 23384 | 21186 | 22998 | 23235 | 23302 | 24566 | 24081 | 23181 | 24963 | 24517 | 25545 | 25948
8268 | 8268 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 12 | 18337 | 19456 | 21024 | 19687 | 19310 | 21060 | 21871 | 22266 | 23388 | 21324 | 22906 | 23149 | 23079 | 24262 | 24060 | 23313 | 24872 | 24297 | 25526 | 25661
8269 | 8269 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 13 | 18263 | 19305 | 20839 | 19525 | 19359 | 20966 | 21785 | 22133 | 23227 | 21339 | 22785 | 23038 | 22780 | 23854 | 23756 | 23206 | 24642 | 23983 | 25379 | 25258
8270 | 8270 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 14 | 18205 | 19060 | 20572 | 19367 | 19205 | 20788 | 21518 | 21820 | 22880 | 21114 | 22625 | 22757 | 22581 | 23512 | 23584 | 23042 | 24544 | 23760 | 24978 | 24896
8271 | 8271 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 15 | 18211 | 18948 | 20322 | 19232 | 19189 | 20630 | 21459 | 21556 | 22485 | 20987 | 22458 | 22469 | 22868 | 23322 | 23029 | 22625 | 24086 | 24020 | 24605 | 24676
8272 | 8272 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 16 | 18538 | 19191 | 20356 | 19293 | 19416 | 20918 | 21604 | 21559 | 22260 | 21041 | 22428 | 22694 | 23227 | 23312 | 22656 | 22479 | 23858 | 24339 | 24406 | 24610
8273 | 8273 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 17 | 19505 | 20121 | 21226 | 20128 | 20458 | 21830 | 22581 | 22489 | 22958 | 22046 | 23266 | 23502 | 24236 | 24337 | 23395 | 23532 | 24720 | 25395 | 25358 | 25639
8274 | 8274 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 18 | 20341 | 21099 | 22063 | 21310 | 21386 | 22464 | 23159 | 23385 | 23802 | 23019 | 24026 | 24133 | 24963 | 25530 | 24810 | 24743 | 25764 | 26240 | 26652 | 26921
8275 | 8275 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 19 | 20042 | 21076 | 21794 | 21148 | 21200 | 22149 | 22921 | 23474 | 23790 | 22951 | 24032 | 24208 | 25011 | 25866 | 25222 | 24906 | 26038 | 26480 | 27266 | 27402
8276 | 8276 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 20 | 19714 | 20960 | 21581 | 20676 | 20907 | 22077 | 22795 | 23511 | 23822 | 22759 | 24059 | 24555 | 25433 | 26302 | 25396 | 25117 | 26248 | 27135 | 27847 | 28007
8277 | 8277 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 21 | 19413 | 20846 | 21326 | 20428 | 20675 | 21943 | 22688 | 23650 | 23890 | 22785 | 24113 | 24912 | 25873 | 26823 | 25910 | 25526 | 26648 | 27850 | 28744 | 28761
8278 | 8278 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 22 | 18665 | 20134 | 20735 | 19849 | 20117 | 21374 | 22195 | 23096 | 23521 | 22432 | 23701 | 24671 | 25754 | 26733 | 25800 | 25382 | 26428 | 27912 | 28646 | 28815
8279 | 8279 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 23 | 17636 | 19050 | 19780 | 19164 | 19343 | 20490 | 21329 | 22174 | 22742 | 21800 | 22893 | 23979 | 25048 | 26078 | 25589 | 25049 | 25898 | 27292 | 27991 | 28239
8280 | 8280 | 345 | 12 | 11 | Winter | 12 | 10 | Winter | 24 | 16467 | 17767 | 18548 | 18253 | 18402 | 19367 | 20238 | 21025 | 21682 | 21015 | 21893 | 22983 | 24098 | 25089 | 24945 | 24345 | 24998 | 26384 | 27014 | 27306
8281 | 8281 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 1 | 15827 | 17031 | 17898 | 17561 | 17838 | 18824 | 19168 | 20302 | 20930 | 20454 | 21469 | 22615 | 23131 | 24468 | 23414 | 23707 | 24885 | 25484 | 26329 | 26600
8282 | 8282 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 2 | 15399 | 16589 | 17361 | 17089 | 17453 | 18420 | 18708 | 19906 | 20435 | 20109 | 21059 | 22189 | 22560 | 23871 | 22866 | 23220 | 24355 | 24838 | 25784 | 25956
8283 | 8283 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 3 | 15182 | 16409 | 17116 | 16902 | 17347 | 18300 | 18577 | 19823 | 20219 | 20094 | 20918 | 22034 | 22281 | 23725 | 22778 | 23227 | 24228 | 24476 | 25528 | 25749
8284 | 8284 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 4 | 15106 | 16357 | 16987 | 16732 | 17306 | 18165 | 18424 | 19659 | 19943 | 19941 | 20575 | 21611 | 21764 | 23174 | 22246 | 22826 | 23615 | 23755 | 24839 | 25038
8285 | 8285 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 5 | 15201 | 16464 | 16939 | 16603 | 17485 | 18163 | 18379 | 19629 | 19706 | 19845 | 20384 | 21231 | 21326 | 22620 | 21657 | 22467 | 23102 | 23073 | 24147 | 24283
8286 | 8286 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 6 | 15762 | 17008 | 17089 | 16585 | 18021 | 18555 | 18794 | 19982 | 19591 | 20075 | 20552 | 21198 | 21228 | 22169 | 21050 | 22397 | 22995 | 22739 | 23841 | 23638
8287 | 8287 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 7 | 17078 | 18410 | 17610 | 17031 | 19196 | 19761 | 20105 | 21235 | 19920 | 21198 | 21250 | 22125 | 22051 | 22160 | 21045 | 23191 | 23411 | 23412 | 24597 | 23509
8288 | 8288 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 8 | 18422 | 19956 | 18317 | 17608 | 20602 | 21075 | 21564 | 22752 | 20621 | 22566 | 22219 | 23260 | 23420 | 22634 | 21541 | 24492 | 24190 | 24713 | 25880 | 23942
8289 | 8289 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 9 | 18749 | 20279 | 18927 | 18191 | 20961 | 21418 | 21937 | 23099 | 21213 | 22883 | 22444 | 23431 | 23805 | 23099 | 22061 | 24782 | 24344 | 25060 | 26100 | 24373
8290 | 8290 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 10 | 18572 | 20062 | 19086 | 18389 | 20738 | 21160 | 21684 | 22814 | 21523 | 22553 | 22526 | 23220 | 23774 | 23447 | 22460 | 24635 | 24657 | 25072 | 25899 | 24763
8291 | 8291 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 11 | 18588 | 19921 | 18957 | 18374 | 20674 | 20868 | 21405 | 22464 | 21676 | 22081 | 22513 | 22895 | 23945 | 23648 | 22801 | 24636 | 25188 | 25261 | 25645 | 25002
8292 | 8292 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 12 | 18564 | 19828 | 18816 | 18376 | 20576 | 20668 | 21121 | 22228 | 21628 | 21727 | 22270 | 22644 | 23871 | 23613 | 22921 | 24519 | 25176 | 25231 | 25351 | 24969
8293 | 8293 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 13 | 18474 | 19568 | 18557 | 18299 | 20482 | 20430 | 20813 | 21867 | 21447 | 21396 | 22008 | 22346 | 23721 | 23324 | 22829 | 24289 | 25007 | 25090 | 24958 | 24662
8294 | 8294 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 14 | 18690 | 19788 | 18887 | 18658 | 20815 | 20685 | 21031 | 22069 | 21630 | 21789 | 22114 | 22570 | 23759 | 23568 | 23080 | 24610 | 25023 | 25097 | 25006 | 24877
8295 | 8295 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 15 | 18762 | 19766 | 19019 | 18950 | 20805 | 20996 | 21169 | 22108 | 21419 | 22089 | 22106 | 22904 | 23460 | 23058 | 22705 | 24197 | 24285 | 24766 | 24828 | 24346
8296 | 8296 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 16 | 18987 | 19881 | 19191 | 19312 | 20864 | 21340 | 21401 | 22138 | 21185 | 22326 | 22427 | 23170 | 23227 | 22586 | 22454 | 23866 | 24072 | 24462 | 24655 | 23845
8297 | 8297 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 17 | 19880 | 20600 | 19889 | 20239 | 21492 | 22202 | 22213 | 22736 | 21789 | 23029 | 23036 | 24020 | 23999 | 23147 | 23331 | 24569 | 24741 | 25251 | 25510 | 24433
8298 | 8298 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 18 | 20576 | 21449 | 21077 | 21206 | 22299 | 22859 | 23144 | 23601 | 22939 | 23785 | 23561 | 24705 | 25182 | 24528 | 24516 | 25571 | 25278 | 26533 | 26783 | 25888
8299 | 8299 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 19 | 20253 | 21148 | 20881 | 20985 | 22105 | 22601 | 23199 | 23526 | 22851 | 23721 | 23509 | 24686 | 25595 | 24883 | 24640 | 25810 | 25535 | 27140 | 27256 | 26406
8300 | 8300 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 20 | 19953 | 20943 | 20389 | 20671 | 21868 | 22431 | 23190 | 23486 | 22614 | 23684 | 23744 | 25029 | 25944 | 25017 | 24819 | 26006 | 26108 | 27717 | 27862 | 26669
8301 | 8301 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 21 | 19602 | 20681 | 20116 | 20413 | 21582 | 22265 | 23264 | 23466 | 22625 | 23668 | 23897 | 25368 | 26526 | 25470 | 25192 | 26363 | 26667 | 28586 | 28606 | 27345
8302 | 8302 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 22 | 18895 | 20070 | 19516 | 19839 | 20927 | 21724 | 22669 | 23052 | 22233 | 23238 | 23662 | 25178 | 26243 | 25313 | 25003 | 26107 | 26646 | 28460 | 28641 | 27313
8303 | 8303 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 23 | 17878 | 19065 | 18763 | 19000 | 19917 | 20769 | 21647 | 22163 | 21680 | 22334 | 22908 | 24416 | 25481 | 25058 | 24635 | 25537 | 26295 | 27781 | 28039 | 27136
8304 | 8304 | 346 | 12 | 12 | Winter | 12 | 11 | Winter | 24 | 16652 | 17807 | 17833 | 18049 | 18786 | 19655 | 20470 | 21072 | 20896 | 21342 | 21997 | 23443 | 24435 | 24394 | 23921 | 24636 | 25448 | 26806 | 27112 | 26532
8305 | 8305 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 1 | 15277 | 16846 | 16830 | 17178 | 17609 | 18188 | 19376 | 20016 | 19598 | 20472 | 21092 | 22122 | 23410 | 22612 | 22981 | 24154 | 24849 | 25801 | 26088 | 24484
8306 | 8306 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 2 | 14799 | 16301 | 16347 | 16782 | 17200 | 17711 | 18970 | 19523 | 19154 | 20070 | 20634 | 21569 | 22939 | 22081 | 22508 | 23633 | 24330 | 25254 | 25441 | 23905
8307 | 8307 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 3 | 14599 | 16036 | 16135 | 16682 | 17063 | 17554 | 18859 | 19329 | 19055 | 19925 | 20418 | 21342 | 22779 | 22027 | 22545 | 23542 | 24073 | 25010 | 25251 | 23799
8308 | 8308 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 4 | 14526 | 15881 | 15944 | 16629 | 16924 | 17396 | 18711 | 19082 | 18779 | 19613 | 20062 | 20865 | 22296 | 21512 | 22155 | 22940 | 23438 | 24316 | 24528 | 23153
8309 | 8309 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 5 | 14698 | 15869 | 15846 | 16815 | 16995 | 17422 | 18764 | 18899 | 18482 | 19530 | 19818 | 20499 | 21856 | 20967 | 21831 | 22456 | 22875 | 23638 | 23784 | 22448
8310 | 8310 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 6 | 15345 | 16070 | 15911 | 17406 | 17494 | 17947 | 19263 | 18895 | 18205 | 19847 | 19939 | 20512 | 21824 | 20429 | 21820 | 22407 | 22648 | 23375 | 23174 | 21756
8311 | 8311 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 7 | 16650 | 16483 | 16275 | 18527 | 18501 | 19166 | 20444 | 19227 | 18411 | 20479 | 20761 | 21338 | 22667 | 20383 | 22567 | 22781 | 23223 | 24068 | 22979 | 21624
8312 | 8312 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 8 | 18114 | 17225 | 16896 | 19943 | 19748 | 20655 | 22034 | 19980 | 19044 | 21541 | 21976 | 22747 | 24071 | 20906 | 23897 | 23600 | 24184 | 25399 | 23428 | 22123
8313 | 8313 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 9 | 18475 | 17894 | 17539 | 20322 | 20041 | 21095 | 22448 | 20620 | 19722 | 21867 | 22206 | 23188 | 24358 | 21463 | 24228 | 23791 | 24268 | 25640 | 23889 | 22657
8314 | 8314 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 10 | 18466 | 18339 | 18028 | 20295 | 20215 | 21164 | 22501 | 21117 | 20134 | 22299 | 22357 | 23340 | 24339 | 22049 | 24271 | 24293 | 24362 | 25638 | 24469 | 23282
8315 | 8315 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 11 | 18385 | 18477 | 18310 | 20260 | 20234 | 21275 | 22568 | 21288 | 20051 | 22745 | 22485 | 23527 | 24096 | 22431 | 24316 | 24845 | 23934 | 25433 | 24754 | 23698
8316 | 8316 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 12 | 18228 | 18462 | 18455 | 20181 | 20077 | 21190 | 22542 | 21247 | 19936 | 22741 | 22477 | 23460 | 23765 | 22547 | 24195 | 24842 | 23526 | 25117 | 24717 | 23813
8317 | 8317 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 13 | 18028 | 18361 | 18538 | 20133 | 19945 | 21086 | 22401 | 21106 | 19779 | 22734 | 22440 | 23353 | 23397 | 22488 | 23995 | 24711 | 23367 | 24747 | 24440 | 23737
8318 | 8318 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 14 | 17996 | 18351 | 18572 | 20219 | 19877 | 20943 | 22231 | 21039 | 19849 | 22455 | 22416 | 23138 | 23211 | 22486 | 24062 | 24472 | 23477 | 24533 | 24398 | 23704
8319 | 8319 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 15 | 18039 | 18243 | 18589 | 20181 | 19822 | 20710 | 21870 | 20797 | 20113 | 21983 | 22294 | 22794 | 23005 | 22064 | 23601 | 23687 | 23758 | 24307 | 23816 | 23263
8320 | 8320 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 16 | 18334 | 18289 | 18782 | 20276 | 20133 | 20699 | 21632 | 20602 | 20436 | 21949 | 22205 | 22578 | 22909 | 21830 | 23285 | 23484 | 23746 | 24149 | 23322 | 23008
8321 | 8321 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 17 | 19147 | 19001 | 19715 | 20940 | 20913 | 21519 | 22221 | 21237 | 21358 | 22523 | 22912 | 23371 | 23791 | 22731 | 24011 | 24175 | 24364 | 25044 | 23935 | 23933
8322 | 8322 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 18 | 20108 | 20100 | 20624 | 21734 | 21517 | 22420 | 23009 | 22344 | 22363 | 22931 | 23576 | 24488 | 24929 | 23885 | 24987 | 24692 | 25239 | 26287 | 25373 | 25146
8323 | 8323 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 19 | 20083 | 19876 | 20384 | 21524 | 21157 | 22458 | 22901 | 22208 | 22253 | 22801 | 23464 | 24845 | 25210 | 23975 | 25198 | 24926 | 25542 | 26764 | 25889 | 25343
8324 | 8324 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 20 | 19962 | 19390 | 20051 | 21283 | 21030 | 22422 | 22816 | 21926 | 22005 | 22957 | 23672 | 25137 | 25588 | 24117 | 25360 | 25476 | 26125 | 27373 | 26161 | 25604
8325 | 8325 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 21 | 19823 | 19099 | 19767 | 20976 | 20741 | 22442 | 22718 | 21862 | 21963 | 23016 | 23951 | 25647 | 26026 | 24433 | 25673 | 25988 | 26833 | 28093 | 26828 | 26105
8326 | 8326 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 22 | 19132 | 18542 | 19188 | 20329 | 20211 | 21812 | 22261 | 21441 | 21606 | 22741 | 23701 | 25329 | 25913 | 24248 | 25424 | 25980 | 26889 | 28150 | 26822 | 26029
8327 | 8327 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 23 | 18014 | 17791 | 18360 | 19300 | 19284 | 20801 | 21375 | 20842 | 20885 | 22008 | 22968 | 24523 | 25214 | 23869 | 24848 | 25597 | 26383 | 27547 | 26656 | 25715
8328 | 8328 | 347 | 12 | 13 | Winter | 12 | 12 | Winter | 24 | 16744 | 16850 | 17399 | 18188 | 18234 | 19606 | 20261 | 20053 | 20109 | 21098 | 22019 | 23487 | 24231 | 23172 | 23967 | 24763 | 25651 | 26620 | 26068 | 25057
8329 | 8329 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 1 | 16278 | 16480 | 17120 | 17544 | 17738 | 19115 | 19814 | 19400 | 19763 | 20788 | 21068 | 23040 | 23869 | 22804 | 24016 | 24721 | 24870 | 26150 | 24607 | 24647
8330 | 8330 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 2 | 15838 | 15990 | 16724 | 17123 | 17271 | 18717 | 19327 | 18949 | 19403 | 20369 | 20533 | 22589 | 23292 | 22338 | 23510 | 24222 | 24287 | 25501 | 24026 | 24136
8331 | 8331 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 3 | 15626 | 15740 | 16603 | 16933 | 17037 | 18603 | 19138 | 18813 | 19340 | 20199 | 20301 | 22426 | 23160 | 22364 | 23400 | 23949 | 23951 | 25289 | 23893 | 24113
8332 | 8332 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 4 | 15584 | 15595 | 16573 | 16823 | 16938 | 18508 | 18953 | 18586 | 19212 | 19936 | 19878 | 22020 | 22661 | 22023 | 22861 | 23359 | 23215 | 24604 | 23273 | 23652
8333 | 8333 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 5 | 15712 | 15493 | 16763 | 16925 | 17006 | 18583 | 18808 | 18361 | 19204 | 19749 | 19505 | 21656 | 22165 | 21743 | 22415 | 22834 | 22445 | 23880 | 22575 | 23220
8334 | 8334 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 6 | 16311 | 15544 | 17360 | 17474 | 17483 | 19099 | 18854 | 18191 | 19566 | 19922 | 19413 | 21700 | 21798 | 21752 | 22392 | 22632 | 21918 | 23274 | 21873 | 23095
8335 | 8335 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 7 | 17682 | 15957 | 18555 | 18521 | 18627 | 20347 | 19289 | 18440 | 20657 | 20845 | 20260 | 22661 | 21822 | 22576 | 22849 | 23289 | 22619 | 23142 | 21793 | 23850
8336 | 8336 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 8 | 19250 | 16553 | 19924 | 19783 | 19976 | 21891 | 20016 | 19078 | 22072 | 22047 | 21568 | 24077 | 22329 | 23889 | 23685 | 24241 | 23818 | 23576 | 22273 | 25121
8337 | 8337 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 9 | 19558 | 17167 | 20266 | 20021 | 20311 | 22235 | 20594 | 19742 | 22454 | 22232 | 21918 | 24347 | 22805 | 24209 | 23847 | 24309 | 24082 | 24005 | 22776 | 25402
8338 | 8338 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 10 | 19395 | 17384 | 19953 | 19963 | 20145 | 21957 | 20735 | 19940 | 22255 | 22004 | 21763 | 24099 | 23115 | 24041 | 24139 | 24180 | 23994 | 24377 | 23194 | 25260
8339 | 8339 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 11 | 19349 | 17367 | 19589 | 19874 | 20056 | 21600 | 20441 | 19779 | 22114 | 21601 | 21611 | 23706 | 23216 | 23941 | 24538 | 23606 | 23633 | 24512 | 23463 | 25181
8340 | 8340 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 12 | 19307 | 17354 | 19332 | 19670 | 19990 | 21311 | 20107 | 19589 | 21956 | 21237 | 21400 | 23340 | 23125 | 23788 | 24496 | 23175 | 23223 | 24440 | 23545 | 25042
8341 | 8341 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 13 | 19301 | 17467 | 19320 | 19708 | 20087 | 21146 | 19933 | 19600 | 22008 | 21127 | 21364 | 23112 | 22995 | 23727 | 24502 | 23153 | 23188 | 24301 | 23606 | 24966
8342 | 8342 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 14 | 19512 | 17843 | 19740 | 19901 | 20429 | 21319 | 20218 | 19892 | 22313 | 21457 | 21580 | 23228 | 23283 | 24096 | 24564 | 23561 | 23448 | 24556 | 23870 | 25306
8343 | 8343 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 15 | 19279 | 18003 | 19858 | 19778 | 20420 | 21183 | 20217 | 20027 | 22167 | 21610 | 21574 | 23050 | 22738 | 23644 | 23793 | 23865 | 23657 | 23981 | 23435 | 24834
8344 | 8344 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 16 | 19261 | 18355 | 20144 | 20059 | 20516 | 21229 | 20318 | 20325 | 22072 | 21856 | 21607 | 22973 | 22283 | 23332 | 23597 | 23862 | 23546 | 23485 | 23175 | 24499
8345 | 8345 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 17 | 19957 | 19359 | 20898 | 20912 | 21249 | 21965 | 21106 | 21352 | 22732 | 22733 | 22484 | 23818 | 22843 | 24031 | 24260 | 24443 | 24296 | 24072 | 24075 | 25228
8346 | 8346 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 18 | 20749 | 20357 | 21802 | 21647 | 21998 | 22949 | 22395 | 22475 | 23415 | 23575 | 23570 | 24919 | 24188 | 25014 | 24770 | 25322 | 25457 | 25541 | 25315 | 26275
8347 | 8347 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 19 | 20434 | 20103 | 21573 | 21258 | 21724 | 22826 | 22226 | 22317 | 23301 | 23389 | 23584 | 25131 | 24486 | 25182 | 24965 | 25589 | 25706 | 26051 | 25512 | 26542
8348 | 8348 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 20 | 20224 | 19750 | 21295 | 21088 | 21466 | 22698 | 21891 | 22012 | 23206 | 23500 | 23686 | 25427 | 24566 | 25301 | 25467 | 26129 | 26253 | 26315 | 25762 | 26766
8349 | 8349 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 21 | 19961 | 19477 | 20988 | 20773 | 21301 | 22566 | 21782 | 21925 | 23133 | 23705 | 23953 | 25796 | 24957 | 25584 | 25949 | 26817 | 26947 | 26982 | 26270 | 27231
8350 | 8350 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 22 | 19339 | 18853 | 20284 | 20163 | 20684 | 22037 | 21277 | 21462 | 22630 | 23373 | 23630 | 25590 | 24766 | 25272 | 25868 | 26808 | 26909 | 26941 | 26156 | 27021
8351 | 8351 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 23 | 18336 | 17974 | 19194 | 19199 | 19722 | 21065 | 20590 | 20691 | 21729 | 22550 | 22918 | 24834 | 24474 | 24661 | 25443 | 26268 | 26478 | 26731 | 25817 | 26469
8352 | 8352 | 348 | 12 | 14 | Winter | 12 | 13 | Winter | 24 | 17102 | 17009 | 18059 | 18130 | 18618 | 19921 | 19771 | 19874 | 20734 | 21598 | 21944 | 23830 | 23825 | 23759 | 24608 | 25522 | 25717 | 26121 | 25155 | 25607
8353 | 8353 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 1 | 16518 | 16655 | 17318 | 17572 | 17308 | 19488 | 19191 | 19587 | 20216 | 20691 | 21247 | 23303 | 22496 | 23566 | 24338 | 24522 | 24742 | 24476 | 24546 | 25618
8354 | 8354 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 2 | 15992 | 16269 | 16886 | 17093 | 16821 | 18981 | 18717 | 19220 | 19841 | 20161 | 20680 | 22753 | 21980 | 23078 | 23853 | 23955 | 24035 | 23903 | 24043 | 25078
8355 | 8355 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 3 | 15727 | 16190 | 16758 | 16960 | 16622 | 18890 | 18695 | 19323 | 19728 | 20109 | 20531 | 22657 | 21925 | 23004 | 23614 | 23649 | 23746 | 23792 | 24039 | 24946
8356 | 8356 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 4 | 15602 | 16160 | 16658 | 16882 | 16473 | 18738 | 18500 | 19246 | 19499 | 19763 | 20121 | 22222 | 21471 | 22506 | 23062 | 22939 | 23017 | 23180 | 23579 | 24302
8357 | 8357 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 5 | 15584 | 16348 | 16772 | 16967 | 16445 | 18633 | 18322 | 19281 | 19452 | 19482 | 19849 | 21792 | 20969 | 22102 | 22573 | 22205 | 22376 | 22491 | 23146 | 23714
8358 | 8358 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 6 | 15750 | 16955 | 17324 | 17460 | 16808 | 18723 | 18210 | 19698 | 19803 | 19484 | 19904 | 21497 | 20453 | 22122 | 22410 | 21702 | 21982 | 21798 | 23018 | 23553
8359 | 8359 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 7 | 16186 | 18143 | 18397 | 18612 | 17982 | 19173 | 18497 | 20825 | 20520 | 20393 | 20804 | 21564 | 20479 | 22598 | 23084 | 22406 | 22564 | 21706 | 23750 | 23896
8360 | 8360 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 8 | 16911 | 19526 | 19696 | 19951 | 19359 | 19920 | 19156 | 22230 | 21593 | 21739 | 22141 | 22115 | 21012 | 23471 | 24068 | 23621 | 23821 | 22199 | 25039 | 24681
8361 | 8361 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 9 | 17535 | 19873 | 19950 | 20277 | 19709 | 20493 | 19841 | 22607 | 21867 | 22122 | 22511 | 22597 | 21566 | 23640 | 24149 | 23887 | 24196 | 22695 | 25318 | 24807
8362 | 8362 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 10 | 17789 | 19717 | 20028 | 20181 | 19619 | 20813 | 20227 | 22473 | 21990 | 22169 | 22476 | 22992 | 22011 | 23993 | 24089 | 23886 | 24217 | 23181 | 25247 | 25215
8363 | 8363 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 11 | 17730 | 19661 | 20255 | 20197 | 19632 | 20934 | 20510 | 22443 | 22007 | 22500 | 22475 | 23183 | 22340 | 24483 | 23614 | 23619 | 24268 | 23551 | 25273 | 25762
8364 | 8364 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 12 | 17559 | 19573 | 20241 | 20146 | 19518 | 20852 | 20594 | 22297 | 21667 | 22592 | 22386 | 23106 | 22423 | 24443 | 23182 | 23218 | 24197 | 23634 | 25129 | 25730
8365 | 8365 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 13 | 17349 | 19459 | 20185 | 20025 | 19371 | 20609 | 20540 | 22100 | 21434 | 22502 | 22201 | 22818 | 22336 | 24283 | 22993 | 23022 | 24000 | 23529 | 24886 | 25553
8366 | 8366 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 14 | 17479 | 19734 | 20254 | 20268 | 19459 | 20772 | 20718 | 22342 | 21346 | 22615 | 22314 | 22941 | 22466 | 24184 | 23233 | 23111 | 24069 | 23625 | 25056 | 25412
8367 | 8367 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 15 | 17547 | 19677 | 19915 | 20157 | 19535 | 20427 | 20467 | 22020 | 21209 | 22132 | 21875 | 22431 | 22108 | 23454 | 23573 | 23350 | 23604 | 23223 | 24617 | 24650
8368 | 8368 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 16 | 17755 | 19784 | 19931 | 20219 | 19690 | 20214 | 20411 | 21851 | 21513 | 21727 | 21540 | 22007 | 21886 | 23287 | 23591 | 23262 | 23169 | 22977 | 24295 | 24441
8369 | 8369 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 17 | 18598 | 20499 | 20752 | 21036 | 20612 | 20921 | 21336 | 22586 | 22326 | 22458 | 22237 | 22629 | 22821 | 24017 | 24237 | 24079 | 23895 | 23945 | 25091 | 25193
8370 | 8370 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 18 | 19786 | 21310 | 21437 | 21847 | 21506 | 22089 | 22299 | 23277 | 22964 | 23304 | 23149 | 23939 | 23986 | 24524 | 25112 | 25249 | 25111 | 25207 | 26151 | 25773
8371 | 8371 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 19 | 19538 | 21054 | 21023 | 21540 | 21259 | 21889 | 22104 | 23112 | 22773 | 23225 | 23278 | 24164 | 24021 | 24660 | 25327 | 25460 | 25568 | 25395 | 26418 | 26048
8372 | 8372 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 20 | 19058 | 20774 | 20831 | 21244 | 21107 | 21538 | 21771 | 22969 | 22852 | 23246 | 23458 | 24181 | 24113 | 25122 | 25830 | 25980 | 26039 | 25658 | 26656 | 26678
8373 | 8373 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 21 | 18786 | 20471 | 20486 | 21048 | 20958 | 21379 | 21633 | 22842 | 22855 | 23421 | 23815 | 24493 | 24400 | 25547 | 26470 | 26627 | 26849 | 26159 | 27110 | 27316
8374 | 8374 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 22 | 18206 | 19749 | 19848 | 20395 | 20346 | 20839 | 21127 | 22290 | 22494 | 23044 | 23596 | 24252 | 24143 | 25440 | 26430 | 26563 | 26887 | 26037 | 26910 | 27355
8375 | 8375 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 23 | 17418 | 18761 | 18995 | 19538 | 19448 | 20307 | 20530 | 21534 | 21678 | 22548 | 23033 | 23946 | 23740 | 25016 | 25892 | 26140 | 26458 | 25711 | 26380 | 27015
8376 | 8376 | 349 | 12 | 15 | Winter | 12 | 14 | Winter | 24 | 16454 | 17608 | 17905 | 18417 | 18268 | 19469 | 19694 | 20517 | 20731 | 21585 | 22029 | 23257 | 23013 | 24153 | 25123 | 25348 | 25542 | 25025 | 25502 | 26194
8377 | 8377 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 1 | 15953 | 16656 | 17151 | 17037 | 17370 | 18679 | 19129 | 19862 | 20379 | 20583 | 21031 | 21957 | 22405 | 23822 | 24056 | 24323 | 24377 | 24362 | 25432 | 25932
8378 | 8378 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 2 | 15452 | 16206 | 16661 | 16517 | 16835 | 18186 | 18746 | 19451 | 19941 | 20029 | 20478 | 21452 | 21947 | 23341 | 23494 | 23622 | 23708 | 23850 | 24882 | 25402
8379 | 8379 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 3 | 15257 | 16034 | 16481 | 16374 | 16647 | 18124 | 18816 | 19445 | 19906 | 19897 | 20306 | 21412 | 21995 | 23105 | 23195 | 23341 | 23412 | 23837 | 24748 | 25098
8380 | 8380 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 4 | 15132 | 15939 | 16420 | 16254 | 16507 | 17949 | 18767 | 19265 | 19715 | 19562 | 19867 | 21012 | 21699 | 22609 | 22531 | 22652 | 22677 | 23392 | 24108 | 24450
8381 | 8381 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 5 | 15036 | 16057 | 16513 | 16265 | 16618 | 17801 | 18844 | 19293 | 19603 | 19375 | 19424 | 20570 | 21463 | 22173 | 21848 | 22051 | 21817 | 22977 | 23535 | 23817
8382 | 8382 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 6 | 15077 | 16601 | 17008 | 16684 | 17090 | 17719 | 19316 | 19717 | 19846 | 19520 | 18976 | 20128 | 21510 | 22060 | 21390 | 21701 | 20938 | 22858 | 23377 | 23503
8383 | 8383 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 7 | 15476 | 17728 | 18173 | 17894 | 18223 | 18033 | 20498 | 20524 | 20824 | 20498 | 19083 | 20213 | 22351 | 22783 | 22132 | 22311 | 20907 | 23601 | 23731 | 24057
8384 | 8384 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 8 | 16081 | 19028 | 19530 | 19266 | 19659 | 18693 | 21918 | 21633 | 22076 | 21872 | 19953 | 20771 | 23692 | 23817 | 23364 | 23582 | 21665 | 24899 | 24510 | 24992
8385 | 8385 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 9 | 16714 | 19311 | 19872 | 19613 | 20075 | 19380 | 22312 | 21954 | 22304 | 22272 | 20558 | 21335 | 24033 | 23923 | 23653 | 23958 | 22182 | 25193 | 24660 | 25039
8386 | 8386 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 10 | 16925 | 19206 | 19640 | 19479 | 19844 | 19614 | 22029 | 22056 | 22141 | 22081 | 20770 | 21635 | 23787 | 23720 | 23507 | 23838 | 22427 | 24981 | 24923 | 24873
8387 | 8387 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 11 | 17059 | 19276 | 19523 | 19626 | 19670 | 19754 | 21858 | 22311 | 22100 | 21931 | 20899 | 21836 | 23659 | 23107 | 23100 | 23763 | 22533 | 24875 | 25335 | 24297
8388 | 8388 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 12 | 17197 | 19281 | 19484 | 19728 | 19602 | 19850 | 21723 | 22277 | 22057 | 21845 | 20882 | 21927 | 23522 | 22669 | 22704 | 23698 | 22383 | 24732 | 25314 | 23880
8389 | 8389 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 13 | 17252 | 19316 | 19434 | 19723 | 19513 | 19871 | 21601 | 22217 | 21959 | 21732 | 20747 | 21904 | 23364 | 22544 | 22572 | 23562 | 22164 | 24555 | 25204 | 23746
8390 | 8390 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 14 | 17400 | 19314 | 19588 | 19761 | 19567 | 19967 | 21759 | 22105 | 22091 | 21767 | 20673 | 21953 | 23478 | 22700 | 22577 | 23544 | 22122 | 24638 | 24978 | 23875
8391 | 8391 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 15 | 17466 | 19102 | 19592 | 19591 | 19412 | 19835 | 21549 | 21570 | 21862 | 21411 | 20303 | 21656 | 23139 | 23120 | 22896 | 23136 | 21885 | 24275 | 24291 | 24280
8392 | 8392 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 16 | 17768 | 19264 | 19828 | 19620 | 19481 | 19955 | 21550 | 21568 | 21819 | 21221 | 20076 | 21581 | 22977 | 23276 | 22946 | 22845 | 21642 | 24080 | 24210 | 24410
8393 | 8393 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 17 | 18824 | 20157 | 20726 | 20494 | 20217 | 20967 | 22363 | 22274 | 22632 | 21975 | 20772 | 22583 | 23810 | 23980 | 23826 | 23643 | 22395 | 24940 | 25021 | 25150
8394 | 8394 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 18 | 19753 | 20878 | 21580 | 21255 | 21147 | 21965 | 23053 | 22740 | 23289 | 22833 | 21734 | 23694 | 24790 | 24824 | 24972 | 24839 | 23546 | 26006 | 25601 | 26085
8395 | 8395 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 19 | 19472 | 20437 | 21259 | 20973 | 21000 | 21755 | 22860 | 22488 | 23020 | 22875 | 21713 | 23669 | 24896 | 24984 | 25137 | 25257 | 23841 | 26269 | 25874 | 26395
8396 | 8396 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 20 | 19141 | 20220 | 20943 | 20811 | 20841 | 21410 | 22690 | 22516 | 23080 | 22971 | 21840 | 23718 | 24997 | 25441 | 25620 | 25709 | 24327 | 26520 | 26503 | 27040
8397 | 8397 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 21 | 18834 | 19822 | 20680 | 20590 | 20718 | 21199 | 22478 | 22400 | 23162 | 23197 | 22098 | 23896 | 25199 | 25981 | 26188 | 26432 | 25009 | 26929 | 27112 | 27819
8398 | 8398 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 22 | 18215 | 19171 | 20013 | 19975 | 20209 | 20669 | 21895 | 21994 | 22785 | 22933 | 22006 | 23616 | 24866 | 25917 | 26103 | 26464 | 25193 | 26727 | 27154 | 27915
8399 | 8399 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 23 | 17434 | 18276 | 19099 | 19181 | 19338 | 20016 | 21081 | 21327 | 22145 | 22328 | 21681 | 23178 | 24249 | 25332 | 25639 | 26005 | 24997 | 26173 | 26791 | 27421
8400 | 8400 | 350 | 12 | 16 | Winter | 12 | 15 | Winter | 24 | 16463 | 17171 | 17950 | 18008 | 18162 | 19148 | 20029 | 20374 | 21184 | 21313 | 20977 | 22440 | 23324 | 24553 | 24837 | 25084 | 24365 | 25284 | 25965 | 26697
8401 | 8401 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 1 | 15793 | 16290 | 16425 | 16796 | 17077 | 18443 | 19159 | 19616 | 19784 | 20212 | 19325 | 21703 | 22856 | 23323 | 23667 | 23795 | 22204 | 25047 | 25571 | 25523
8402 | 8402 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 2 | 15408 | 15818 | 15925 | 16276 | 16566 | 18071 | 18764 | 19199 | 19280 | 19705 | 18793 | 21286 | 22397 | 22802 | 23005 | 23165 | 21587 | 24520 | 25059 | 24933
8403 | 8403 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 3 | 15298 | 15633 | 15775 | 16077 | 16379 | 18132 | 18759 | 19170 | 19247 | 19580 | 18630 | 21372 | 22361 | 22541 | 22761 | 22901 | 21329 | 24403 | 24782 | 24586
8404 | 8404 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 4 | 15221 | 15544 | 15645 | 15931 | 16155 | 18075 | 18590 | 19002 | 18944 | 19185 | 18223 | 21102 | 21890 | 21906 | 22096 | 22176 | 20677 | 23755 | 24112 | 23774
8405 | 8405 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 5 | 15391 | 15660 | 15691 | 16078 | 16005 | 18193 | 18680 | 18963 | 18750 | 18831 | 17724 | 20935 | 21560 | 21294 | 21557 | 21368 | 19936 | 23214 | 23504 | 22959
8406 | 8406 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 6 | 15987 | 16182 | 16169 | 16609 | 15933 | 18716 | 19185 | 19291 | 18854 | 18483 | 17122 | 21065 | 21652 | 20912 | 21274 | 20544 | 19092 | 23094 | 23219 | 22383
8407 | 8407 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 7 | 17166 | 17374 | 17421 | 17769 | 16380 | 19923 | 20064 | 20330 | 19835 | 18659 | 17167 | 21961 | 22186 | 21693 | 21921 | 20543 | 18891 | 23467 | 23792 | 23059
8408 | 8408 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 8 | 18498 | 18734 | 18789 | 19189 | 17393 | 21325 | 21201 | 21602 | 21198 | 19551 | 18207 | 23315 | 23067 | 22927 | 23185 | 21300 | 19801 | 24236 | 24726 | 24245
8409 | 8409 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 9 | 18825 | 19122 | 19161 | 19624 | 18053 | 21731 | 21550 | 21881 | 21620 | 20208 | 18902 | 23704 | 23292 | 23246 | 23591 | 21853 | 20420 | 24414 | 24788 | 24538
8410 | 8410 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 10 | 18425 | 18720 | 18849 | 19221 | 18008 | 21258 | 21449 | 21537 | 21326 | 20237 | 19032 | 23285 | 23302 | 22914 | 23288 | 21925 | 20590 | 24493 | 24443 | 24238
8411 | 8411 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 11 | 18325 | 18569 | 18955 | 19008 | 18040 | 21044 | 21643 | 21449 | 21478 | 20324 | 19203 | 23118 | 23618 | 22463 | 23171 | 21991 | 20808 | 24864 | 23842 | 23817
8412 | 8412 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 12 | 18172 | 18401 | 18922 | 18802 | 17912 | 20776 | 21471 | 21259 | 21449 | 20166 | 19211 | 22836 | 23461 | 21924 | 22976 | 21697 | 20833 | 24707 | 23272 | 23294
8413 | 8413 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 13 | 18260 | 18454 | 19013 | 18806 | 17921 | 20753 | 21507 | 21249 | 21516 | 20118 | 19229 | 22763 | 23456 | 21886 | 22927 | 21561 | 20840 | 24689 | 23231 | 23259
8414 | 8414 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 14 | 18486 | 18729 | 19173 | 18983 | 18014 | 21037 | 21528 | 21504 | 21669 | 20172 | 19408 | 23004 | 23400 | 22016 | 23034 | 21642 | 20991 | 24587 | 23481 | 23373
8415 | 8415 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 15 | 18383 | 18735 | 19026 | 18851 | 17819 | 20852 | 21016 | 21293 | 21267 | 19788 | 19190 | 22652 | 22727 | 22322 | 22612 | 21387 | 20745 | 23884 | 23866 | 23653
8416 | 8416 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 16 | 18609 | 19022 | 19124 | 18990 | 17867 | 20922 | 21048 | 21320 | 21050 | 19594 | 19153 | 22522 | 22712 | 22404 | 22352 | 21169 | 20658 | 23823 | 24014 | 23683
8417 | 8417 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 17 | 19527 | 20008 | 20088 | 19816 | 18765 | 21835 | 21851 | 22223 | 21934 | 20359 | 20184 | 23424 | 23584 | 23363 | 23224 | 21997 | 21650 | 24709 | 24826 | 24661
8418 | 8418 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 18 | 20329 | 20923 | 20865 | 20776 | 19708 | 22594 | 22386 | 22925 | 22798 | 21297 | 21495 | 24376 | 24104 | 24511 | 24429 | 23144 | 23153 | 25330 | 25800 | 25910
8419 | 8419 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 19 | 19979 | 20581 | 20569 | 20613 | 19364 | 22400 | 22111 | 22619 | 22662 | 21202 | 21511 | 24439 | 24185 | 24636 | 24813 | 23419 | 23506 | 25605 | 26113 | 26168
8420 | 8420 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 20 | 19710 | 20233 | 20369 | 20412 | 19153 | 22200 | 22079 | 22596 | 22609 | 21237 | 21669 | 24470 | 24588 | 25061 | 25211 | 23860 | 23942 | 26223 | 26746 | 26751
8421 | 8421 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 21 | 19332 | 19935 | 20127 | 20260 | 18993 | 21953 | 21899 | 22597 | 22666 | 21407 | 21973 | 24606 | 24907 | 25574 | 25885 | 24501 | 24584 | 26811 | 27513 | 27495
8422 | 8422 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 22 | 18626 | 19236 | 19478 | 19720 | 18597 | 21323 | 21426 | 22151 | 22232 | 21256 | 21712 | 24228 | 24757 | 25446 | 25872 | 24655 | 24513 | 26832 | 27591 | 27496
8423 | 8423 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 23 | 17672 | 18301 | 18663 | 18831 | 18040 | 20488 | 20730 | 21474 | 21682 | 20921 | 21196 | 23602 | 24305 | 24982 | 25424 | 24465 | 24081 | 26483 | 27111 | 27118
8424 | 8424 | 351 | 12 | 17 | Winter | 12 | 16 | Winter | 24 | 16536 | 17142 | 17463 | 17637 | 17172 | 19408 | 19744 | 20474 | 20694 | 20212 | 20311 | 22665 | 23436 | 24170 | 24490 | 23829 | 23237 | 25651 | 26389 | 26357
8425 | 8425 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 1 | 15879 | 15839 | 16457 | 16780 | 16157 | 18695 | 19158 | 19282 | 19765 | 18881 | 19629 | 22357 | 23175 | 23214 | 23442 | 21952 | 22497 | 25454 | 25434 | 25427
8426 | 8426 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 2 | 15443 | 15329 | 15923 | 16234 | 15590 | 18272 | 18714 | 18758 | 19228 | 18351 | 19198 | 21895 | 22714 | 22551 | 22807 | 21321 | 22066 | 24923 | 24832 | 24691
8427 | 8427 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 3 | 15271 | 15140 | 15686 | 15994 | 15346 | 18227 | 18658 | 18689 | 19105 | 18197 | 19247 | 21858 | 22508 | 22313 | 22545 | 21051 | 21863 | 24638 | 24483 | 24381
8428 | 8428 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 4 | 15181 | 15047 | 15570 | 15800 | 15140 | 18097 | 18537 | 18462 | 18826 | 17863 | 19017 | 21463 | 22056 | 21714 | 21879 | 20446 | 21399 | 23994 | 23705 | 23606
8429 | 8429 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 5 | 15308 | 15093 | 15722 | 15662 | 14885 | 18209 | 18539 | 18322 | 18715 | 17412 | 18903 | 21189 | 21688 | 21220 | 21104 | 19726 | 21023 | 23402 | 22885 | 22911
8430 | 8430 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 6 | 15881 | 15612 | 16306 | 15642 | 14616 | 18775 | 18946 | 18533 | 18978 | 16890 | 19107 | 21364 | 21665 | 21010 | 20342 | 18924 | 20947 | 23154 | 22334 | 22509
8431 | 8431 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 7 | 17040 | 16846 | 17496 | 16105 | 14837 | 19696 | 20037 | 19580 | 20021 | 16980 | 20186 | 21961 | 22437 | 21688 | 20368 | 18735 | 21882 | 23743 | 23001 | 23082
8432 | 8432 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 8 | 18340 | 18227 | 18927 | 17121 | 15933 | 20862 | 21334 | 20992 | 21412 | 18051 | 21686 | 22891 | 23481 | 22985 | 21143 | 19654 | 23337 | 24677 | 24200 | 24326
8433 | 8433 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 9 | 18608 | 18563 | 19333 | 17755 | 16668 | 21164 | 21599 | 21396 | 21817 | 18738 | 22086 | 23115 | 23614 | 23364 | 21669 | 20256 | 23681 | 24725 | 24448 | 24678
8434 | 8434 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 10 | 18272 | 18208 | 18887 | 17674 | 16701 | 20983 | 21191 | 21062 | 21414 | 18816 | 21838 | 23076 | 23202 | 23008 | 21689 | 20385 | 23323 | 24326 | 24106 | 24340
8435 | 8435 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 11 | 18234 | 18225 | 18623 | 17653 | 16750 | 21094 | 21036 | 21149 | 21165 | 18930 | 21899 | 23324 | 22495 | 22830 | 21698 | 20547 | 22618 | 23658 | 23632 | 24185
8436 | 8436 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 12 | 18148 | 18227 | 18459 | 17554 | 16799 | 20959 | 20880 | 21134 | 20978 | 18968 | 21858 | 23185 | 21952 | 22655 | 21439 | 20592 | 21896 | 23122 | 23138 | 24030
8437 | 8437 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 13 | 18229 | 18286 | 18432 | 17531 | 16802 | 20963 | 20833 | 21160 | 20907 | 18941 | 21781 | 23138 | 21876 | 22564 | 21261 | 20554 | 21675 | 23040 | 23061 | 23946
8438 | 8438 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 14 | 18216 | 18303 | 18470 | 17485 | 16855 | 20858 | 20952 | 21173 | 20921 | 18984 | 21822 | 22952 | 22010 | 22537 | 21207 | 20564 | 21624 | 23153 | 23033 | 23901
8439 | 8439 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 15 | 18106 | 18310 | 18490 | 17449 | 16918 | 20508 | 20884 | 20926 | 20677 | 18878 | 21419 | 22402 | 22513 | 22230 | 21065 | 20432 | 22001 | 23646 | 23425 | 23565
8440 | 8440 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 16 | 18430 | 18573 | 18806 | 17675 | 17250 | 20719 | 21080 | 20893 | 20687 | 18981 | 21239 | 22505 | 22837 | 22114 | 20985 | 20478 | 22300 | 23921 | 23589 | 23393
8441 | 8441 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 17 | 19438 | 19578 | 19669 | 18614 | 18348 | 21577 | 22027 | 21816 | 21554 | 20029 | 22148 | 23404 | 23643 | 23015 | 21838 | 21497 | 23463 | 24766 | 24588 | 24303
8442 | 8442 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 18 | 20206 | 20333 | 20612 | 19566 | 19630 | 22166 | 22766 | 22657 | 22426 | 21291 | 23138 | 23905 | 24494 | 24206 | 22979 | 22997 | 24956 | 25742 | 25835 | 25587
8443 | 8443 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 19 | 19795 | 20054 | 20452 | 19219 | 19564 | 21899 | 22453 | 22493 | 22441 | 21262 | 23184 | 23949 | 24631 | 24567 | 23237 | 23351 | 25276 | 26070 | 26121 | 26089
8444 | 8444 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 20 | 19552 | 19827 | 20216 | 18984 | 19402 | 21821 | 22369 | 22373 | 22455 | 21350 | 23295 | 24282 | 25015 | 24908 | 23630 | 23762 | 25647 | 26689 | 26703 | 26601
8445 | 8445 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 21 | 19105 | 19551 | 20003 | 18763 | 19340 | 21553 | 22274 | 22317 | 22561 | 21546 | 23489 | 24495 | 25451 | 25479 | 24189 | 24342 | 26182 | 27418 | 27399 | 27411
8446 | 8446 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 22 | 18451 | 18925 | 19463 | 18375 | 18870 | 21053 | 21790 | 21856 | 22251 | 21274 | 22958 | 24318 | 25350 | 25451 | 24333 | 24276 | 25795 | 27498 | 27425 | 27525
8447 | 8447 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 23 | 17558 | 18066 | 18525 | 17787 | 18119 | 20297 | 21053 | 21250 | 21615 | 20726 | 22284 | 23831 | 24768 | 24966 | 24112 | 23830 | 25043 | 27001 | 27032 | 27128
8448 | 8448 | 352 | 12 | 18 | Winter | 12 | 17 | Winter | 24 | 16419 | 16833 | 17278 | 16873 | 17061 | 19251 | 19987 | 20192 | 20547 | 19810 | 21200 | 22909 | 23951 | 23997 | 23439 | 22952 | 24081 | 26233 | 26248 | 26221
8449 | 8449 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 1 | 15804 | 15950 | 16529 | 16032 | 16333 | 18803 | 18958 | 19418 | 19737 | 19247 | 21041 | 22670 | 22996 | 23029 | 21677 | 22272 | 24280 | 25347 | 25359 | 25162
8450 | 8450 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 2 | 15326 | 15448 | 16020 | 15489 | 15927 | 18402 | 18487 | 18936 | 19231 | 18895 | 20639 | 22243 | 22486 | 22422 | 21072 | 21860 | 23807 | 24763 | 24640 | 24495
8451 | 8451 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 3 | 15121 | 15142 | 15698 | 15150 | 15843 | 18243 | 18322 | 18709 | 19087 | 18809 | 20532 | 22057 | 22220 | 22174 | 20810 | 21661 | 23592 | 24409 | 24329 | 24182
8452 | 8452 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 4 | 15044 | 15031 | 15501 | 14938 | 15788 | 18131 | 18122 | 18467 | 18761 | 18624 | 20217 | 21660 | 21664 | 21548 | 20232 | 21217 | 23005 | 23642 | 23563 | 23400
8453 | 8453 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 5 | 15164 | 15177 | 15376 | 14694 | 15905 | 18165 | 18027 | 18411 | 18471 | 18536 | 19986 | 21369 | 21111 | 20836 | 19557 | 20877 | 22456 | 22849 | 22887 | 22488
8454 | 8454 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 6 | 15656 | 15707 | 15317 | 14382 | 16375 | 18541 | 18227 | 18679 | 18168 | 18661 | 20141 | 21378 | 20768 | 20084 | 18746 | 20784 | 22283 | 22267 | 22445 | 21535
8455 | 8455 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 7 | 16856 | 16936 | 15844 | 14658 | 17746 | 19740 | 19395 | 19859 | 18396 | 19904 | 20890 | 22212 | 21590 | 20149 | 18584 | 21731 | 22662 | 22944 | 23019 | 21476
8456 | 8456 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 8 | 18226 | 18375 | 16882 | 15761 | 19324 | 21071 | 20843 | 21298 | 19330 | 21520 | 21875 | 23299 | 22877 | 20949 | 19523 | 23207 | 23523 | 24153 | 24265 | 22236
8457 | 8457 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 9 | 18603 | 18793 | 17530 | 16492 | 19735 | 21348 | 21263 | 21727 | 19973 | 22013 | 22207 | 23457 | 23163 | 21492 | 20136 | 23558 | 23760 | 24408 | 24619 | 22743
8458 | 8458 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 10 | 18301 | 18432 | 17543 | 16579 | 19499 | 20989 | 20981 | 21342 | 20095 | 21737 | 22249 | 23153 | 22929 | 21645 | 20400 | 23313 | 23884 | 24199 | 24423 | 22937
8459 | 8459 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 11 | 18200 | 18015 | 17317 | 16362 | 19434 | 20459 | 20653 | 20636 | 20220 | 21111 | 22092 | 22538 | 22511 | 21747 | 20656 | 22707 | 23794 | 23827 | 24369 | 23076
8460 | 8460 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 12 | 18132 | 17751 | 17087 | 16233 | 19363 | 20064 | 20365 | 20142 | 20151 | 20617 | 21749 | 22047 | 22053 | 21547 | 20761 | 22036 | 23278 | 23392 | 24269 | 22883
8461 | 8461 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 13 | 18151 | 17739 | 17087 | 16263 | 19298 | 20037 | 20402 | 20094 | 20071 | 20502 | 21656 | 21991 | 21976 | 21390 | 20743 | 21842 | 23093 | 23333 | 24200 | 22709
8462 | 8462 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 14 | 18281 | 17793 | 17067 | 16354 | 19386 | 20199 | 20460 | 20168 | 19985 | 20618 | 21567 | 22132 | 21965 | 21335 | 20748 | 21793 | 22810 | 23296 | 24147 | 22625
8463 | 8463 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 15 | 18327 | 18088 | 17357 | 16809 | 19311 | 20622 | 20756 | 20526 | 19673 | 21060 | 21569 | 22586 | 22323 | 21135 | 20555 | 22117 | 22658 | 23626 | 23750 | 22403
8464 | 8464 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 16 | 18619 | 18448 | 17658 | 17223 | 19383 | 20956 | 20885 | 20712 | 19516 | 21206 | 21800 | 22792 | 22422 | 20944 | 20483 | 22287 | 22924 | 23672 | 23452 | 22179
8465 | 8465 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 17 | 19541 | 19188 | 18472 | 18193 | 20327 | 21770 | 21663 | 21429 | 20218 | 22026 | 22560 | 23488 | 23308 | 21686 | 21393 | 23342 | 23990 | 24558 | 24266 | 22944
8466 | 8466 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 18 | 20447 | 20111 | 19396 | 19479 | 21291 | 22545 | 22493 | 22282 | 21117 | 23072 | 23144 | 24287 | 24401 | 22773 | 22846 | 24807 | 24992 | 25774 | 25518 | 24104
8467 | 8467 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 19 | 20097 | 19906 | 18995 | 19359 | 21139 | 22187 | 22270 | 22215 | 20960 | 23038 | 23318 | 24327 | 24469 | 22956 | 23138 | 25071 | 25412 | 26027 | 25987 | 24414
8468 | 8468 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 20 | 19731 | 19658 | 18733 | 19180 | 21014 | 22057 | 22101 | 22153 | 20921 | 23003 | 23574 | 24636 | 24834 | 23301 | 23516 | 25417 | 26016 | 26612 | 26500 | 24917
8469 | 8469 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 21 | 19407 | 19430 | 18497 | 19110 | 20924 | 21913 | 21988 | 22190 | 21001 | 23141 | 23826 | 24998 | 25258 | 23801 | 24064 | 25929 | 26689 | 27296 | 27307 | 25650
8470 | 8470 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 22 | 18700 | 18880 | 18101 | 18645 | 20140 | 21398 | 21505 | 21850 | 20807 | 22581 | 23646 | 24833 | 25095 | 23905 | 23969 | 25525 | 26706 | 27315 | 27412 | 25892
8471 | 8471 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 23 | 17727 | 17870 | 17422 | 17798 | 19141 | 20542 | 20769 | 21068 | 20401 | 21706 | 22950 | 24193 | 24579 | 23650 | 23497 | 24746 | 26146 | 26888 | 26998 | 25709
8472 | 8472 | 353 | 12 | 19 | Winter | 12 | 18 | Winter | 24 | 16581 | 16708 | 16583 | 16836 | 17909 | 19571 | 19811 | 20101 | 19679 | 20755 | 22038 | 23405 | 23775 | 23013 | 22658 | 23819 | 25290 | 26141 | 26125 | 25121
8473 | 8473 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 1 | 15127 | 15612 | 15418 | 15866 | 17094 | 18131 | 18653 | 19078 | 18346 | 20226 | 21272 | 22130 | 22580 | 21022 | 21689 | 23688 | 24373 | 24957 | 24794 | 22897
8474 | 8474 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 2 | 14664 | 15113 | 14882 | 15493 | 16668 | 17669 | 18191 | 18639 | 17884 | 19870 | 20839 | 21645 | 21952 | 20434 | 21292 | 23228 | 23839 | 24254 | 24134 | 22264
8475 | 8475 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 3 | 14439 | 14762 | 14519 | 15315 | 16519 | 17489 | 17949 | 18390 | 17632 | 19779 | 20658 | 21415 | 21732 | 20188 | 21105 | 23020 | 23546 | 23945 | 23824 | 21965
8476 | 8476 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 4 | 14353 | 14573 | 14318 | 15264 | 16427 | 17320 | 17759 | 18107 | 17335 | 19532 | 20325 | 20922 | 21200 | 19653 | 20698 | 22468 | 22949 | 23201 | 23050 | 21298
8477 | 8477 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 5 | 14419 | 14439 | 14072 | 15371 | 16539 | 17254 | 17736 | 17843 | 16926 | 19349 | 20023 | 20447 | 20777 | 19019 | 20390 | 21952 | 22334 | 22536 | 22146 | 20503
8478 | 8478 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 6 | 14908 | 14411 | 13795 | 15854 | 17077 | 17510 | 18089 | 17595 | 16388 | 19581 | 19961 | 20206 | 20606 | 18262 | 20341 | 21827 | 21934 | 22123 | 21213 | 19591
8479 | 8479 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 7 | 16188 | 14924 | 14076 | 17281 | 18103 | 18692 | 19308 | 17959 | 16604 | 20383 | 20377 | 21104 | 21337 | 18127 | 21309 | 22238 | 22087 | 22700 | 21156 | 19369
8480 | 8480 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 8 | 17547 | 15938 | 15160 | 18824 | 19276 | 20107 | 20756 | 18908 | 17688 | 21388 | 21134 | 22384 | 22659 | 19048 | 22771 | 23090 | 22717 | 23941 | 21886 | 20268
8481 | 8481 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 9 | 17924 | 16626 | 15925 | 19259 | 19656 | 20562 | 21215 | 19614 | 18430 | 21778 | 21633 | 22731 | 23075 | 19699 | 23164 | 23373 | 23158 | 24317 | 22424 | 20899
8482 | 8482 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 10 | 17682 | 16696 | 16033 | 18961 | 19575 | 20287 | 20840 | 19635 | 18559 | 21809 | 21610 | 22497 | 22869 | 19977 | 22936 | 23501 | 23199 | 24148 | 22637 | 21220
8483 | 8483 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 11 | 17505 | 16465 | 15810 | 18471 | 19433 | 19929 | 20091 | 19122 | 18144 | 21547 | 21276 | 22042 | 22757 | 20197 | 22296 | 23375 | 22941 | 24070 | 22745 | 21476
8484 | 8484 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 12 | 17411 | 16229 | 15673 | 18119 | 19239 | 19602 | 19538 | 18606 | 17860 | 21097 | 20822 | 21595 | 22642 | 20311 | 21629 | 22867 | 22490 | 23969 | 22561 | 21591
8485 | 8485 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 13 | 17591 | 16271 | 15758 | 18116 | 19301 | 19669 | 19515 | 18557 | 17948 | 21013 | 20850 | 21614 | 22671 | 20380 | 21523 | 22783 | 22519 | 23981 | 22474 | 21649
8486 | 8486 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 14 | 17904 | 16529 | 16106 | 18504 | 19579 | 19976 | 19838 | 18780 | 18325 | 21182 | 21052 | 21892 | 22919 | 20673 | 21761 | 22788 | 22665 | 24209 | 22674 | 21922
8487 | 8487 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 15 | 18029 | 16723 | 16458 | 18804 | 19501 | 20193 | 20129 | 19070 | 18736 | 21148 | 21034 | 22141 | 22445 | 20367 | 21971 | 22529 | 22607 | 23699 | 22337 | 21603
8488 | 8488 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 16 | 18097 | 16893 | 16769 | 18983 | 19605 | 20258 | 20260 | 19145 | 18828 | 21317 | 21043 | 22077 | 22027 | 20117 | 21962 | 22625 | 22553 | 23227 | 21926 | 21332
8489 | 8489 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 17 | 18860 | 17660 | 17709 | 19856 | 20260 | 21043 | 20980 | 19785 | 19605 | 22075 | 21756 | 22849 | 22706 | 20924 | 22913 | 23582 | 23269 | 23940 | 22590 | 22161
8490 | 8490 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 18 | 19577 | 18603 | 19005 | 20868 | 21012 | 21934 | 21855 | 20723 | 20862 | 22658 | 22735 | 23902 | 23837 | 22364 | 24370 | 24582 | 24446 | 25189 | 23758 | 23673
8491 | 8491 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 19 | 19269 | 18210 | 18884 | 20707 | 20946 | 21705 | 21766 | 20527 | 20768 | 22765 | 22785 | 23915 | 24118 | 22632 | 24616 | 24980 | 24779 | 25672 | 24084 | 24039
8492 | 8492 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 20 | 19015 | 17915 | 18677 | 20560 | 20837 | 21495 | 21645 | 20415 | 20789 | 22931 | 22908 | 24197 | 24388 | 22961 | 24926 | 25542 | 25237 | 26170 | 24583 | 24491
8493 | 8493 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 21 | 18763 | 17698 | 18601 | 20450 | 20679 | 21347 | 21621 | 20414 | 20942 | 23108 | 23146 | 24539 | 24906 | 23470 | 25408 | 26171 | 25866 | 26978 | 25314 | 25180
8494 | 8494 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 22 | 18138 | 17279 | 18099 | 19670 | 20171 | 20800 | 21211 | 20186 | 20659 | 22860 | 22947 | 24311 | 24831 | 23333 | 24965 | 26159 | 25913 | 27055 | 25538 | 25151
8495 | 8495 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 23 | 17239 | 16593 | 17236 | 18613 | 19239 | 20037 | 20393 | 19673 | 20003 | 22150 | 22471 | 23778 | 24327 | 22858 | 24186 | 25600 | 25567 | 26641 | 25375 | 24738
8496 | 8496 | 354 | 12 | 20 | Winter | 12 | 19 | Winter | 24 | 16071 | 15702 | 16218 | 17412 | 18125 | 19014 | 19358 | 18992 | 19200 | 21211 | 21772 | 22935 | 23367 | 21996 | 23235 | 24727 | 24928 | 25744 | 24767 | 23911
8497 | 8497 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 1 | 15056 | 14695 | 15389 | 16611 | 17725 | 17952 | 18419 | 17721 | 18457 | 20704 | 21100 | 21945 | 22308 | 21250 | 23270 | 24029 | 24124 | 24600 | 22755 | 23117
8498 | 8498 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 2 | 14568 | 14094 | 14949 | 16110 | 17255 | 17406 | 17888 | 17183 | 18109 | 20265 | 20656 | 21317 | 21701 | 20844 | 22798 | 23483 | 23586 | 23920 | 22100 | 22665
8499 | 8499 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 3 | 14282 | 13774 | 14821 | 16005 | 17071 | 17245 | 17735 | 17022 | 18030 | 20127 | 20511 | 21139 | 21489 | 20690 | 22622 | 23219 | 23326 | 23632 | 21821 | 22464
8500 | 8500 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 4 | 14199 | 13590 | 14783 | 15930 | 16959 | 17097 | 17501 | 16774 | 17896 | 19861 | 20196 | 20675 | 20924 | 20325 | 22114 | 22649 | 22744 | 22879 | 21168 | 21974
8501 | 8501 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 5 | 14345 | 13378 | 14928 | 16079 | 16963 | 17148 | 17331 | 16438 | 17847 | 19637 | 19937 | 20334 | 20280 | 20067 | 21647 | 22075 | 22163 | 22003 | 20389 | 21563
8502 | 8502 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 6 | 14911 | 13148 | 15475 | 16685 | 17253 | 17595 | 17214 | 16026 | 18054 | 19650 | 19917 | 20259 | 19618 | 20066 | 21572 | 21717 | 21810 | 21098 | 19491 | 21421
8503 | 8503 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 7 | 16144 | 13372 | 16866 | 17681 | 17944 | 18769 | 17564 | 16209 | 19325 | 20103 | 20365 | 21038 | 19730 | 21040 | 21999 | 21874 | 22041 | 21036 | 19252 | 22326
8504 | 8504 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 8 | 17557 | 14438 | 18389 | 18862 | 18856 | 20201 | 18518 | 17301 | 20935 | 20895 | 21167 | 22375 | 20525 | 22501 | 22863 | 22495 | 22736 | 21758 | 20138 | 23763
8505 | 8505 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 9 | 17966 | 15181 | 18795 | 19198 | 19368 | 20625 | 19198 | 18030 | 21449 | 21398 | 21611 | 22785 | 21091 | 22877 | 23132 | 22915 | 23123 | 22275 | 20743 | 24103
8506 | 8506 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 10 | 17514 | 15235 | 18459 | 19046 | 19190 | 20234 | 19200 | 18141 | 21062 | 21251 | 21458 | 22464 | 21147 | 22534 | 23141 | 22845 | 23030 | 22373 | 20951 | 23794
8507 | 8507 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 11 | 17000 | 15283 | 18296 | 19216 | 18923 | 19974 | 19211 | 18242 | 20314 | 20835 | 21045 | 22272 | 21155 | 21824 | 22940 | 22510 | 22691 | 22410 | 21139 | 23111
8508 | 8508 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 12 | 16658 | 15370 | 18207 | 19251 | 18623 | 19800 | 19106 | 18298 | 19686 | 20327 | 20553 | 22106 | 20908 | 21107 | 22380 | 22015 | 22213 | 22169 | 21204 | 22402
8509 | 8509 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 13 | 16673 | 15463 | 18234 | 19286 | 18677 | 19819 | 19113 | 18356 | 19558 | 20330 | 20552 | 22092 | 20808 | 20973 | 22266 | 21995 | 22189 | 22055 | 21233 | 22255
8510 | 8510 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 14 | 16896 | 15692 | 18506 | 19448 | 18845 | 20017 | 19214 | 18575 | 19825 | 20438 | 20676 | 22249 | 20942 | 21113 | 22175 | 22047 | 22274 | 22153 | 21402 | 22368
8511 | 8511 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 15 | 17140 | 15724 | 18437 | 19003 | 18859 | 19761 | 18900 | 18388 | 20240 | 20463 | 20710 | 21816 | 20660 | 21363 | 21959 | 22026 | 22261 | 21853 | 21119 | 22603
8512 | 8512 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 16 | 17538 | 16033 | 18595 | 19129 | 19117 | 19782 | 18827 | 18428 | 20502 | 20649 | 20846 | 21595 | 20459 | 21530 | 22234 | 22157 | 22337 | 21612 | 21014 | 22748
8513 | 8513 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 17 | 18381 | 17117 | 19612 | 20016 | 19967 | 20646 | 19598 | 19444 | 21492 | 21513 | 21698 | 22439 | 21258 | 22637 | 23347 | 23043 | 23237 | 22436 | 22002 | 23883
8514 | 8514 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 18 | 19311 | 18394 | 20585 | 20795 | 20934 | 21504 | 20486 | 20665 | 22577 | 22472 | 22690 | 23526 | 22330 | 24082 | 24339 | 24217 | 24406 | 23622 | 23523 | 25400
8515 | 8515 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 19 | 19127 | 18269 | 20420 | 20716 | 20782 | 21405 | 20268 | 20542 | 22524 | 22464 | 22719 | 23761 | 22488 | 24304 | 24707 | 24538 | 24697 | 23955 | 23903 | 25721
8516 | 8516 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 20 | 18854 | 18052 | 20256 | 20577 | 20577 | 21254 | 20111 | 20518 | 22420 | 22493 | 22822 | 23960 | 22759 | 24580 | 25229 | 24964 | 25113 | 24452 | 24359 | 26099
8517 | 8517 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 21 | 18625 | 17972 | 20144 | 20394 | 20418 | 21188 | 20054 | 20621 | 22512 | 22661 | 23047 | 24401 | 23209 | 25027 | 25817 | 25570 | 25708 | 25186 | 25058 | 26720
8518 | 8518 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 22 | 18061 | 17471 | 19347 | 19831 | 19941 | 20726 | 19761 | 20255 | 21899 | 22428 | 22858 | 24267 | 23267 | 24572 | 25791 | 25592 | 25743 | 25414 | 25040 | 26368
8519 | 8519 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 23 | 17039 | 16603 | 18275 | 18888 | 19207 | 19899 | 19247 | 19596 | 20983 | 21903 | 22347 | 23701 | 22980 | 23755 | 25198 | 25206 | 25354 | 25213 | 24602 | 25605
8520 | 8520 | 355 | 12 | 21 | Winter | 12 | 20 | Winter | 24 | 15859 | 15524 | 16987 | 17681 | 18304 | 18741 | 18436 | 18650 | 19980 | 21203 | 21665 | 22724 | 22311 | 22799 | 24318 | 24564 | 24721 | 24594 | 23774 | 24682
8521 | 8521 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 1 | 14961 | 14816 | 16276 | 17459 | 17753 | 17959 | 17369 | 17934 | 19543 | 20636 | 21291 | 21797 | 20709 | 22864 | 23717 | 23867 | 24335 | 22676 | 23063 | 24950
8522 | 8522 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 2 | 14435 | 14382 | 15783 | 16976 | 17300 | 17434 | 16833 | 17521 | 19108 | 20224 | 20835 | 21225 | 20125 | 22419 | 23197 | 23350 | 23780 | 22035 | 22625 | 24462
8523 | 8523 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 3 | 14129 | 14200 | 15626 | 16756 | 17113 | 17237 | 16636 | 17511 | 19121 | 20086 | 20664 | 21022 | 19898 | 22241 | 22930 | 23091 | 23498 | 21742 | 22408 | 24233
8524 | 8524 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 4 | 13953 | 14154 | 15546 | 16648 | 16998 | 17021 | 16403 | 17413 | 18933 | 19818 | 20339 | 20518 | 19407 | 21765 | 22385 | 22532 | 22921 | 21089 | 21913 | 23607
8525 | 8525 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 5 | 13826 | 14264 | 15676 | 16648 | 16987 | 16854 | 16076 | 17414 | 18840 | 19602 | 20041 | 19928 | 18815 | 21332 | 21837 | 21973 | 22311 | 20310 | 21493 | 22989
8526 | 8526 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 6 | 13835 | 14813 | 16269 | 16959 | 17275 | 16756 | 15688 | 17700 | 19199 | 19655 | 19969 | 19353 | 18116 | 21308 | 21525 | 21652 | 21910 | 19430 | 21358 | 22784
8527 | 8527 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 7 | 14292 | 16253 | 17357 | 17681 | 17988 | 17208 | 15998 | 19033 | 19980 | 20188 | 20455 | 19532 | 17998 | 21790 | 21731 | 21909 | 22136 | 19214 | 22276 | 23132
8528 | 8528 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 8 | 15315 | 17785 | 18595 | 18631 | 18958 | 18205 | 17134 | 20679 | 21031 | 21048 | 21378 | 20382 | 18947 | 22706 | 22399 | 22638 | 22944 | 20125 | 23736 | 23958
8529 | 8529 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 9 | 15963 | 18179 | 18932 | 19142 | 19444 | 18864 | 17864 | 21196 | 21402 | 21509 | 21893 | 20951 | 19583 | 22981 | 22822 | 23024 | 23415 | 20725 | 24078 | 24190
8530 | 8530 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 10 | 16099 | 17973 | 18869 | 19077 | 19366 | 18966 | 18070 | 21022 | 21527 | 21458 | 21873 | 21117 | 19848 | 23093 | 22859 | 23042 | 23444 | 21042 | 23883 | 24361
8531 | 8531 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 11 | 16170 | 17883 | 19064 | 18925 | 19165 | 18994 | 18182 | 20930 | 21938 | 21115 | 21534 | 21191 | 20069 | 22963 | 22600 | 22771 | 23154 | 21310 | 23283 | 24289
8532 | 8532 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 12 | 16089 | 17705 | 19018 | 18665 | 18859 | 18769 | 18104 | 20662 | 21938 | 20601 | 21020 | 20926 | 20111 | 22381 | 22080 | 22266 | 22637 | 21356 | 22550 | 23720
8533 | 8533 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 13 | 16351 | 17934 | 19250 | 18959 | 19132 | 18957 | 18333 | 20788 | 22136 | 20825 | 21231 | 21051 | 20369 | 22491 | 22282 | 22466 | 22827 | 21606 | 22624 | 23817
8534 | 8534 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 14 | 16433 | 18186 | 19410 | 19076 | 19246 | 19062 | 18560 | 21039 | 22121 | 20901 | 21287 | 21132 | 20494 | 22353 | 22282 | 22492 | 22830 | 21719 | 22682 | 23634
8535 | 8535 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 15 | 16351 | 18211 | 19105 | 19092 | 19269 | 18914 | 18543 | 20911 | 21385 | 20939 | 21305 | 20863 | 20222 | 22145 | 22263 | 22488 | 22808 | 21434 | 22914 | 23388
8536 | 8536 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 16 | 16413 | 18303 | 19126 | 19232 | 19381 | 18805 | 18541 | 20750 | 21218 | 20955 | 21277 | 20554 | 20027 | 22308 | 22275 | 22445 | 22730 | 21201 | 22929 | 23505
8537 | 8537 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 17 | 17172 | 19149 | 19839 | 19944 | 20088 | 19389 | 19357 | 21492 | 21948 | 21659 | 21993 | 21190 | 20838 | 23261 | 23003 | 23188 | 23485 | 22033 | 23906 | 24476
8538 | 8538 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 18 | 18078 | 20119 | 20662 | 20902 | 21031 | 20311 | 20590 | 22509 | 22460 | 22575 | 23092 | 22187 | 22247 | 24214 | 24138 | 24328 | 24776 | 23540 | 25399 | 25500
8539 | 8539 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 19 | 17660 | 19919 | 20540 | 20695 | 20808 | 20051 | 20417 | 22383 | 22486 | 22502 | 23073 | 22250 | 22453 | 24504 | 24395 | 24557 | 25043 | 23892 | 25690 | 25941
8540 | 8540 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 20 | 17364 | 19744 | 20367 | 20452 | 20611 | 19861 | 20356 | 22237 | 22591 | 22524 | 23126 | 22456 | 22748 | 24971 | 24785 | 24953 | 25407 | 24345 | 26073 | 26574
8541 | 8541 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 21 | 17156 | 19611 | 20156 | 20273 | 20448 | 19755 | 20410 | 22279 | 22696 | 22672 | 23321 | 22831 | 23212 | 25509 | 25343 | 25523 | 25967 | 25036 | 26695 | 27330
8542 | 8542 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 22 | 16714 | 18832 | 19565 | 19754 | 19960 | 19430 | 20012 | 21612 | 22355 | 22418 | 23106 | 22823 | 23034 | 25425 | 25310 | 25516 | 25962 | 24987 | 26316 | 27386
8543 | 8543 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 23 | 16051 | 17742 | 18591 | 19013 | 19249 | 18869 | 19308 | 20718 | 21676 | 21909 | 22640 | 22520 | 22538 | 24824 | 24928 | 25131 | 25612 | 24561 | 25576 | 26861
8544 | 8544 | 356 | 12 | 22 | Winter | 12 | 21 | Winter | 24 | 15114 | 16454 | 17372 | 18085 | 18368 | 18045 | 18349 | 19598 | 20605 | 21218 | 21935 | 21834 | 21667 | 23933 | 24277 | 24492 | 24957 | 23724 | 24652 | 26020
8545 | 8545 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 1 | 13963 | 15436 | 16884 | 17252 | 17672 | 16741 | 17351 | 18847 | 20010 | 20609 | 21357 | 20043 | 20762 | 23110 | 23349 | 23843 | 24403 | 22768 | 24663 | 25117
8546 | 8546 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 2 | 13393 | 14939 | 16406 | 16793 | 17210 | 16210 | 16947 | 18421 | 19605 | 20190 | 20909 | 19491 | 20397 | 22614 | 22859 | 23313 | 23859 | 22347 | 24187 | 24568
8547 | 8547 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 3 | 13072 | 14756 | 16174 | 16593 | 17027 | 15995 | 16926 | 18426 | 19465 | 20053 | 20730 | 19294 | 20252 | 22374 | 22624 | 23053 | 23568 | 22143 | 23970 | 24268
8548 | 8548 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 4 | 12879 | 14666 | 16048 | 16478 | 16907 | 15773 | 16848 | 18270 | 19234 | 19782 | 20388 | 18844 | 19915 | 21850 | 22095 | 22491 | 22959 | 21653 | 23346 | 23595
8549 | 8549 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 5 | 12661 | 14811 | 16024 | 16488 | 16892 | 15494 | 16909 | 18236 | 19060 | 19561 | 20058 | 18314 | 19693 | 21313 | 21578 | 21919 | 22314 | 21251 | 22741 | 22885
8550 | 8550 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 6 | 12407 | 15423 | 16229 | 16809 | 17146 | 15173 | 17289 | 18658 | 19138 | 19562 | 19924 | 17682 | 19734 | 20915 | 21290 | 21547 | 21856 | 21120 | 22534 | 22307
8551 | 8551 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 7 | 12654 | 16499 | 16822 | 17556 | 17871 | 15431 | 18589 | 19519 | 19663 | 20084 | 20286 | 17625 | 20745 | 20995 | 21565 | 21801 | 21990 | 22032 | 22874 | 22270
8552 | 8552 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 8 | 13732 | 17751 | 17709 | 18525 | 18902 | 16559 | 20240 | 20621 | 20509 | 21025 | 21202 | 18594 | 22241 | 21633 | 22305 | 22619 | 22780 | 23488 | 23699 | 22846
8553 | 8553 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 9 | 14496 | 18134 | 18289 | 19046 | 19486 | 17313 | 20796 | 21051 | 21041 | 21600 | 21768 | 19283 | 22658 | 22113 | 22737 | 23132 | 23262 | 23870 | 23972 | 23296
8554 | 8554 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 10 | 14719 | 18088 | 18356 | 19018 | 19488 | 17551 | 20654 | 21204 | 21058 | 21609 | 21826 | 19590 | 22481 | 22254 | 22788 | 23206 | 23397 | 23709 | 24177 | 23475
8555 | 8555 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 11 | 14830 | 18288 | 18317 | 18867 | 19294 | 17704 | 20609 | 21599 | 20747 | 21254 | 21507 | 19809 | 21856 | 22029 | 22505 | 22916 | 23147 | 23102 | 24097 | 23286
8556 | 8556 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 12 | 14963 | 18425 | 18269 | 18731 | 19104 | 17854 | 20581 | 21714 | 20360 | 20849 | 21104 | 19964 | 21232 | 21667 | 22112 | 22514 | 22746 | 22480 | 23637 | 22924
8557 | 8557 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 13 | 15059 | 18510 | 18395 | 18837 | 19192 | 17961 | 20589 | 21736 | 20411 | 20878 | 21121 | 20041 | 21136 | 21689 | 22128 | 22522 | 22747 | 22370 | 23554 | 22949
8558 | 8558 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 14 | 15014 | 18419 | 18259 | 18725 | 19060 | 17881 | 20533 | 21499 | 20228 | 20697 | 20904 | 19937 | 20981 | 21448 | 21913 | 22293 | 22487 | 22185 | 23130 | 22682
8559 | 8559 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 15 | 15209 | 18186 | 18368 | 18835 | 19169 | 17856 | 20381 | 20901 | 20349 | 20810 | 21009 | 19762 | 21328 | 21554 | 22002 | 22366 | 22561 | 22507 | 22976 | 22766
8560 | 8560 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 16 | 15502 | 18284 | 18572 | 19027 | 19315 | 17933 | 20290 | 20811 | 20500 | 20867 | 21079 | 19648 | 21454 | 21610 | 22044 | 22363 | 22575 | 22598 | 23170 | 22787
8561 | 8561 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 17 | 16478 | 19104 | 19398 | 19804 | 20095 | 18899 | 21178 | 21624 | 21283 | 21633 | 21906 | 20525 | 22477 | 22466 | 22859 | 23187 | 23436 | 23648 | 24209 | 23664
8562 | 8562 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 18 | 17715 | 19930 | 20394 | 20707 | 21107 | 20113 | 22139 | 22127 | 22187 | 22656 | 22972 | 21853 | 23854 | 23670 | 23956 | 24438 | 24678 | 25123 | 25210 | 24944
8563 | 8563 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 19 | 17551 | 19757 | 20153 | 20461 | 20888 | 19908 | 21969 | 22085 | 22060 | 22566 | 22973 | 21989 | 23983 | 23876 | 24136 | 24658 | 24960 | 25401 | 25629 | 25271
8564 | 8564 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 20 | 17325 | 19539 | 19829 | 20220 | 20631 | 19820 | 21782 | 22110 | 22030 | 22537 | 22990 | 22209 | 24210 | 24140 | 24486 | 24973 | 25323 | 25776 | 26253 | 25691
8565 | 8565 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 21 | 17221 | 19297 | 19567 | 20008 | 20431 | 19813 | 21752 | 22121 | 22102 | 22629 | 23186 | 22588 | 24586 | 24585 | 24983 | 25480 | 25905 | 26363 | 26980 | 26344
8566 | 8566 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 22 | 16717 | 18636 | 19063 | 19499 | 19952 | 19350 | 21013 | 21728 | 21800 | 22372 | 23013 | 22371 | 24084 | 24559 | 24945 | 25456 | 25955 | 25975 | 27030 | 26443
8567 | 8567 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 23 | 15836 | 17644 | 18378 | 18751 | 19256 | 18615 | 20089 | 20984 | 21242 | 21869 | 22569 | 21836 | 23256 | 24232 | 24535 | 25082 | 25634 | 25218 | 26499 | 26200
8568 | 8568 | 357 | 12 | 23 | Winter | 12 | 22 | Winter | 24 | 14775 | 16407 | 17577 | 17848 | 18369 | 17617 | 18924 | 19882 | 20522 | 21169 | 21816 | 20960 | 22302 | 23734 | 23900 | 24430 | 24934 | 24293 | 25662 | 25743
8569 | 8569 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 1 | 15651 | 15013 | 15811 | 16269 | 17347 | 17426 | 18028 | 18605 | 19608 | 19956 | 20618 | 21342 | 21945 | 22571 | 23125 | 23593 | 24168 | 24317 | 24541 | 24730
8570 | 8570 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 2 | 15284 | 14488 | 15278 | 15761 | 16876 | 16929 | 17560 | 18142 | 19204 | 19489 | 20126 | 20828 | 21524 | 22020 | 22557 | 23012 | 23625 | 23721 | 23942 | 24135
8571 | 8571 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 3 | 15200 | 14131 | 14941 | 15459 | 16692 | 16689 | 17349 | 17950 | 19086 | 19312 | 19922 | 20600 | 21382 | 21748 | 22268 | 22707 | 23347 | 23398 | 23610 | 23806
8572 | 8572 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 4 | 15161 | 13881 | 14686 | 15198 | 16545 | 16409 | 17047 | 17614 | 18856 | 18878 | 19424 | 20040 | 20945 | 21076 | 21551 | 21952 | 22709 | 22589 | 22788 | 22982
8573 | 8573 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 5 | 15375 | 13655 | 14448 | 14951 | 16517 | 16117 | 16717 | 17277 | 18721 | 18371 | 18889 | 19385 | 20592 | 20288 | 20710 | 21065 | 22065 | 21636 | 21826 | 21998
8574 | 8574 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 6 | 15999 | 13462 | 14250 | 14793 | 16719 | 15845 | 16439 | 16941 | 18837 | 17886 | 18337 | 18703 | 20630 | 19472 | 19839 | 20150 | 21553 | 20651 | 20818 | 20981
8575 | 8575 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 7 | 17186 | 13599 | 14321 | 14908 | 17356 | 15839 | 16436 | 16831 | 19397 | 17711 | 18051 | 18398 | 21142 | 19061 | 19385 | 19659 | 21542 | 20104 | 20252 | 20408
8576 | 8576 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 8 | 18546 | 14328 | 15021 | 15558 | 18417 | 16505 | 17035 | 17399 | 20283 | 18335 | 18638 | 18875 | 22074 | 19471 | 19768 | 20146 | 22252 | 20430 | 20566 | 20716
8577 | 8577 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 9 | 18935 | 15062 | 15771 | 16247 | 19007 | 17243 | 17716 | 18070 | 20810 | 18957 | 19227 | 19437 | 22410 | 19982 | 20259 | 20619 | 22711 | 20880 | 21010 | 21153
8578 | 8578 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 10 | 18910 | 15582 | 16316 | 16796 | 19295 | 17822 | 18313 | 18684 | 21062 | 19598 | 19878 | 20101 | 22817 | 20666 | 20951 | 21318 | 23146 | 21593 | 21728 | 21875
8579 | 8579 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 11 | 18919 | 15912 | 16619 | 17107 | 19342 | 18162 | 18672 | 19061 | 20916 | 20001 | 20290 | 20525 | 22856 | 21110 | 21403 | 21777 | 23133 | 22066 | 22208 | 22357
8580 | 8580 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 12 | 18889 | 16112 | 16818 | 17301 | 19218 | 18352 | 18862 | 19252 | 20573 | 20196 | 20488 | 20728 | 22417 | 21319 | 21614 | 21990 | 22804 | 22284 | 22427 | 22576
8581 | 8581 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 13 | 18561 | 15888 | 16574 | 17048 | 18871 | 18084 | 18585 | 18969 | 20192 | 19901 | 20193 | 20431 | 21912 | 21019 | 21313 | 21688 | 22389 | 21979 | 22121 | 22270
8582 | 8582 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 14 | 18391 | 15642 | 16310 | 16780 | 18521 | 17806 | 18303 | 18682 | 19832 | 19602 | 19887 | 20117 | 21341 | 20689 | 20976 | 21345 | 21929 | 21627 | 21766 | 21912
8583 | 8583 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 15 | 18356 | 15637 | 16279 | 16710 | 18482 | 17658 | 18114 | 18457 | 19865 | 19311 | 19591 | 19814 | 21136 | 20375 | 20658 | 21024 | 21925 | 21301 | 21439 | 21585
8584 | 8584 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 16 | 18885 | 15979 | 16585 | 16969 | 18947 | 17821 | 18226 | 18525 | 20304 | 19292 | 19559 | 19767 | 21711 | 20302 | 20574 | 20931 | 22284 | 21198 | 21336 | 21483
8585 | 8585 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 17 | 19576 | 16691 | 17286 | 17656 | 19656 | 18473 | 18859 | 19067 | 20996 | 19898 | 20097 | 20393 | 22651 | 20943 | 21223 | 21586 | 23072 | 21863 | 22005 | 22156
8586 | 8586 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 18 | 20338 | 17386 | 17976 | 18223 | 20561 | 19039 | 19306 | 19566 | 21835 | 20314 | 20640 | 20975 | 23504 | 21594 | 21905 | 22292 | 24301 | 22600 | 22749 | 22906
8587 | 8587 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 19 | 20098 | 16751 | 17442 | 17701 | 20354 | 18540 | 18827 | 19118 | 21731 | 19979 | 20388 | 20716 | 23757 | 21460 | 21823 | 22254 | 24657 | 22606 | 22759 | 22920
8588 | 8588 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 20 | 19785 | 16255 | 16894 | 17265 | 20099 | 18101 | 18517 | 18868 | 21640 | 19884 | 20382 | 20796 | 24136 | 21685 | 22108 | 22587 | 25026 | 23000 | 23163 | 23334
8589 | 8589 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 21 | 19457 | 16032 | 16708 | 17112 | 19927 | 18045 | 18525 | 18950 | 21695 | 20145 | 20740 | 21252 | 24588 | 22314 | 22806 | 23344 | 25632 | 23839 | 24022 | 24202
8590 | 8590 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 22 | 18727 | 15881 | 16583 | 17019 | 19466 | 18041 | 18577 | 19063 | 21390 | 20380 | 21026 | 21596 | 24461 | 22762 | 23296 | 23869 | 25699 | 24422 | 24619 | 24813
8591 | 8591 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 23 | 17734 | 15542 | 16264 | 16740 | 18816 | 17841 | 18424 | 18941 | 20859 | 20375 | 21031 | 21647 | 23855 | 22868 | 23423 | 24016 | 25446 | 24590 | 24800 | 24990
8592 | 8592 | 358 | 12 | 24 | Winter | 12 | 23 | Winter | 24 | 16572 | 15078 | 15814 | 16296 | 17843 | 17463 | 18060 | 18628 | 20151 | 19982 | 20659 | 21414 | 22960 | 22661 | 23224 | 23698 | 24834 | 24420 | 24640 | 24837
8593 | 8593 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 1 | 14304 | 14281 | 14927 | 15358 | 16800 | 16395 | 17003 | 17580 | 19319 | 18938 | 19601 | 20337 | 22077 | 21568 | 22121 | 22589 | 24099 | 23313 | 23536 | 23723
8594 | 8594 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 2 | 13760 | 13792 | 14466 | 14902 | 16282 | 15963 | 16579 | 17161 | 18819 | 18515 | 19150 | 19845 | 21521 | 21031 | 21565 | 22017 | 23485 | 22721 | 22942 | 23126
8595 | 8595 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 3 | 13413 | 13571 | 14264 | 14721 | 16022 | 15819 | 16451 | 17040 | 18648 | 18389 | 18995 | 19658 | 21277 | 20794 | 21306 | 21741 | 23175 | 22422 | 22642 | 22818
8596 | 8596 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 4 | 13166 | 13511 | 14194 | 14641 | 15748 | 15707 | 16311 | 16862 | 18264 | 18102 | 18639 | 19235 | 20653 | 20251 | 20714 | 21108 | 22384 | 21731 | 21935 | 22108
8597 | 8597 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 5 | 12997 | 13653 | 14340 | 14822 | 15487 | 15794 | 16405 | 16858 | 17830 | 18011 | 18427 | 18945 | 19933 | 19820 | 20227 | 20573 | 21466 | 21125 | 21307 | 21467
8598 | 8598 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 6 | 12877 | 14001 | 14741 | 15228 | 15269 | 16133 | 16704 | 17040 | 17391 | 18099 | 18384 | 18821 | 19195 | 19549 | 19896 | 20192 | 20530 | 20665 | 20821 | 20969
8599 | 8599 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 7 | 12988 | 14542 | 15326 | 15751 | 15351 | 16647 | 17122 | 17450 | 17230 | 18348 | 18619 | 18947 | 18837 | 19564 | 19866 | 20125 | 20014 | 20539 | 20678 | 20818
8600 | 8600 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 8 | 13668 | 15095 | 15825 | 16363 | 16162 | 17096 | 17549 | 17896 | 17806 | 18798 | 18957 | 19240 | 19276 | 19796 | 20201 | 20440 | 20355 | 20700 | 20830 | 20968
8601 | 8601 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 9 | 14387 | 15664 | 16331 | 16855 | 16820 | 17579 | 18026 | 18364 | 18484 | 19224 | 19356 | 19669 | 19791 | 20190 | 20582 | 20810 | 20787 | 21061 | 21193 | 21328
8602 | 8602 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 10 | 14393 | 15754 | 16401 | 16915 | 16874 | 17645 | 18100 | 18447 | 18607 | 19318 | 19457 | 19780 | 19960 | 20324 | 20725 | 20961 | 20987 | 21228 | 21366 | 21504
8603 | 8603 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 11 | 14423 | 15759 | 16371 | 16840 | 16889 | 17505 | 17931 | 18256 | 18692 | 19085 | 19235 | 19572 | 20089 | 20140 | 20552 | 20797 | 21147 | 21082 | 21228 | 21371
8604 | 8604 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 12 | 14448 | 15791 | 16370 | 16795 | 16904 | 17382 | 17771 | 18067 | 18708 | 18844 | 18999 | 19340 | 20118 | 19914 | 20328 | 20575 | 21184 | 20865 | 21013 | 21157
8605 | 8605 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 13 | 14718 | 15998 | 16561 | 16979 | 17131 | 17548 | 17929 | 18218 | 18906 | 18985 | 19140 | 19480 | 20308 | 20050 | 20462 | 20707 | 21369 | 20995 | 21141 | 21288
8606 | 8606 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 14 | 14836 | 15979 | 16527 | 16944 | 17213 | 17504 | 17879 | 18164 | 18968 | 18917 | 19065 | 19398 | 20338 | 19952 | 20357 | 20597 | 21376 | 20876 | 21020 | 21164
8607 | 8607 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 15 | 14865 | 16056 | 16622 | 17046 | 17133 | 17613 | 17990 | 18274 | 18736 | 19024 | 19167 | 19492 | 20061 | 20033 | 20433 | 20669 | 21083 | 20940 | 21082 | 21225
8608 | 8608 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 16 | 14959 | 16371 | 16910 | 17308 | 17084 | 17819 | 18164 | 18418 | 18494 | 19108 | 19233 | 19541 | 19737 | 20049 | 20436 | 20660 | 20724 | 20915 | 21054 | 21195
8609 | 8609 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 17 | 15879 | 17330 | 17886 | 18201 | 18041 | 18774 | 19029 | 19355 | 19387 | 19961 | 20176 | 20492 | 20655 | 21011 | 21402 | 21631 | 21672 | 21891 | 22031 | 22175
8610 | 8610 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 18 | 16683 | 18337 | 18798 | 19169 | 18772 | 19618 | 19928 | 20240 | 19986 | 20865 | 21129 | 21486 | 21387 | 22072 | 22491 | 22745 | 22519 | 23034 | 23165 | 23327
8611 | 8611 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 19 | 16098 | 18209 | 18674 | 19067 | 18175 | 19552 | 19885 | 20154 | 19566 | 20977 | 21247 | 21759 | 21171 | 22474 | 22947 | 23245 | 22493 | 23580 | 23716 | 23874
8612 | 8612 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 20 | 15598 | 18038 | 18611 | 19042 | 17796 | 19611 | 19995 | 20328 | 19322 | 21313 | 21678 | 22201 | 21342 | 23073 | 23609 | 23960 | 22880 | 24359 | 24512 | 24678
8613 | 8613 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 21 | 15345 | 18022 | 18627 | 19097 | 17681 | 19770 | 20219 | 20629 | 19483 | 21802 | 22267 | 22892 | 21883 | 23942 | 24548 | 24961 | 23677 | 25443 | 25615 | 25797
8614 | 8614 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 22 | 15191 | 17697 | 18323 | 18827 | 17637 | 19597 | 20104 | 20578 | 19672 | 21880 | 22399 | 23085 | 22299 | 24244 | 24893 | 25340 | 24247 | 25878 | 26069 | 26264
8615 | 8615 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 23 | 14836 | 17145 | 17794 | 18318 | 17401 | 19185 | 19720 | 20260 | 19629 | 21642 | 22209 | 22929 | 22390 | 24149 | 24814 | 25289 | 24412 | 25860 | 26062 | 26266
8616 | 8616 | 359 | 12 | 25 | Winter | 12 | 24 | Winter | 24 | 14378 | 16370 | 17027 | 17482 | 16872 | 18546 | 19146 | 19734 | 19365 | 21070 | 21774 | 22510 | 22181 | 23764 | 24317 | 24801 | 24234 | 25523 | 25743 | 25942
8617 | 8617 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 1 | 13851 | 15643 | 16339 | 16826 | 16039 | 17973 | 18611 | 19233 | 18446 | 20630 | 21335 | 22063 | 21236 | 23338 | 23910 | 24393 | 23254 | 25129 | 25358 | 25562
8618 | 8618 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 2 | 13412 | 15156 | 15849 | 16335 | 15605 | 17504 | 18153 | 18767 | 18057 | 20176 | 20838 | 21559 | 20745 | 22791 | 23345 | 23812 | 22694 | 24535 | 24763 | 24956
8619 | 8619 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 3 | 13177 | 14919 | 15623 | 16124 | 15426 | 17321 | 17985 | 18604 | 17923 | 20010 | 20640 | 21333 | 20515 | 22514 | 23047 | 23496 | 22386 | 24201 | 24421 | 24611
8620 | 8620 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 4 | 13128 | 14844 | 15556 | 16043 | 15333 | 17202 | 17839 | 18418 | 17697 | 19713 | 20274 | 20898 | 20032 | 21957 | 22440 | 22848 | 21721 | 23495 | 23702 | 23880
8621 | 8621 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 5 | 13254 | 14861 | 15605 | 16027 | 15431 | 17168 | 17714 | 18235 | 17613 | 19386 | 19866 | 20408 | 19649 | 21321 | 21746 | 22105 | 21128 | 22678 | 22869 | 23038
8622 | 8622 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 6 | 13568 | 15125 | 15854 | 16186 | 15730 | 17285 | 17720 | 18159 | 17740 | 19132 | 19526 | 20025 | 19416 | 20780 | 21149 | 21460 | 20675 | 21961 | 22130 | 22289
8623 | 8623 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 7 | 14166 | 15585 | 16235 | 16561 | 16227 | 17515 | 17940 | 18257 | 18101 | 19119 | 19396 | 19874 | 19480 | 20501 | 20827 | 21102 | 20576 | 21549 | 21703 | 21858
8624 | 8624 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 8 | 14754 | 15920 | 16697 | 17057 | 16750 | 17811 | 18274 | 18552 | 18597 | 19348 | 19578 | 19976 | 19751 | 20665 | 20969 | 21098 | 20759 | 21520 | 21660 | 21950
8625 | 8625 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 9 | 15270 | 16205 | 16965 | 17308 | 17268 | 18062 | 18525 | 18843 | 19028 | 19536 | 19787 | 20106 | 20144 | 20745 | 21031 | 21144 | 21103 | 21549 | 21680 | 21969
8626 | 8626 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 10 | 15437 | 16321 | 17075 | 17414 | 17393 | 18185 | 18661 | 18992 | 19183 | 19703 | 19965 | 20299 | 20335 | 20961 | 21257 | 21378 | 21328 | 21800 | 21938 | 22231
8627 | 8627 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 11 | 15535 | 16481 | 17203 | 17494 | 17365 | 18197 | 18642 | 18948 | 19052 | 19611 | 19884 | 20231 | 20227 | 20916 | 21221 | 21350 | 21259 | 21787 | 21931 | 22228
8628 | 8628 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 12 | 15641 | 16502 | 17143 | 17380 | 17346 | 17985 | 18383 | 18652 | 18899 | 19248 | 19524 | 19875 | 20067 | 20566 | 20874 | 21004 | 21109 | 21446 | 21591 | 21888
8629 | 8629 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 13 | 15734 | 16644 | 17272 | 17493 | 17402 | 18070 | 18454 | 18711 | 18925 | 19286 | 19561 | 19911 | 20084 | 20599 | 20905 | 21034 | 21120 | 21473 | 21632 | 21917
8630 | 8630 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 14 | 15731 | 16686 | 17333 | 17548 | 17373 | 18108 | 18483 | 18730 | 18874 | 19286 | 19554 | 19896 | 20002 | 20567 | 20866 | 20990 | 21014 | 21420 | 21575 | 21858
8631 | 8631 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 15 | 15736 | 16735 | 17385 | 17610 | 17414 | 18184 | 18565 | 18816 | 18919 | 19377 | 19640 | 19974 | 20023 | 20633 | 20927 | 21046 | 21015 | 21470 | 21624 | 21905
8632 | 8632 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 16 | 16210 | 17132 | 17769 | 17975 | 17799 | 18506 | 18863 | 19093 | 19180 | 19608 | 19855 | 20171 | 20204 | 20799 | 21080 | 21189 | 21148 | 21596 | 21752 | 22030
8633 | 8633 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 17 | 17021 | 18129 | 18697 | 18989 | 18631 | 19440 | 19874 | 20106 | 19977 | 20638 | 20898 | 21225 | 21026 | 21865 | 22145 | 22267 | 21990 | 22672 | 22821 | 23106
8634 | 8634 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 18 | 17994 | 19093 | 19765 | 20099 | 19559 | 20549 | 20973 | 21227 | 20755 | 21837 | 22160 | 22459 | 22028 | 23199 | 23513 | 23660 | 23099 | 24091 | 24250 | 24544
8635 | 8635 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 19 | 17775 | 19009 | 19702 | 19981 | 19489 | 20540 | 20904 | 21272 | 20803 | 21921 | 22412 | 22785 | 22371 | 23655 | 24021 | 24207 | 23638 | 24684 | 24846 | 25143
8636 | 8636 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 20 | 17638 | 18815 | 19542 | 19863 | 19420 | 20492 | 20901 | 21251 | 21043 | 22137 | 22647 | 23187 | 22883 | 24205 | 24622 | 24854 | 24377 | 25399 | 25570 | 25871
8637 | 8637 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 21 | 17616 | 18633 | 19384 | 19744 | 19546 | 20471 | 20944 | 21371 | 21456 | 22443 | 23057 | 23700 | 23690 | 24883 | 25383 | 25678 | 25450 | 26307 | 26499 | 26811
8638 | 8638 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 22 | 17246 | 18113 | 18884 | 19276 | 19287 | 20094 | 20624 | 21115 | 21444 | 22314 | 22982 | 23685 | 23916 | 24988 | 25520 | 25851 | 25840 | 26537 | 26748 | 27066
8639 | 8639 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 23 | 16671 | 17413 | 18194 | 18639 | 18822 | 19513 | 20104 | 20642 | 21172 | 21943 | 22638 | 23373 | 23790 | 24725 | 25302 | 25641 | 25799 | 26358 | 26579 | 26901
8640 | 8640 | 360 | 12 | 26 | Winter | 12 | 25 | Winter | 24 | 15871 | 16537 | 17240 | 17722 | 18133 | 18799 | 19437 | 20022 | 20538 | 21408 | 22113 | 22845 | 23377 | 24113 | 24698 | 25171 | 25431 | 25915 | 26148 | 26346
8641 | 8641 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 1 | 14735 | 16198 | 16850 | 17326 | 17091 | 18359 | 18971 | 19518 | 19672 | 20871 | 21501 | 22206 | 22549 | 23406 | 23954 | 24411 | 24630 | 25120 | 25355 | 25517
8642 | 8642 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 2 | 14240 | 15731 | 16398 | 16865 | 16604 | 17942 | 18549 | 19121 | 19214 | 20456 | 21081 | 21764 | 22008 | 22923 | 23454 | 23896 | 24022 | 24585 | 24814 | 24971
8643 | 8643 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 3 | 14030 | 15493 | 16179 | 16662 | 16426 | 17775 | 18394 | 18975 | 19071 | 20305 | 20904 | 21559 | 21770 | 22670 | 23181 | 23610 | 23709 | 24276 | 24496 | 24649
8644 | 8644 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 4 | 13968 | 15379 | 16069 | 16544 | 16332 | 17626 | 18221 | 18765 | 18837 | 19991 | 20523 | 21113 | 21273 | 22108 | 22571 | 22961 | 23032 | 23572 | 23777 | 23921
8645 | 8645 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 5 | 14016 | 15473 | 16109 | 16569 | 16306 | 17605 | 18163 | 18657 | 18646 | 19750 | 20202 | 20759 | 20723 | 21617 | 22022 | 22364 | 22265 | 22907 | 23097 | 23236
8646 | 8646 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 6 | 14284 | 15909 | 16496 | 16946 | 16493 | 17925 | 18441 | 18919 | 18559 | 19815 | 20227 | 20707 | 20281 | 21417 | 21763 | 22055 | 21611 | 22529 | 22701 | 22839
8647 | 8647 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 7 | 14737 | 16675 | 17271 | 17639 | 16841 | 18592 | 19019 | 19482 | 18589 | 20179 | 20568 | 20921 | 20073 | 21502 | 21802 | 22057 | 21241 | 22481 | 22642 | 22776
8648 | 8648 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 8 | 15115 | 17734 | 18324 | 18517 | 17145 | 19423 | 19811 | 20311 | 18927 | 20826 | 21124 | 21432 | 20141 | 22061 | 22211 | 22444 | 21224 | 22838 | 23107 | 23245
8649 | 8649 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 9 | 15530 | 18208 | 18818 | 19057 | 17458 | 19939 | 20384 | 20819 | 19209 | 21354 | 21583 | 21878 | 20313 | 22483 | 22629 | 22858 | 21325 | 23246 | 23510 | 23656
8650 | 8650 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 10 | 15990 | 18305 | 18924 | 19174 | 17915 | 20088 | 20542 | 20986 | 19713 | 21548 | 21800 | 22116 | 20864 | 22756 | 22917 | 23157 | 21914 | 23556 | 23821 | 23969
8651 | 8651 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 11 | 16437 | 18452 | 19047 | 19264 | 18238 | 20135 | 20560 | 20981 | 19924 | 21511 | 21790 | 22131 | 21095 | 22809 | 22988 | 23241 | 22179 | 23654 | 23921 | 24074
8652 | 8652 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 12 | 16706 | 18508 | 19048 | 19208 | 18294 | 19972 | 20347 | 20728 | 19809 | 21190 | 21474 | 21819 | 20965 | 22501 | 22681 | 22936 | 22058 | 23351 | 23619 | 23772
8653 | 8653 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 13 | 16718 | 18484 | 18991 | 19134 | 18258 | 19876 | 20243 | 20617 | 19722 | 21055 | 21330 | 21670 | 20865 | 22346 | 22519 | 22771 | 21952 | 23195 | 23476 | 23629
8654 | 8654 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 14 | 16626 | 18428 | 18910 | 19035 | 18176 | 19737 | 20090 | 20451 | 19602 | 20858 | 21117 | 21442 | 20711 | 22094 | 22256 | 22500 | 21774 | 22915 | 23194 | 23345
8655 | 8655 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 15 | 16660 | 18409 | 18885 | 19011 | 18230 | 19697 | 20048 | 20408 | 19676 | 20808 | 21056 | 21368 | 20764 | 21999 | 22151 | 22387 | 21809 | 22792 | 23066 | 23214
8656 | 8656 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 16 | 16725 | 18587 | 19073 | 19237 | 18233 | 19891 | 20222 | 20589 | 19585 | 20996 | 21243 | 21549 | 20600 | 22180 | 22315 | 22540 | 21602 | 22925 | 23193 | 23337
8657 | 8657 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 17 | 17470 | 19146 | 19716 | 19879 | 19001 | 20515 | 20838 | 21203 | 20277 | 21616 | 21872 | 22104 | 21411 | 22742 | 22880 | 23107 | 22442 | 23494 | 23748 | 23893
8658 | 8658 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 18 | 18363 | 19911 | 20501 | 20638 | 19934 | 21220 | 21518 | 21794 | 21327 | 22304 | 22526 | 22874 | 22592 | 23559 | 23730 | 23986 | 23742 | 24382 | 24644 | 24793
8659 | 8659 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 19 | 18285 | 19745 | 20278 | 20512 | 19949 | 21047 | 21449 | 21758 | 21453 | 22382 | 22683 | 23103 | 23012 | 23912 | 24125 | 24429 | 24352 | 24874 | 25139 | 25297
8660 | 8660 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 20 | 17982 | 19547 | 20130 | 20321 | 19867 | 21008 | 21376 | 21821 | 21583 | 22523 | 22996 | 23504 | 23490 | 24464 | 24740 | 25092 | 25043 | 25602 | 25878 | 26044
8661 | 8661 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 21 | 17740 | 19357 | 19951 | 20178 | 19759 | 20958 | 21387 | 21907 | 21759 | 22787 | 23357 | 23961 | 24064 | 25091 | 25435 | 25836 | 25873 | 26434 | 26731 | 26906
8662 | 8662 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 22 | 17252 | 18745 | 19369 | 19628 | 19377 | 20488 | 20968 | 21544 | 21616 | 22548 | 23174 | 23839 | 24159 | 25082 | 25460 | 25895 | 26111 | 26544 | 26854 | 27035
8663 | 8663 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 23 | 16532 | 17839 | 18517 | 18806 | 18761 | 19745 | 20274 | 20900 | 21168 | 22000 | 22655 | 23334 | 23874 | 24644 | 25039 | 25503 | 25921 | 26182 | 26507 | 26700
8664 | 8664 | 361 | 12 | 27 | Winter | 12 | 26 | Winter | 24 | 15667 | 16637 | 17329 | 17782 | 17979 | 18800 | 19375 | 19903 | 20465 | 21228 | 21872 | 22581 | 23362 | 23796 | 24328 | 24804 | 25455 | 25505 | 25716 | 25920
8665 | 8665 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 1 | 15774 | 16006 | 16669 | 17080 | 18004 | 18066 | 18581 | 19074 | 20418 | 20232 | 20788 | 21396 | 23132 | 22430 | 22902 | 23304 | 25115 | 23929 | 24130 | 24303
8666 | 8666 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 2 | 15300 | 15543 | 16211 | 16651 | 17568 | 17655 | 18204 | 18708 | 20012 | 19876 | 20413 | 21003 | 22656 | 22005 | 22462 | 22853 | 24575 | 23462 | 23659 | 23828
8667 | 8667 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 3 | 15044 | 15313 | 16017 | 16481 | 17365 | 17529 | 18100 | 18616 | 19849 | 19793 | 20309 | 20879 | 22404 | 21844 | 22287 | 22664 | 24249 | 23257 | 23450 | 23618
8668 | 8668 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 4 | 14965 | 15223 | 15920 | 16378 | 17263 | 17414 | 17968 | 18458 | 19621 | 19554 | 20016 | 20534 | 21928 | 21405 | 21810 | 22155 | 23598 | 22704 | 22886 | 23046
8669 | 8669 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 5 | 15010 | 15276 | 15981 | 16433 | 17297 | 17442 | 17973 | 18470 | 19437 | 19419 | 19861 | 20272 | 21486 | 21033 | 21393 | 21700 | 22949 | 22197 | 22365 | 22517
8670 | 8670 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 6 | 15387 | 15645 | 16362 | 16862 | 17645 | 17795 | 18340 | 18800 | 19534 | 19625 | 20007 | 20298 | 21307 | 20942 | 21254 | 21521 | 22552 | 21963 | 22116 | 22261
8671 | 8671 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 7 | 16232 | 16528 | 17191 | 17746 | 18303 | 18593 | 19160 | 19529 | 20021 | 20315 | 20592 | 20875 | 21455 | 21430 | 21706 | 21942 | 22534 | 22342 | 22486 | 22626
8672 | 8672 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 8 | 17182 | 17707 | 18222 | 18722 | 19099 | 19588 | 20216 | 20560 | 20713 | 21161 | 21408 | 21715 | 22040 | 22222 | 22478 | 22696 | 22897 | 23201 | 23331 | 23347
8673 | 8673 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 9 | 17632 | 18125 | 18668 | 19108 | 19587 | 20016 | 20583 | 20916 | 21192 | 21486 | 21716 | 22007 | 22461 | 22490 | 22736 | 22945 | 23298 | 23438 | 23563 | 23577
8674 | 8674 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 10 | 17908 | 18417 | 18961 | 19398 | 19914 | 20298 | 20861 | 21193 | 21562 | 21771 | 22018 | 22321 | 22911 | 22826 | 23082 | 23299 | 23801 | 23797 | 23921 | 23937
8675 | 8675 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 11 | 17993 | 18545 | 19066 | 19455 | 19932 | 20269 | 20788 | 21084 | 21480 | 21613 | 21880 | 22198 | 22895 | 22727 | 22994 | 23221 | 23847 | 23726 | 23849 | 23866
8676 | 8676 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 12 | 17990 | 18586 | 19054 | 19390 | 19745 | 20105 | 20576 | 20834 | 21110 | 21295 | 21568 | 21891 | 22509 | 22424 | 22693 | 22921 | 23467 | 23429 | 23553 | 23570
8677 | 8677 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 13 | 17933 | 18510 | 18947 | 19267 | 19608 | 19961 | 20424 | 20675 | 20943 | 21112 | 21376 | 21695 | 22311 | 22220 | 22485 | 22713 | 23256 | 23222 | 23356 | 23368
8678 | 8678 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 14 | 17796 | 18399 | 18826 | 19138 | 19387 | 19818 | 20275 | 20520 | 20662 | 20938 | 21191 | 21500 | 21969 | 22010 | 22268 | 22491 | 22877 | 22995 | 23130 | 23142
8679 | 8679 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 15 | 17815 | 18397 | 18844 | 19165 | 19383 | 19856 | 20321 | 20568 | 20645 | 20989 | 21234 | 21536 | 21911 | 22031 | 22283 | 22502 | 22783 | 22999 | 23130 | 23139
8680 | 8680 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 16 | 18024 | 18537 | 18988 | 19294 | 19636 | 19949 | 20393 | 20619 | 20872 | 21002 | 21238 | 21528 | 22128 | 21999 | 22241 | 22452 | 22951 | 22937 | 23064 | 23073
8681 | 8681 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 17 | 18709 | 19159 | 19608 | 19913 | 20245 | 20563 | 21004 | 21153 | 21535 | 21621 | 21787 | 22164 | 22734 | 22645 | 22892 | 23107 | 23568 | 23597 | 23727 | 23739
8682 | 8682 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 18 | 19423 | 19920 | 20357 | 20550 | 21019 | 21229 | 21570 | 21786 | 22237 | 22187 | 22471 | 22881 | 23563 | 23418 | 23692 | 23929 | 24495 | 24444 | 24566 | 24592
8683 | 8683 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 19 | 19214 | 19569 | 20087 | 20290 | 20891 | 20987 | 21344 | 21585 | 22145 | 22078 | 22429 | 22820 | 23830 | 23459 | 23775 | 24047 | 24937 | 24592 | 24724 | 24754
8684 | 8684 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 20 | 19003 | 19370 | 19836 | 20148 | 20838 | 20824 | 21297 | 21583 | 22299 | 22205 | 22633 | 23097 | 24328 | 23861 | 24228 | 24542 | 25663 | 25129 | 25277 | 25305
8685 | 8685 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 21 | 18822 | 19120 | 19621 | 19962 | 20755 | 20718 | 21244 | 21591 | 22486 | 22361 | 22869 | 23413 | 24884 | 24315 | 24743 | 25105 | 26475 | 25756 | 25917 | 25952
8686 | 8686 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 22 | 18164 | 18543 | 19056 | 19427 | 20218 | 20253 | 20822 | 21216 | 22163 | 22088 | 22641 | 23234 | 24800 | 24221 | 24684 | 25071 | 26543 | 25771 | 25950 | 25983
8687 | 8687 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 23 | 17238 | 17694 | 18211 | 18610 | 19390 | 19500 | 20110 | 20529 | 21552 | 21496 | 22049 | 22682 | 24319 | 23715 | 24191 | 24591 | 26138 | 25314 | 25511 | 25540
8688 | 8688 | 362 | 12 | 28 | Winter | 12 | 27 | Winter | 24 | 16157 | 16592 | 17276 | 17691 | 18402 | 18668 | 19176 | 19652 | 20755 | 20800 | 21371 | 22014 | 23469 | 23068 | 23549 | 23959 | 25454 | 24576 | 24780 | 24944
8689 | 8689 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 1 | 14905 | 15860 | 16540 | 16979 | 17057 | 17980 | 18524 | 19019 | 19224 | 20178 | 20732 | 21359 | 21550 | 22392 | 22865 | 23266 | 23273 | 23889 | 24085 | 24265
8690 | 8690 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 2 | 14495 | 15340 | 16046 | 16492 | 16697 | 17524 | 18083 | 18587 | 18898 | 19754 | 20284 | 20876 | 21188 | 21874 | 22331 | 22720 | 22860 | 23333 | 23531 | 23705
8691 | 8691 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 3 | 14268 | 15108 | 15842 | 16307 | 16560 | 17374 | 17951 | 18466 | 18821 | 19638 | 20144 | 20711 | 21051 | 21669 | 22110 | 22485 | 22667 | 23081 | 23276 | 23447
8692 | 8692 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 4 | 14151 | 15015 | 15748 | 16206 | 16418 | 17251 | 17809 | 18296 | 18593 | 19385 | 19838 | 20353 | 20623 | 21217 | 21619 | 21962 | 22098 | 22514 | 22698 | 22862
8693 | 8693 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 5 | 14239 | 15052 | 15762 | 16253 | 16450 | 17208 | 17778 | 18177 | 18504 | 19205 | 19552 | 20005 | 20294 | 20757 | 21116 | 21421 | 21603 | 21919 | 22086 | 22242
8694 | 8694 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 6 | 14680 | 15377 | 16113 | 16586 | 16846 | 17470 | 18007 | 18291 | 18760 | 19235 | 19464 | 19851 | 20290 | 20480 | 20796 | 21066 | 21424 | 21509 | 21661 | 21811
8695 | 8695 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 7 | 15473 | 16257 | 17029 | 17429 | 17658 | 18348 | 18810 | 19090 | 19404 | 19886 | 20112 | 20408 | 20774 | 20953 | 21245 | 21493 | 21777 | 21906 | 22052 | 22206
8696 | 8696 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 8 | 16630 | 17574 | 18335 | 18735 | 18701 | 19812 | 20279 | 20469 | 20352 | 21169 | 21421 | 21819 | 21742 | 22205 | 22489 | 22729 | 22548 | 23262 | 23281 | 23439
8697 | 8697 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 9 | 17036 | 18257 | 18971 | 19366 | 19055 | 20489 | 20970 | 21162 | 20718 | 21837 | 22067 | 22506 | 21992 | 22873 | 23153 | 23388 | 22763 | 23925 | 23951 | 24115
8698 | 8698 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 10 | 17122 | 18425 | 19130 | 19511 | 19142 | 20633 | 21120 | 21318 | 20793 | 21998 | 22235 | 22683 | 22115 | 23067 | 23355 | 23598 | 22919 | 24149 | 24183 | 24350
8699 | 8699 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 11 | 17170 | 18466 | 19111 | 19440 | 19077 | 20480 | 20930 | 21098 | 20570 | 21720 | 21962 | 22419 | 21925 | 22819 | 23113 | 23360 | 22770 | 23924 | 23962 | 24132
8700 | 8700 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 12 | 17097 | 18401 | 19005 | 19273 | 18835 | 20201 | 20602 | 20726 | 20152 | 21270 | 21512 | 21968 | 21495 | 22362 | 22654 | 22899 | 22346 | 23456 | 23490 | 23656
8701 | 8701 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 13 | 17044 | 18296 | 18885 | 19140 | 18704 | 20039 | 20425 | 20537 | 19993 | 21058 | 21299 | 21753 | 21305 | 22141 | 22429 | 22672 | 22145 | 23225 | 23256 | 23420
8702 | 8702 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 14 | 17090 | 18267 | 18851 | 19102 | 18707 | 19987 | 20365 | 20471 | 19970 | 20976 | 21211 | 21659 | 21243 | 22034 | 22316 | 22555 | 22059 | 23100 | 23129 | 23291
8703 | 8703 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 15 | 17077 | 18210 | 18792 | 19053 | 18738 | 19951 | 20336 | 20446 | 20021 | 20958 | 21188 | 21629 | 21271 | 21991 | 22269 | 22504 | 22064 | 23044 | 23071 | 23231
8704 | 8704 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 16 | 17344 | 18308 | 18886 | 19130 | 18981 | 19990 | 20355 | 20448 | 20180 | 20923 | 21143 | 21571 | 21378 | 21910 | 22179 | 22407 | 22137 | 22937 | 22964 | 23125
8705 | 8705 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 17 | 17992 | 19021 | 19594 | 19770 | 19705 | 20710 | 20993 | 21168 | 20896 | 21580 | 21891 | 22329 | 22121 | 22683 | 22957 | 23189 | 22899 | 23725 | 23754 | 23918
8706 | 8706 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 18 | 18795 | 20126 | 20664 | 20957 | 20438 | 21818 | 22168 | 22361 | 21557 | 22846 | 23216 | 23701 | 22899 | 24155 | 24456 | 24710 | 23772 | 25264 | 25306 | 25475
8707 | 8707 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 19 | 18532 | 19905 | 20441 | 20742 | 20125 | 21597 | 21953 | 22088 | 21402 | 22735 | 23091 | 23708 | 22896 | 24252 | 24588 | 24871 | 23924 | 25441 | 25469 | 25639
8708 | 8708 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 20 | 18321 | 19505 | 20126 | 20450 | 20026 | 21322 | 21699 | 21870 | 21389 | 22627 | 23053 | 23652 | 23249 | 24302 | 24679 | 24996 | 24460 | 25604 | 25623 | 25804
8709 | 8709 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 21 | 18046 | 19191 | 19816 | 20161 | 19876 | 21080 | 21495 | 21718 | 21465 | 22608 | 23108 | 23780 | 23638 | 24558 | 24985 | 25343 | 25059 | 26011 | 26047 | 26231
8710 | 8710 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 22 | 17483 | 18698 | 19329 | 19692 | 19399 | 20650 | 21099 | 21363 | 21172 | 22338 | 22873 | 23586 | 23537 | 24432 | 24885 | 25263 | 25082 | 25976 | 26014 | 26203
8711 | 8711 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 23 | 16594 | 17946 | 18601 | 18972 | 18580 | 19995 | 20457 | 20774 | 20520 | 21804 | 22376 | 23107 | 22984 | 23987 | 24455 | 24847 | 24587 | 25579 | 25619 | 25801
8712 | 8712 | 363 | 12 | 29 | Winter | 12 | 28 | Winter | 24 | 15500 | 16931 | 17586 | 18004 | 17721 | 18938 | 19451 | 19933 | 19831 | 21024 | 21598 | 22207 | 22218 | 23230 | 23701 | 24099 | 23976 | 24716 | 24896 | 25079
8713 | 8713 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 1 | 15137 | 16394 | 17092 | 17536 | 17401 | 18552 | 19127 | 19677 | 19560 | 20924 | 21553 | 22204 | 21924 | 23346 | 23862 | 24296 | 23647 | 24976 | 25188 | 25363
8714 | 8714 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 2 | 14604 | 15867 | 16552 | 17002 | 16877 | 18046 | 18632 | 19176 | 19102 | 20440 | 21029 | 21676 | 21385 | 22778 | 23277 | 23699 | 23052 | 24365 | 24575 | 24742
8715 | 8715 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 3 | 14385 | 15577 | 16283 | 16752 | 16720 | 17832 | 18435 | 18986 | 18999 | 20253 | 20812 | 21436 | 21208 | 22492 | 22973 | 23382 | 22815 | 24028 | 24233 | 24401
8716 | 8716 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 4 | 14302 | 15431 | 16140 | 16603 | 16614 | 17663 | 18244 | 18764 | 18796 | 19936 | 20435 | 20999 | 20805 | 21948 | 22386 | 22759 | 22270 | 23355 | 23550 | 23707
8717 | 8717 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 5 | 14372 | 15335 | 16090 | 16497 | 16617 | 17555 | 18056 | 18527 | 18646 | 19577 | 20007 | 20500 | 20417 | 21323 | 21710 | 22041 | 21718 | 22573 | 22750 | 22903
8718 | 8718 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 6 | 14690 | 15443 | 16200 | 16529 | 16850 | 17578 | 17982 | 18384 | 18718 | 19282 | 19637 | 20100 | 20180 | 20782 | 21120 | 21408 | 21321 | 21878 | 22036 | 22182
8719 | 8719 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 7 | 15638 | 15899 | 16609 | 16960 | 17705 | 17945 | 18369 | 18672 | 19494 | 19497 | 19752 | 20213 | 20714 | 20797 | 21104 | 21366 | 21761 | 21797 | 21947 | 22095
8720 | 8720 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 8 | 17031 | 16569 | 17274 | 17675 | 19034 | 18762 | 19113 | 19389 | 20769 | 20169 | 20511 | 20904 | 21951 | 21319 | 21615 | 21865 | 23093 | 22284 | 22433 | 22584
8721 | 8721 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 9 | 17610 | 17237 | 17935 | 18324 | 19687 | 19439 | 19799 | 20121 | 21404 | 20809 | 21176 | 21497 | 22583 | 21878 | 22164 | 22404 | 23706 | 22814 | 22962 | 23107
8722 | 8722 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 10 | 17710 | 17535 | 18211 | 18585 | 19752 | 19693 | 20058 | 20386 | 21487 | 21081 | 21454 | 21785 | 22695 | 22185 | 22479 | 22726 | 23847 | 23152 | 23307 | 23456
8723 | 8723 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 11 | 17668 | 17605 | 18226 | 18542 | 19531 | 19559 | 19886 | 20185 | 21130 | 20821 | 21200 | 21540 | 22338 | 21957 | 22257 | 22510 | 23515 | 22949 | 23109 | 23260
8724 | 8724 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 12 | 17672 | 17603 | 18163 | 18417 | 19354 | 19324 | 19601 | 19859 | 20761 | 20423 | 20805 | 21145 | 21936 | 21563 | 21863 | 22116 | 23101 | 22555 | 22716 | 22880
8725 | 8725 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 13 | 17635 | 17565 | 18102 | 18340 | 19277 | 19211 | 19471 | 19716 | 20630 | 20256 | 20636 | 20973 | 21789 | 21383 | 21680 | 21930 | 22944 | 22365 | 22523 | 22685
8726 | 8726 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 14 | 17740 | 17558 | 18096 | 18326 | 19371 | 19178 | 19429 | 19665 | 20695 | 20185 | 20557 | 20887 | 21826 | 21281 | 21570 | 21815 | 22961 | 22240 | 22395 | 22554
8727 | 8727 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 15 | 17741 | 17541 | 18093 | 18333 | 19385 | 19198 | 19455 | 19695 | 20730 | 20221 | 20588 | 20911 | 21844 | 21291 | 21575 | 21816 | 22962 | 22235 | 22388 | 22546
8728 | 8728 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 16 | 17726 | 17657 | 18189 | 18416 | 19327 | 19244 | 19479 | 19700 | 20593 | 20186 | 20540 | 20848 | 21653 | 21201 | 21475 | 21707 | 22740 | 22115 | 22268 | 22427
8729 | 8729 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 17 | 18441 | 18507 | 18979 | 19295 | 20057 | 20046 | 20360 | 20585 | 21328 | 21088 | 21456 | 21774 | 22424 | 22144 | 22423 | 22661 | 23533 | 23076 | 23233 | 23395
8730 | 8730 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 18 | 19517 | 19493 | 20085 | 20439 | 21264 | 21187 | 21490 | 21734 | 22485 | 22310 | 22737 | 23028 | 23859 | 23494 | 23800 | 24062 | 25074 | 24500 | 24655 | 24821
8731 | 8731 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 19 | 19250 | 19274 | 19868 | 20164 | 21082 | 21015 | 21255 | 21609 | 22344 | 22218 | 22803 | 23161 | 23930 | 23744 | 24097 | 24397 | 25271 | 24866 | 25018 | 25199
8732 | 8732 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 20 | 18914 | 18786 | 19389 | 19713 | 20718 | 20597 | 20867 | 21189 | 22169 | 22009 | 22596 | 23106 | 23923 | 23816 | 24218 | 24560 | 25414 | 25072 | 25232 | 25406
8733 | 8733 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 21 | 18584 | 18462 | 19090 | 19441 | 20445 | 20391 | 20709 | 21095 | 22075 | 22074 | 22750 | 23347 | 24113 | 24210 | 24673 | 25063 | 25791 | 25649 | 25826 | 26008
8734 | 8734 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 22 | 18038 | 18077 | 18697 | 19070 | 19937 | 20074 | 20434 | 20870 | 21714 | 21953 | 22673 | 23318 | 23905 | 24269 | 24763 | 25185 | 25680 | 25811 | 26015 | 26192
8735 | 8735 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 23 | 17373 | 17513 | 18152 | 18576 | 19343 | 19620 | 20034 | 20512 | 21252 | 21680 | 22426 | 23098 | 23537 | 24100 | 24612 | 25054 | 25361 | 25700 | 25913 | 26092
8736 | 8736 | 364 | 12 | 30 | Winter | 12 | 29 | Winter | 24 | 16193 | 16769 | 17443 | 17901 | 18365 | 18879 | 19460 | 19978 | 20401 | 21220 | 21845 | 22507 | 22742 | 23661 | 24184 | 24629 | 24460 | 25298 | 25518 | 25696
8737 | 8737 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 1 | 15730 | 15925 | 16652 | 17143 | 17968 | 18237 | 18872 | 19426 | 20276 | 20792 | 21425 | 22137 | 22854 | 23349 | 23896 | 24358 | 24741 | 25070 | 25291 | 25480
8738 | 8738 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 2 | 15210 | 15433 | 16166 | 16649 | 17460 | 17788 | 18417 | 18998 | 19807 | 20345 | 20970 | 21660 | 22312 | 22830 | 23359 | 23807 | 24136 | 24506 | 24723 | 24909
8739 | 8739 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 3 | 14914 | 15155 | 15912 | 16414 | 17221 | 17592 | 18234 | 18824 | 19615 | 20168 | 20766 | 21429 | 22038 | 22552 | 23062 | 23494 | 23792 | 24172 | 24385 | 24568
8740 | 8740 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 4 | 14783 | 14963 | 15725 | 16221 | 17074 | 17371 | 17990 | 18543 | 19361 | 19785 | 20317 | 20916 | 21556 | 21926 | 22389 | 22782 | 23150 | 23406 | 23607 | 23782
8741 | 8741 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 5 | 14662 | 14847 | 15549 | 16029 | 16920 | 17123 | 17700 | 18198 | 19083 | 19307 | 19764 | 20331 | 20962 | 21205 | 21614 | 21961 | 22370 | 22517 | 22701 | 22867
8742 | 8742 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 6 | 14747 | 14747 | 15383 | 15829 | 16985 | 16839 | 17361 | 17825 | 18933 | 18722 | 19143 | 19635 | 20504 | 20361 | 20717 | 21019 | 21725 | 21507 | 21670 | 21828
8743 | 8743 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 7 | 15131 | 14749 | 15391 | 15750 | 17394 | 16718 | 17143 | 17588 | 19141 | 18288 | 18696 | 19067 | 20544 | 19675 | 19992 | 20261 | 21649 | 20701 | 20851 | 21007
8744 | 8744 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 8 | 15849 | 15234 | 15915 | 16255 | 18196 | 17217 | 17621 | 17992 | 19792 | 18794 | 19121 | 19333 | 21092 | 19880 | 20177 | 20555 | 22277 | 20844 | 20988 | 21143
8745 | 8745 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 9 | 16593 | 15849 | 16512 | 16888 | 18873 | 17799 | 18256 | 18563 | 20476 | 19367 | 19609 | 19795 | 21691 | 20293 | 20572 | 20934 | 22832 | 21206 | 21347 | 21497
8746 | 8746 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 10 | 16832 | 16227 | 16894 | 17265 | 19055 | 18193 | 18662 | 18981 | 20670 | 19801 | 20054 | 20254 | 21917 | 20774 | 21062 | 21432 | 23089 | 21719 | 21866 | 22021
8747 | 8747 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 11 | 16816 | 16447 | 17055 | 17376 | 18858 | 18234 | 18671 | 18965 | 20332 | 19735 | 19996 | 20209 | 21581 | 20749 | 21045 | 21422 | 22778 | 21723 | 21876 | 22033
8748 | 8748 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 12 | 16806 | 16549 | 17117 | 17381 | 18646 | 18142 | 18532 | 18788 | 19932 | 19490 | 19755 | 19972 | 21156 | 20519 | 20817 | 21197 | 22353 | 21503 | 21657 | 21815
8749 | 8749 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 13 | 16743 | 16517 | 17049 | 17301 | 18517 | 18032 | 18408 | 18652 | 19742 | 19332 | 19597 | 19812 | 20946 | 20354 | 20651 | 21029 | 22131 | 21332 | 21486 | 21642
8750 | 8750 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 14 | 16678 | 16465 | 16988 | 17234 | 18435 | 17949 | 18315 | 18550 | 19621 | 19211 | 19468 | 19674 | 20792 | 20200 | 20490 | 20862 | 21951 | 21156 | 21306 | 21460
8751 | 8751 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 15 | 16689 | 16577 | 17128 | 17386 | 18482 | 18115 | 18488 | 18727 | 19688 | 19394 | 19646 | 19846 | 20839 | 20360 | 20645 | 21013 | 21980 | 21301 | 21449 | 21602
8752 | 8752 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 16 | 16951 | 16917 | 17461 | 17702 | 18686 | 18392 | 18743 | 18962 | 19809 | 19588 | 19826 | 20011 | 20897 | 20498 | 20772 | 21132 | 22002 | 21410 | 21558 | 21706
8753 | 8753 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 17 | 17844 | 17865 | 18506 | 18756 | 19625 | 19445 | 19793 | 20016 | 20676 | 20658 | 20910 | 21026 | 21885 | 21533 | 21813 | 22173 | 23008 | 22462 | 22617 | 22762
8754 | 8754 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 18 | 18919 | 19056 | 19717 | 20003 | 20752 | 20683 | 21020 | 21184 | 21913 | 21978 | 22212 | 22459 | 23242 | 23059 | 23371 | 23752 | 24466 | 24062 | 24217 | 24374
8755 | 8755 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 19 | 18687 | 18938 | 19547 | 19929 | 20572 | 20551 | 20985 | 21182 | 21827 | 22092 | 22408 | 22726 | 23422 | 23450 | 23811 | 24234 | 24817 | 24584 | 24742 | 24903
8756 | 8756 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 20 | 18105 | 18474 | 19099 | 19442 | 20140 | 20210 | 20606 | 20938 | 21544 | 21924 | 22409 | 22804 | 23433 | 23674 | 24088 | 24558 | 25008 | 24963 | 25129 | 25303
8757 | 8757 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 21 | 17762 | 18104 | 18773 | 19151 | 19898 | 20010 | 20466 | 20872 | 21524 | 22033 | 22614 | 23105 | 23754 | 24144 | 24624 | 25151 | 25554 | 25633 | 25818 | 25987
8758 | 8758 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 22 | 17411 | 17717 | 18390 | 18803 | 19585 | 19753 | 20264 | 20730 | 21392 | 22013 | 22644 | 23192 | 23813 | 24333 | 24856 | 25413 | 25738 | 25950 | 26144 | 26328
8759 | 8759 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 23 | 16789 | 17286 | 18015 | 18461 | 19073 | 19482 | 20035 | 20546 | 21019 | 21921 | 22581 | 23144 | 23580 | 24338 | 24883 | 25444 | 25574 | 26021 | 26226 | 26412
8760 | 8760 | 365 | 12 | 31 | Winter | 12 | 30 | Winter | 24 | 16107 | 17005 | 17756 | 18238 | 18314 | 19334 | 19932 | 20472 | 20565 | 21817 | 22467 | 23185 | 23168 | 24408 | 24958 | 25423 | 25069 | 26139 | 26360 | 26542
8761 | 8761 | 366 |  |  |  | 12 | 31 | Winter | 1 | Year 1 2024: 15217; Year 5 2028: 17598; Year 9 2032: 20076; Year 13 2036: 22817; Year 17 2040: 24806
8762 | 8762 | 366 |  |  |  | 12 | 31 | Winter | 2 | Year 1 2024: 14740; Year 5 2028: 17148; Year 9 2032: 19663; Year 13 2036: 22328; Year 17 2040: 24256
8763 | 8763 | 366 |  |  |  | 12 | 31 | Winter | 3 | Year 1 2024: 14491; Year 5 2028: 16966; Year 9 2032: 19528; Year 13 2036: 22105; Year 17 2040: 23962
8764 | 8764 | 366 |  |  |  | 12 | 31 | Winter | 4 | Year 1 2024: 14287; Year 5 2028: 16745; Year 9 2032: 19185; Year 13 2036: 21517; Year 17 2040: 23202
8765 | 8765 | 366 |  |  |  | 12 | 31 | Winter | 5 | Year 1 2024: 14150; Year 5 2028: 16585; Year 9 2032: 18788; Year 13 2036: 20872; Year 17 2040: 22356
8766 | 8766 | 366 |  |  |  | 12 | 31 | Winter | 6 | Year 1 2024: 14026; Year 5 2028: 16369; Year 9 2032: 18258; Year 13 2036: 20067; Year 17 2040: 21353
8767 | 8767 | 366 |  |  |  | 12 | 31 | Winter | 7 | Year 1 2024: 14093; Year 5 2028: 16233; Year 9 2032: 17924; Year 13 2036: 19419; Year 17 2040: 20559
8768 | 8768 | 366 |  |  |  | 12 | 31 | Winter | 8 | Year 1 2024: 14608; Year 5 2028: 16835; Year 9 2032: 18371; Year 13 2036: 19679; Year 17 2040: 20739
8769 | 8769 | 366 |  |  |  | 12 | 31 | Winter | 9 | Year 1 2024: 15283; Year 5 2028: 17464; Year 9 2032: 18972; Year 13 2036: 20171; Year 17 2040: 21162
8770 | 8770 | 366 |  |  |  | 12 | 31 | Winter | 10 | Year 1 2024: 16001; Year 5 2028: 18189; Year 9 2032: 19742; Year 13 2036: 20987; Year 17 2040: 22012
8771 | 8771 | 366 |  |  |  | 12 | 31 | Winter | 11 | Year 1 2024: 16495; Year 5 2028: 18517; Year 9 2032: 19954; Year 13 2036: 21213; Year 17 2040: 22269
8772 | 8772 | 366 |  |  |  | 12 | 31 | Winter | 12 | Year 1 2024: 16699; Year 5 2028: 18561; Year 9 2032: 19826; Year 13 2036: 21072; Year 17 2040: 22137
8773 | 8773 | 366 |  |  |  | 12 | 31 | Winter | 13 | Year 1 2024: 16607; Year 5 2028: 18396; Year 9 2032: 19609; Year 13 2036: 20840; Year 17 2040: 21899
8774 | 8774 | 366 |  |  |  | 12 | 31 | Winter | 14 | Year 1 2024: 16349; Year 5 2028: 18112; Year 9 2032: 19288; Year 13 2036: 20484; Year 17 2040: 21519
8775 | 8775 | 366 |  |  |  | 12 | 31 | Winter | 15 | Year 1 2024: 16355; Year 5 2028: 18173; Year 9 2032: 19371; Year 13 2036: 20548; Year 17 2040: 21566
8776 | 8776 | 366 |  |  |  | 12 | 31 | Winter | 16 | Year 1 2024: 16559; Year 5 2028: 18329; Year 9 2032: 19440; Year 13 2036: 20552; Year 17 2040: 21534
8777 | 8777 | 366 |  |  |  | 12 | 31 | Winter | 17 | Year 1 2024: 17434; Year 5 2028: 19168; Year 9 2032: 20361; Year 13 2036: 21434; Year 17 2040: 22445
8778 | 8778 | 366 |  |  |  | 12 | 31 | Winter | 18 | Year 1 2024: 18452; Year 5 2028: 20358; Year 9 2032: 21578; Year 13 2036: 22856; Year 17 2040: 23982
8779 | 8779 | 366 |  |  |  | 12 | 31 | Winter | 19 | Year 1 2024: 18335; Year 5 2028: 20318; Year 9 2032: 21556; Year 13 2036: 23194; Year 17 2040: 24498
8780 | 8780 | 366 |  |  |  | 12 | 31 | Winter | 20 | Year 1 2024: 17832; Year 5 2028: 19931; Year 9 2032: 21367; Year 13 2036: 23334; Year 17 2040: 24829
8781 | 8781 | 366 |  |  |  | 12 | 31 | Winter | 21 | Year 1 2024: 17435; Year 5 2028: 19686; Year 9 2032: 21388; Year 13 2036: 23729; Year 17 2040: 25471
8782 | 8782 | 366 |  |  |  | 12 | 31 | Winter | 22 | Year 1 2024: 16991; Year 5 2028: 19340; Year 9 2032: 21276; Year 13 2036: 23839; Year 17 2040: 25724
8783 | 8783 | 366 |  |  |  | 12 | 31 | Winter | 23 | Year 1 2024: 16567; Year 5 2028: 19013; Year 9 2032: 21143; Year 13 2036: 23823; Year 17 2040: 25785
8784 | 8784 | 366 |  |  |  | 12 | 31 | Winter | 24 | Year 1 2024: 16256; Year 5 2028: 18679; Year 9 2032: 21121; Year 13 2036: 23870; Year 17 2040: 25873

## Census data (hidden)
Census Profile, 2021 Census of Population
|  |  | Ontario [Province] | Hamilton--Niagara Peninsula [Economic region], Ontario | Kitchener--Waterloo--Barrie [Economic region], Ontario | Muskoka--Kawarthas [Economic region], Ontario | Stratford--Bruce Peninsula [Economic region], Ontario | Toronto [Economic region], Ontario | Kingston--Pembroke [Economic region], Ontario | Ottawa [Economic region], Ontario | London [Economic region], Ontario | Windsor--Sarnia [Economic region], Ontario | Northeast [Economic region], Ontario | Northwest [Economic region], Ontario
|  |  | Counts | Counts | Counts | Counts | Counts | Counts | Counts | Counts | Counts | Counts | Counts | Counts
Topic | Characteristic | Note | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total | Total
Population and dwellings | Population, 2021 | 1 | 14223942 | 1495885 | 1427617 | 403538 | 317232 | 6525393 | 484777 | 1407555 | 717096 | 655330 | 557220 | 232299
Population and dwellings | Population, 2016 | 1 | 13448494 | 1412714 | 1299250 | 377933 | 298086 | 6234202 | 456937 | 1306249 | 655350 | 627633 | 548449 | 231691
Population and dwellings | Population percentage change, 2016 to 2021 |  | 5.8 | 5.9 | 9.9 | 6.8 | 6.4 | 4.7 | 6.1 | 7.8 | 9.4 | 4.4 | 1.6 | 0.3
Population and dwellings | Total private dwellings | 2 | 5929250 | 625484 | 580015 | 221262 | 156292 | 2517061 | 233529 | 602529 | 305070 | 281689 | 290216 | 116103
Population and dwellings | Private dwellings occupied by usual residents | 3 | 5491201 | 594468 | 540382 | 170062 | 131527 | 2381141 | 205300 | 570809 | 289311 | 265170 | 245297 | 97734
Population and dwellings | Population density per square kilometre |  | 15.9 | 209.7 | 138.1 | 24.4 | 22.4 | 940.6 | 23.1 | 97.5 | 99.1 | 89.7 | 2 | 0.5
Population and dwellings | Land area in square kilometres |  | 892411.76 | 7135.15 | 10341.13 | 16569.47 | 14190.67 | 6937.51 | 20942.44 | 14443.63 | 7234.51 | 7308.66 | 273580.09 | 513728.5
Household and dwelling characteristics | Total - Occupied private dwellings by structural type of dwelling - 100% data |  | 5491200 | 594470 | 540385 | 170060 | 131530 | 2381140 | 205300 | 570810 | 289315 | 265170 | 245300 | 97735
| Total single detached, attached, row |  | 3751515 | 454795 | 417990 | 143880 | 111360 | 1352910 | 162175 | 413515 | 212335 | 214720 | 188675 | 79155
Household and dwelling characteristics | Single-detached house |  | 2942990 | 367540 | 340700 | 134410 | 101040 | 961005 | 143280 | 289230 | 172965 | 190960 | 168445 | 73415
Household and dwelling characteristics | Semi-detached house |  | 303260 | 24300 | 25735 | 2890 | 4420 | 169280 | 9100 | 31185 | 10995 | 10465 | 11575 | 3305
Household and dwelling characteristics | Row house |  | 505265 | 62955 | 51555 | 6580 | 5900 | 222625 | 9795 | 93100 | 28375 | 13295 | 8655 | 2435
% |  |  | 100% | 12.12% | 11.14% | 3.835% | 2.968% | 36.06% | 4.323% | 11.02% | 5.66% | 5.724% | 5.029% | 2.11%
Household and dwelling characteristics | Apartment or flat in a duplex |  | 181030 | 17455 | 18775 | 4870 | 2060 | 94550 | 4375 | 12360 | 6310 | 6315 | 10835 | 3130
Household and dwelling characteristics | Apartment in a building that has fewer than five storeys |  | 548785 | 54805 | 58635 | 15440 | 14325 | 224115 | 24200 | 62360 | 28515 | 23025 | 32425 | 10940
Household and dwelling characteristics | Apartment in a building that has five or more storeys |  | 984665 | 65060 | 42625 | 4460 | 1770 | 705300 | 12595 | 79285 | 40655 | 19645 | 10485 | 2780
Household and dwelling characteristics | Other single-attached house |  | 10220 | 1350 | 980 | 490 | 390 | 3615 | 555 | 1070 | 390 | 420 | 695 | 270
Household and dwelling characteristics | Movable dwelling | 4 | 14985 | 995 | 1385 | 920 | 1625 | 655 | 1390 | 2220 | 1100 | 1040 | 2185 | 1465
Household and dwelling characteristics | Total - Private households by household size - 100% data |  | 5491205 | 594465 | 540380 | 170060 | 131525 | 2381140 | 205300 | 570810 | 289310 | 265170 | 245295 | 97735
Household and dwelling characteristics | 1 person |  | 1452540 | 161655 | 128470 | 46565 | 37165 | 591990 | 59215 | 160905 | 81710 | 76535 | 77585 | 30745
Household and dwelling characteristics | 2 persons |  | 1798040 | 204980 | 183735 | 69930 | 52320 | 681340 | 80825 | 201145 | 101175 | 93410 | 94160 | 35030
Household and dwelling characteristics | 3 persons |  | 872480 | 92215 | 87850 | 23365 | 16545 | 412010 | 28605 | 84540 | 42730 | 37840 | 33405 | 13380
Household and dwelling characteristics | 4 persons |  | 825445 | 84400 | 86270 | 19165 | 14990 | 407515 | 23455 | 78685 | 38810 | 34310 | 26745 | 11105
Household and dwelling characteristics | 5 or more persons |  | 542700 | 51225 | 54055 | 11045 | 10515 | 288280 | 13200 | 45540 | 24880 | 23075 | 13410 | 7480
Household and dwelling characteristics | Number of persons in private households |  | 14031750 | 1471795 | 1407880 | 394185 | 311635 | 6463150 | 473320 | 1383540 | 707140 | 643865 | 546710 | 228535
Household and dwelling characteristics | Average household size |  | 2.6 | 2.5 | 2.6 | 2.3 | 2.4 | 2.7 | 2.3 | 2.4 | 2.4 | 2.4 | 2.2 | 2.3
Household characteristics | Total - Private households by tenure - 25% sample data | 50 | 5491200 | 594470 | 540380 | 170060 | 131530 | 2381140 | 205300 | 570810 | 289310 | 265170 | 245300 | 97735
Household characteristics | Owner |  | 3755720 | 422220 | 388300 | 133980 | 101610 | 1559830 | 144935 | 384040 | 189880 | 193000 | 170725 | 67200
Household characteristics | Renter |  | 1724970 | 172180 | 151850 | 35890 | 29715 | 821265 | 60070 | 186770 | 99395 | 71885 | 71920 | 24035
Household characteristics | Dwelling provided by the local government, First Nation or Indian band |  | 10510 | 65 | 230 | 195 | 205 | 50 | 290 | 0 | 35 | 285 | 2650 | 6500
Household characteristics | Total - Occupied private dwellings by condominium status - 25% sample data | 51 | 5491200 | 594470 | 540380 | 170060 | 131530 | 2381140 | 205300 | 570810 | 289310 | 265170 | 245300 | 97735
Household characteristics | Condominium |  | 822780 | 64560 | 60785 | 6675 | 6180 | 547225 | 7620 | 72320 | 33610 | 14665 | 6070 | 3055
Household characteristics | Not condominium |  | 4668425 | 529910 | 479595 | 163385 | 125345 | 1833915 | 197685 | 498490 | 255700 | 250505 | 239225 | 94675
Household characteristics | Total - Occupied private dwellings by number of bedrooms - 25% sample data | 52 | 5491200 | 594470 | 540380 | 170060 | 131530 | 2381140 | 205300 | 570810 | 289310 | 265170 | 245300 | 97735
Household characteristics | No bedrooms |  | 48740 | 2860 | 2080 | 595 | 390 | 33795 | 825 | 4305 | 1320 | 1160 | 1085 | 325
Household characteristics | 1 bedroom |  | 769570 | 68330 | 50750 | 14160 | 10440 | 430310 | 20710 | 73290 | 35710 | 26940 | 28505 | 10440
Household characteristics | 2 bedrooms |  | 1205540 | 128740 | 109105 | 39115 | 29615 | 509805 | 49705 | 126155 | 67455 | 60115 | 61465 | 24260
Household characteristics | 3 bedrooms |  | 1918935 | 242355 | 220975 | 68730 | 52820 | 679440 | 80415 | 220445 | 110005 | 108690 | 96710 | 38360
Household characteristics | 4 or more bedrooms |  | 1548420 | 152190 | 157480 | 47460 | 38260 | 727785 | 53650 | 146610 | 74825 | 68275 | 57530 | 24345
Household characteristics | Total - Occupied private dwellings by number of rooms - 25% sample data | 53 | 5491200 | 594470 | 540380 | 170060 | 131530 | 2381140 | 205300 | 570810 | 289310 | 265170 | 245300 | 97735
Household characteristics | 1 to 4 rooms |  | 1579320 | 132885 | 116215 | 30455 | 21920 | 882400 | 43935 | 148295 | 68620 | 52260 | 59500 | 22840
Household characteristics | 5 rooms |  | 775580 | 84905 | 78265 | 25070 | 17275 | 325065 | 30125 | 80160 | 38565 | 37510 | 41070 | 17575
Household characteristics | 6 rooms |  | 791100 | 93535 | 87170 | 28695 | 21515 | 301940 | 32515 | 85320 | 43060 | 40640 | 40005 | 16710
Household characteristics | 7 rooms |  | 708205 | 85865 | 75940 | 26385 | 20380 | 262515 | 30170 | 79935 | 39780 | 39445 | 34030 | 13760
Household characteristics | 8 or more rooms |  | 1636990 | 197280 | 182790 | 59465 | 50440 | 609210 | 68550 | 177095 | 99295 | 95310 | 70695 | 26850
Household characteristics | Average number of rooms per dwelling |  | 6.2 | 6.5 | 6.6 | 6.7 | 6.9 | 5.8 | 6.6 | 6.4 | 6.6 | 6.7 | 6.3 | 6.3
Household characteristics | Total - Private households by number of persons per room - 25% sample data | 54 | 5491200 | 594470 | 540380 | 170060 | 131530 | 2381140 | 205300 | 570810 | 289310 | 265170 | 245300 | 97735
Household characteristics | One person or fewer per room |  | 5328575 | 585150 | 530245 | 168990 | 130515 | 2265160 | 203805 | 560590 | 283910 | 261030 | 243430 | 95760
Household characteristics | More than one person per room |  | 162625 | 9315 | 10135 | 1075 | 1010 | 115985 | 1495 | 10220 | 5400 | 4135 | 1870 | 1975
Household characteristics | Total - Private households by housing suitability - 25% sample data | 55 | 5491200 | 594470 | 540380 | 170060 | 131530 | 2381140 | 205300 | 570810 | 289310 | 265170 | 245300 | 97735
Household characteristics | Suitable |  | 5122185 | 566765 | 514955 | 165155 | 128075 | 2143340 | 198800 | 544475 | 275475 | 253730 | 238305 | 93110
Household characteristics | Not suitable |  | 369015 | 27705 | 25425 | 4905 | 3450 | 237800 | 6505 | 26335 | 13840 | 11435 | 6995 | 4630
Household characteristics | Total - Occupied private dwellings by period of construction - 25% sample data | 56 | 5491200 | 594470 | 540380 | 170060 | 131530 | 2381140 | 205300 | 570810 | 289310 | 265170 | 245300 | 97735
Household characteristics | 1960 or before |  | 1247430 | 179985 | 96065 | 47515 | 47155 | 434995 | 58225 | 112700 | 74740 | 89520 | 75430 | 31100
Household characteristics | 1961 to 1980 |  | 1456110 | 171715 | 130950 | 46960 | 32840 | 580820 | 59290 | 155400 | 79940 | 78125 | 89095 | 30975
Household characteristics | 1981 to 1990 |  | 711940 | 66835 | 74115 | 24410 | 13755 | 317030 | 25385 | 86160 | 35990 | 24975 | 30560 | 12735
Household characteristics | 1991 to 2000 |  | 644080 | 59705 | 76620 | 17400 | 12040 | 296325 | 21840 | 64695 | 31410 | 31320 | 21790 | 10920
Household characteristics | 2001 to 2005 |  | 385045 | 31080 | 46480 | 8745 | 5625 | 205480 | 10325 | 36845 | 15745 | 14625 | 6880 | 3205
Household characteristics | 2006 to 2010 |  | 348760 | 26995 | 37565 | 8920 | 6360 | 185040 | 10245 | 37565 | 16115 | 8415 | 8550 | 2985
Household characteristics | 2011 to 2015 |  | 328735 | 26020 | 34635 | 7685 | 5520 | 177240 | 9070 | 36520 | 14355 | 7620 | 7265 | 2805
Household characteristics | 2016 to 2021 | 57 | 369095 | 32135 | 43955 | 8430 | 8225 | 184215 | 10915 | 40905 | 21005 | 10565 | 5730 | 3010
| % built before 1981 |  | 49.23% | 59.16% | 42.01% | 55.55% | 60.82% | 42.66% | 57.24% | 46.97% | 53.47% | 63.22% | 67.07% | 63.51%
Household characteristics | Total - Occupied private dwellings by dwelling condition - 25% sample data | 58 | 5491200 | 594470 | 540380 | 170060 | 131530 | 2381140 | 205300 | 570810 | 289310 | 265170 | 245300 | 97735
Household characteristics | Only regular maintenance and minor repairs needed |  | 5177155 | 559980 | 514285 | 158590 | 123320 | 2260250 | 190280 | 537315 | 273735 | 248155 | 224365 | 86860
Household characteristics | Major repairs needed |  | 314050 | 34485 | 26095 | 11470 | 8200 | 120895 | 15025 | 33490 | 15570 | 17010 | 20930 | 10875
Household characteristics | Total - Private households by number of household maintainers - 25% sample data | 59 | 5491200 | 594470 | 540380 | 170060 | 131530 | 2381140 | 205300 | 570810 | 289310 | 265170 | 245300 | 97735
Household characteristics | One-maintainer household |  | 2677880 | 292765 | 244265 | 81950 | 65390 | 1140500 | 102965 | 278165 | 144540 | 140560 | 133005 | 53775
Household characteristics | Two-maintainer household |  | 2506110 | 276030 | 266730 | 81815 | 62780 | 1059580 | 95465 | 268950 | 132995 | 115405 | 105480 | 40890
Household characteristics | Three-or-more-maintainer household |  | 307210 | 25675 | 29390 | 6295 | 3355 | 181060 | 6870 | 23695 | 11775 | 9200 | 6815 | 3070
Household characteristics | Total - Private households by age of primary household maintainers - 25% sample data | 60 | 5491200 | 594470 | 540380 | 170060 | 131530 | 2381140 | 205300 | 570810 | 289310 | 265170 | 245300 | 97735
Household characteristics | 15 to 24 years |  | 126385 | 11040 | 13625 | 2810 | 2265 | 48490 | 5955 | 17235 | 9140 | 5620 | 7340 | 2875
Household characteristics | 25 to 34 years |  | 727305 | 72125 | 75265 | 16370 | 15170 | 325195 | 25955 | 80820 | 42790 | 31225 | 29445 | 12935
Household characteristics | 35 to 44 years |  | 930410 | 94660 | 95595 | 21075 | 18330 | 440100 | 28885 | 94960 | 48460 | 39695 | 34030 | 14620
Household characteristics | 45 to 54 years |  | 1013210 | 104335 | 100090 | 23765 | 18790 | 483325 | 30440 | 103270 | 49060 | 46140 | 38245 | 15735
Household characteristics | 55 to 64 years |  | 1149345 | 125790 | 111700 | 39550 | 29140 | 489425 | 44590 | 117870 | 57365 | 57760 | 54760 | 21395
Household characteristics | 65 to 74 years |  | 876960 | 103370 | 82225 | 37865 | 27505 | 335770 | 39600 | 91740 | 46365 | 48205 | 46525 | 17800
Household characteristics | 75 to 84 years |  | 481250 | 59615 | 45360 | 20955 | 14870 | 182070 | 22030 | 48555 | 26365 | 26515 | 25820 | 9095
Household characteristics | 85 years and over |  | 186330 | 23530 | 16525 | 7680 | 5460 | 76760 | 7845 | 16355 | 9765 | 10000 | 9130 | 3295
Household characteristics | Total - Owner and tenant households with household total income greater than zero, in non-farm, non-reserve private dwellings by shelter-cost-to-income ratio - 25% sample data | 61 | 5415420 | 588625 | 533925 | 166365 | 124015 | 2365225 | 201165 | 565220 | 283950 | 259905 | 237705 | 89320
Household characteristics | Spending less than 30% of income on shelter costs |  | 4103320 | 460350 | 416285 | 133835 | 102895 | 1652995 | 163305 | 457405 | 224320 | 216315 | 198520 | 77100
Household characteristics | Spending 30% or more of income on shelter costs |  | 1312095 | 128280 | 117640 | 32535 | 21120 | 712230 | 37855 | 107815 | 59625 | 43585 | 39185 | 12220
Household characteristics | 30% to less than 100% |  | 1169040 | 117150 | 106875 | 29785 | 19490 | 622015 | 34915 | 97085 | 54000 | 39980 | 36500 | 11240
Household characteristics | Total - Occupied private dwellings by housing indicators - 25% sample data | 62 | 5491205 | 594470 | 540385 | 170060 | 131530 | 2381140 | 205300 | 570810 | 289310 | 265170 | 245295 | 97735
Household characteristics | Total - Households 'spending 30% or more of income on shelter costs' or 'not suitable' or 'major repairs needed' |  | 1802285 | 173925 | 155820 | 44625 | 30340 | 957995 | 53945 | 152395 | 81520 | 65615 | 61200 | 24905
Household characteristics | Spending 30% or more of income on shelter costs only |  | 1150405 | 114380 | 106070 | 28875 | 19110 | 617060 | 33365 | 94955 | 53230 | 38280 | 34400 | 10680
Household characteristics | Not suitable only |  | 262900 | 20715 | 19345 | 3620 | 2715 | 164820 | 4705 | 19360 | 10265 | 8905 | 5315 | 3130
Household characteristics | Major repairs needed only |  | 201870 | 22720 | 17355 | 7905 | 6150 | 66980 | 10610 | 23195 | 10730 | 12200 | 15695 | 8320
Household characteristics | 'Spending 30% or more of income on shelter costs' and 'not suitable' |  | 74930 | 4350 | 4300 | 655 | 315 | 55220 | 855 | 4585 | 2460 | 1420 | 555 | 220
Household characteristics | 'Spending 30% or more of income on shelter costs' and 'major repairs needed' |  | 80990 | 9125 | 6960 | 2935 | 1630 | 36155 | 3470 | 7910 | 3725 | 3700 | 4110 | 1275
Household characteristics | 'Not suitable' and 'major repairs needed' |  | 25420 | 2215 | 1470 | 565 | 350 | 13965 | 775 | 2025 | 900 | 925 | 995 | 1235
Household characteristics | 'Spending 30% or more of income on shelter costs' and 'not suitable' and 'major repairs needed' |  | 5765 | 430 | 310 | 70 | 65 | 3800 | 165 | 365 | 215 | 190 | 125 | 40
Household characteristics | Acceptable housing |  | 3688915 | 420540 | 384565 | 125440 | 101190 | 1423150 | 151350 | 418415 | 207785 | 199550 | 184100 | 72830
Household characteristics | Total - Owner and tenant households with household total income greater than zero and shelter-cost-to-income ratio less than 100%, in non-farm, non-reserve private dwellings - 25% sample data | 63 | 5272360 | 577495 | 523160 | 163615 | 122385 | 2275010 | 198220 | 554490 | 278325 | 256295 | 235020 | 88340
Household characteristics | In core need |  | 639805 | 60895 | 48650 | 16165 | 6920 | 360515 | 17780 | 55155 | 24830 | 20405 | 21205 | 7295
Household characteristics | Not in core need |  | 4632550 | 516600 | 474510 | 147445 | 115465 | 1914500 | 180440 | 499340 | 253490 | 235885 | 213815 | 81050
Household characteristics | Total - Owner households in non-farm, non-reserve private dwellings - 25% sample data |  | 3718255 | 418910 | 384010 | 131145 | 95045 | 1558315 | 141950 | 380790 | 186095 | 188990 | 167125 | 65865
Household characteristics | % of owner households with a mortgage | 64 | 59.7 | 59 | 62.7 | 52.6 | 52 | 61.9 | 55.4 | 59.4 | 60.6 | 55.6 | 54.3 | 50.9
Household characteristics | % of owner households spending 30% or more of its income on shelter costs | 61 | 17.7 | 14.8 | 15.8 | 13.7 | 11.7 | 24.7 | 11 | 11.3 | 12.2 | 10.2 | 9.7 | 8.3
Household characteristics | % in core housing need | 63 | 6.4 | 4.7 | 4.8 | 5.4 | 2.8 | 9.3 | 4.2 | 4.1 | 3.3 | 3.4 | 4.8 | 4.5
Household characteristics | Median monthly shelter costs for owned dwellings ($) | 65 | 1440 | 1310 | 1530 | 1050 | 1000 | 1880 | 1070 | 1380 | 1240 | 1000 | 970 | 880
Household characteristics | Average monthly shelter costs for owned dwellings ($) | 65 | 1700 | 1524 | 1642 | 1284 | 1235 | 2090 | 1242 | 1536 | 1392 | 1203 | 1155 | 1100
Household characteristics | Median value of dwellings ($) | 66 | 700000 | 650000 | 700000 | 572000 | 500000 | 950000 | 400000 | 552000 | 532000 | 400000 | 286000 | 278000
Household characteristics | Average value of dwellings ($) | 66 | 807000 | 724000 | 756000 | 645000 | 579000 | 1092000 | 479200 | 595000 | 581500 | 459200 | 332000 | 300400
Household characteristics | Total - Tenant households in non-farm, non-reserve private dwellings - 25% sample data |  | 1722000 | 171950 | 151605 | 35700 | 29310 | 821080 | 59875 | 186545 | 99105 | 71650 | 71410 | 23755
Household characteristics | % of tenant households in subsidized housing | 67 | 13.7 | 13.6 | 11.2 | 16.4 | 15.3 | 13.3 | 14.4 | 14.2 | 11.3 | 15.8 | 19.3 | 23.3
Household characteristics | % of tenant households spending 30% or more of its income on shelter costs | 61 | 38.4 | 38.9 | 38 | 41 | 34.2 | 40.6 | 37.4 | 35.1 | 37.5 | 34.1 | 32.5 | 28.7
Household characteristics | % in core housing need | 63 | 24.9 | 25.1 | 21.1 | 26.6 | 15 | 28.7 | 20.5 | 22.3 | 19.8 | 20.2 | 19.1 | 18.9
Household characteristics | Median monthly shelter costs for rented dwellings ($) | 65 | 1300 | 1150 | 1320 | 1100 | 990 | 1530 | 1090 | 1290 | 1100 | 950 | 920 | 930
Household characteristics | Average monthly shelter costs for rented dwellings ($) | 65 | 1408 | 1257 | 1376 | 1178 | 1045 | 1612 | 1169 | 1338 | 1187 | 1035 | 954 | 962
Household characteristics | Total - Households living in a dwelling provided by the local government, First Nation or Indian band in non-farm private dwellings - 25% sample data |  | 10510 | 65 | 230 | 195 | 205 | 50 | 290 | 0 | 35 | 285 | 2650 | 6500
Household characteristics | % of households living in a dwelling provided by the local government, First Nation or Indian band spending more than 30% on shelter costs | 61 | 8.7 | 15.4 | 8.7 | 21.1 | 7.3 | 33.3 | 12.1 |  | 0 | 14.5 | 10.5 | 7.1
Household characteristics | Median monthly shelter costs for dwellings provided by local government, First Nation or Indian band ($) | 65 | 324 | 456 | 588 | 420 | 400 | 444 | 645 |  | 388 | 480 | 444 | 250
Household characteristics | Average monthly shelter costs for dwellings provided by local government, First Nation or Indian band ($) | 65 | 380 | 480 | 600 | 508 | 416 | 580 | 675 |  | 440 | 492 | 457 | 314
Symbols:
r | revised
Notes:
1 | 2021 and 2016 population
Statistics Canada is committed to protect the privacy of all Canadians and the confidentiality of the data they provide to us. As part of this commitment some population counts of geographic areas are adjusted in order to ensure confidentiality.
The adjustment to counts of the total population for any dissemination block is controlled to ensure that the population counts for dissemination areas will always be within 5 of the actual values. The adjustment has no impact on the population counts of census divisions and large census subdivisions.
2 | Total private dwellings
Private dwelling refers to a separate set of living quarters with a private entrance either from outside the building or from a common hall lobby vestibule or stairway inside the building. The entrance to the dwelling must be one that can be used without passing through the living quarters of some other person or group of persons.
3 | Private dwellings occupied by usual residents
A private dwelling occupied by usual residents refers to a private dwelling in which a person or a group of persons is permanently residing. Also included are private dwellings whose usual residents are temporarily absent on May 11 2021.
4 | The category 'Movable dwelling' includes mobile homes and other movable dwellings such as houseboats recreational vehicles and railroad cars.
50 | Tenure refers to whether the household owns or rents their private dwelling. The private dwelling may be situated on rented or leased land or be part of a condominium. A household is considered to own their dwelling if some member of the household owns the dwelling even if it is not fully paid for for example if there is a mortgage or some other claim on it. A household is considered to rent their dwelling if no member of the household owns the dwelling. A household is considered to rent that dwelling even if the dwelling is provided without cash rent or at a reduced rent or if the dwelling is part of a cooperative.
For historical and statutory reasons shelter occupancy on Indian reserves or settlements does not lend itself to the usual classification by standard tenure categories. Therefore a special category 'dwelling provided by the local government First Nation or Indian band ' has been created for census purposes.
51 | Condominium status refers to whether the private dwelling is part of a condominium development. A condominium is a residential complex in which dwellings are owned individually while land and common elements are held in joint ownership with others.
52 | Bedrooms refers to rooms in a private dwelling that are designed mainly for sleeping purposes even if they are now used for other purposes such as guest rooms and television rooms. Also included are rooms used as bedrooms now even if they were not originally built as bedrooms such as bedrooms in a finished basement. Bedrooms exclude rooms designed for another use during the day such as dining rooms and living rooms even if they may be used for sleeping purposes at night. By definition one-room private dwellings such as bachelor or studio apartments have zero bedrooms.
53 | Rooms refers to enclosed areas within a private dwelling which are finished and suitable for year round living. The number of rooms in a private dwelling includes kitchens bedrooms and finished rooms in the attic or basement. The number of rooms in a private dwelling excludes bathrooms halls vestibules and rooms used solely for business purposes. Partially divided rooms are considered to be separate rooms if they are considered as such by the respondent (e.g. L-shaped dining-room and living-room arrangements).
54 | Number of persons per room - Refers to an indicator of the level of crowding in a private dwelling. It is calculated by dividing the number of persons in the household by the number of rooms in the dwelling.
55 | Housing suitability refers to whether a private household is living in suitable accommodations according to the National Occupancy Standard (NOS); that is whether the dwelling has enough bedrooms for the size and composition of the household. A household is deemed to be living in suitable accommodations if its dwelling has enough bedrooms as calculated using the NOS.
'Housing suitability' assesses the required number of bedrooms for a household based on the age sex and relationships among household members. An alternative variable 'persons per room ' considers all rooms in a private dwelling and the number of household members.
Housing suitability and the National Occupancy Standard (NOS) on which it is based were developed by Canada Mortgage and Housing Corporation (CMHC) through consultations with provincial housing agencies.
56 | Period of construction refers to the period in time during which the building or dwelling was originally constructed.
This refers to the period in which the building was completed not the time of any later remodeling additions or conversions.
For properties having multiple residential structures this refers to the period in which the most recent structure was completed.
57 | Includes data up to May 11 2021.
58 | Dwelling condition refers to whether the dwelling is in need of repairs. This does not include desirable remodelling or additions.
59 | Refers to whether or not a person residing in the household is responsible for paying the rent or the mortgage or the taxes or the electricity or other services or utilities. Where a number of people may contribute to the payments more than one person in the household may be identified as a household maintainer. If no person in the household is identified as making such payments the reference person is identified by default.
60 | Primary household maintainer - The first person in the household identified as someone who pays the rent or the mortgage or the taxes or the electricity or other services or utilities for the dwelling. When more than one member of the household contributes to the payments the first person listed is chosen as the primary household maintainer. If no person in the household is identified as making any such payments the first person listed is selected by default.
The order of the persons in a household is determined by the order in which they are listed on the questionnaire. Generally an adult is listed first followed if applicable by their spouse or common-law partner and then by their children. The order does not necessarily correspond to the proportion of household payments made by each person.
61 | Shelter-cost-to-income ratio - Refers to the proportion of average total income of household which is spent on shelter costs.
Shelter-cost-to-income ratio is calculated for private households who reported a total household income greater than zero.
Private households located on an agricultural operation that is operated by a member of the household and households who reported a zero or negative total household income are excluded.
The relatively high shelter-costs-to-household income ratios for some households may have resulted from the difference in the reference period for shelter costs and household total income data. The reference period for shelter cost data is 2021 while household total income is reported for the year 2020. As well for some households the 2020 household total income may represent income for only part of a year.
For more information on household total income or shelter costs refer to the Census Dictionary: Total income and Shelter cost.
62 | Acceptable housing refers to whether a household meets each of the three indicator thresholds established by the Canada Mortgage and Housing Corporation for housing adequacy suitability and affordability.Housing indicator thresholds are defined as follows:
*Adequate housing is reported by their residents as not requiring any major repairs.
*Affordable housing has shelter costs equal to less than 30% of total before-tax household income.
*Suitable housing has enough bedrooms for the size and composition of resident households according to the National Occupancy Standard (NOS) conceived by the Canada Mortgage and Housing Corporation and provincial and territorial representatives.
Acceptable housing identifies which thresholds the household falls below if any. Housing that is adequate in condition suitable in size and affordable is considered to be acceptable.
Households below and above the thresholds are based on the indicators for which individual households can be assessed. Farm and on-reserve households whose housing does not meet either or both of the suitability and adequacy thresholds are counted in the total of households below the thresholds. Farm and on-reserve households who live in housing that meets both the suitability and adequacy thresholds are counted in the total of households above the thresholds (even though it is not possible to assess housing affordability for these households). Farm households and on-reserve households cannot be assessed for housing affordability because the concept is not applicable.
Housing affordability is assessed for owner and tenant households with household total income greater than zero in non-farm non-reserve private dwellings.
63 | Core housing need refers to whether a private household's housing falls below at least one of the indicator thresholds for housing adequacy affordability or suitability and would have to spend 30% or more of its total before-tax income to pay the median rent of alternative local housing that is acceptable (attains all three housing indicator thresholds). Housing indicator thresholds are defined as follows: Adequate housing is reported by their residents as not requiring any major repairs. Affordable housing has shelter costs equal to less than 30% of total before-tax household income. Suitable housing has enough bedrooms for the size and composition of resident households according to the National Occupancy Standard (NOS) conceived by the Canada Mortgage and Housing Corporation and provincial and territorial representatives. Only private non-farm non-reserve and owner- or renter-households with incomes greater than zero and shelter-cost-to-income ratios less than 100% are assessed for 'core housing need.' Non-family households with at least one maintainer aged 15 to 29 attending school are considered not to be in 'core housing need' regardless of their housing circumstances. Attending school is considered a transitional phase and low incomes earned by student households are viewed as being a temporary condition.
64 | Presence of mortgage payments refers to whether an owner household makes regular mortgage or loan payments for their dwelling.
65 | Shelter cost refers to the average monthly total of all shelter expenses paid by households.
Shelter costs for owner households include where applicable mortgage payments property taxes and condominium fees along with the costs of electricity heat water and other municipal services. For renter households shelter costs include where applicable the rent and the costs of electricity heat water and other municipal services. For households living in a dwelling provided by the local government First Nation or Indian band shelter costs include where applicable the monthly use or occupancy payment and the costs of electricity heat water and other municipal services.
66 | Value (owner estimated) refers to the dollar amount expected by the owner if the asset were to be sold.
In the context of dwelling it refers to the value of the entire dwelling including the value of the land it is on and of any other structure such as a garage which is on the property. If the dwelling is located in a building which contains several dwellings or a combination of residential and business premises all of which the household owns the value is estimated as a portion of the market value that applies only to the dwelling in which the household resides.
67 | Subsidized housing refers to whether a renter household lives in a dwelling that is subsidized. Subsidized housing includes rent geared to income social housing public housing government-assisted housing non-profit housing rent supplements and housing allowances.
Data quality:
Ontario
Excludes census data for one or more incompletely enumerated reserves or settlements.
Total non-response (TNR) rate, short-form census questionnaire: 2.8%
Total non-response (TNR) rate, long-form census questionnaire: 3.8%
Hamilton--Niagara Peninsula
Excludes census data for one or more incompletely enumerated reserves or settlements.
Total non-response (TNR) rate, short-form census questionnaire: 2.5%
Total non-response (TNR) rate, long-form census questionnaire: 3.5%
Kitchener--Waterloo--Barrie
Total non-response (TNR) rate, short-form census questionnaire: 2.4%
Total non-response (TNR) rate, long-form census questionnaire: 3.5%
Muskoka--Kawarthas
Excludes census data for one or more incompletely enumerated reserves or settlements.
Total non-response (TNR) rate, short-form census questionnaire: 4.5%
Total non-response (TNR) rate, long-form census questionnaire: 5.9%
Stratford--Bruce Peninsula
Total non-response (TNR) rate, short-form census questionnaire: 2.7%
Total non-response (TNR) rate, long-form census questionnaire: 3.7%
Source: Statistics Canada, 2021 Census of Population.
How to cite: Statistics Canada. 2022. Census Profile. 2021 Census.
Statistics Canada Catalogue no. 98-316-X2021001. Ottawa. Released December 15 2022.
https://www12.statcan.gc.ca/census-recensement/2021/dp-pd/prof/index.cfm?Lang=E

## other data (hidden)
housing stock
2021 census economic region | population | detached | attached | row
Windsor-Sarnia | 655330 | 190960 | 10465 | 13295
Stratford-Bruce Peninsula | 317232 | 101040 | 4420 | 5900
London | 717096 | 172965 | 10995 | 28375
Hamilton-Niagara Peninsula | 1495885 | 367540 | 24300 | 62955
Kitchener-Waterloo - Barrie | 1427617 | 340700 | 25735 | 51735
Toronto | 6525393 | 961005 | 169280 | 222625
Total | 11138553 | 2134210 | 245195 | 384885
Ontario | 14223942 | 2942990 | 303260 | 505265
% of Ontario | 0.78308 | 0.72518 | 0.80853 | 0.76175
Muskoka-Kawarthas | 403538 | 134410 | 2890 | 6580
IESO communications
They currently use a median temperature estimate for the whole province when developing APO demand forescast (seems to be -13.5'C)
APO 2022 demand forecast includes 254,000 ASHPs and 90,000 GSHPs by 2038, mostly in the Toronto region driven by the Toronto Green Standard, No hybrid heat pumps are included in the forecast
To convert daily avoided costs for Capacity, Transmission, or Distribution, multiply the daily avoided costs by 250 days.
So for example, if the avoided transmission cost is $116.80 per MW-day, it equates to $29,200/MW-year.
Metric | System Demand (GW), by Metric, By Hour Ending
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
2024 Hourly Minimum | 15.38 | 15.07 | 14.79 | 14.61 | 14.57 | 14.67 | 15.03 | 15.6 | 15.91 | 16.45 | 17.08 | 17.54 | 17.83 | 17.93 | 17.82 | 17.85 | 18.33 | 18.73 | 18.96 | 18.7 | 18.41 | 17.81 | 16.92 | 15.75
2024 Hourly Median | 16.47 | 16.08 | 15.89 | 15.82 | 15.97 | 16.5 | 17.61 | 19.06 | 19.44 | 19.59 | 19.85 | 19.95 | 19.99 | 19.98 | 19.86 | 19.87 | 20.21 | 20.88 | 20.72 | 20.39 | 20.03 | 19.31 | 18.32 | 17.16
2024 Hourly Maximum | 18.25 | 17.82 | 17.49 | 17.41 | 17.47 | 17.93 | 19.23 | 20.96 | 21.16 | 21.12 | 21.29 | 21.41 | 21.28 | 21.21 | 21.04 | 20.91 | 20.99 | 22.01 | 22.54 | 22.6 | 22.44 | 21.68 | 20.47 | 19.13
2043 Hourly Minimum | 25.08 | 24.69 | 24.44 | 23.74 | 22.99 | 22.4 | 22.24 | 22.68 | 22.9 | 23.56 | 24.28 | 24.53 | 24.71 | 24.5 | 24.12 | 23.88 | 24.29 | 25.35 | 25.86 | 26.35 | 26.99 | 26.95 | 26.66 | 26.11
2043 Hourly Median | 28.04 | 27.57 | 27.46 | 26.76 | 26.02 | 25.55 | 25.94 | 27.07 | 27.18 | 27.01 | 26.78 | 26.51 | 26.28 | 25.93 | 25.71 | 25.66 | 26.27 | 27.25 | 28.14 | 28.78 | 29.6 | 29.67 | 29.11 | 28.29
2043 Hourly Maximum | 30.19 | 29.75 | 29.13 | 28.29 | 27.37 | 26.93 | 27.52 | 28.88 | 29.07 | 29.25 | 29.56 | 29.65 | 29.27 | 28.93 | 28.53 | 27.86 | 27.33 | 28.29 | 29.04 | 29.8 | 30.87 | 31.46 | 31.13 | 30.37