## inputs
input | value | notes | source
W/ sq m | 32.5127 | average for fixed angle grid-scale PV based on NREL values https://www.nrel.gov/docs/fy13osti/56290.pdf (2013 paper)
annual kWh/kW Wesleyville | 1270 | https://pvwatts.nrel.gov/pvwatts.php
% of annual generation during TOU summer on-peak times | 33.26% | calculated from Engineering Climate Datasets for Toronto | https://collaboration.cmc.ec.gc.ca/cmc/climate/Engineer_Climate/CWEEDS_FMCEG/CWEEDS_FMCEG_v_2020/CWEEDS-FMCEG_by_par_prov.CSV/
marginal emissions factor for 2024 (kg/kW array) | 158.8696 | OCAA rooftop solar report | https://www.cleanairalliance.org/making-the-most-of-rooftop-solar/
marginal emissions factor for 2030 (kg/kW array) | 407.389 | OCAA rooftop solar report | https://www.cleanairalliance.org/making-the-most-of-rooftop-solar/
assumptions
zero production in January due to snow
tilt angle is optimized for each site (30' in all locations)
14.08% system losses
180' aximuth
1.2 DC to AC size ratio
96% inverter efficiency
albedo from weather file

## analysis by area size
area type | total area for solar (m2) | MW of potential | GWh/yr | summer peak GWh/yr | kT/yr emissions avoided 2024 | kT/yr emissions avoided 2030
Wesleyville | 2565798 | 83.4211 | 105.9447 | 35.2372 | 13.2531 | 33.9848
Total | 2565798 | 83.4211 | 105.9447 | 35.2372 | 13.2531 | 33.9848

## site details
site name | subsection | area (acres) | area (m2) | final area (m2) | notes | Sources
Wesleyville | 510630121 | 4 | 16188 | 16188 |  | Wesleyville | https://www.opg.com/projects-services/projects/new-generation-opportunities/wesleyville/
Wesleyville | 510630099 | 414 | 1675458 | 1116972
Wesleyville | 510630101 | 34 | 137598 | 137598
Wesleyville | 510630087 | 862 | 3488514 | 3488514
Wesleyville | 510630001 | 19 | 76893 | 0 | over water
Wesleyville | from Port Hope press release | 634 | 2565798 | 2565798
Wesleyville total area |  |  |  | 4759272
Wesleyville total area for solar |  |  |  | 2565798